## Change Log
Entry # | Date | Name | New Document Name | Cell/Range Modified | Changes Made | Comments
1 | 2020-04-14 | Jillian Panagakos | 2020_0414_AHU Fan Variable Volume_jp | Change Log sheet | Change log sheet created
2 | 2020-05-12 | Duncan | 2020_0512_ahu_fan_var_volm_v1.xlsx | Intro | Moidified language to be more explicit on tabs and steps
3 | 2023-02-03 | Linyuan Cui | 2023_0203_ahu_fan_var_volm | Step 1.1 | Inputted hourly kW data of supply fan B2 from MSC from 3/11 to 12/31/2022
|  |  |  | Step 1.2 | Inputted hourly kW data of return fan B2 from MSC from 3/11 to 12/31/2022
|  |  |  | Step 1.3 | Inputted hourly OAT at NY JFK station from NEWA website from 1/1 to 12/31/2022
|  |  |  | Step 6 | Aligned the years in columns I and A.

## Intro
Introduction and Instructions
Model Description
Measured variables: supply fan motor power, return fan motor power, OAT
The model calculates total annual energy for the two fans in an AHU
The hourly energy is a regression equation with OAT as the independent variable
General supply fan equation: Total supply fan energy = sum(supply fan true power (OAT))
General return fan equation: Total return fan energy = sum(return fan true power (OAT))
Model Instructions
The yellow cells are the input cells.
Instructions for each sheet
1.1 | in tab "Step 1.1 Supply RMS Power Data" – Paste the hourly supply fan data from the Dent meter. The data format is · Date and time – mm/dd/yyyy hh:mm · RMS Power – kWh
1.2 | In tab "Step 1.2 Return RMS Power Data" – Paste the hourly supply fan data from the Dent meter. The data format is · Date and time – mm/dd/yyyy hh:mm · RMS Power – kWh
1.3 | In tab "Step 1.3 Outdoor Air Temperature Data" – Paste the hourly outdoor air temperature data from the data logger. The data format is · Date and time – mm/dd/yyyy hh:mm · Outdoor Air Temperature, F
2 | "Step 2 Aggregate data" tab – There are no inputs on this worksheet. The raw time series data is compiled on this worksheet. The data is then sorted by ascending RMS power value. The purpose of the sort is to remove the data rows when zero power was measured (i.e., when the fan is off).
3 | "Step 3 Regression Model" – There are no inputs on this worksheet. It takes the sorted data from the previous worksheet, and fits a polynomial regression for power as a function of OAT.
The statistics for the regression are generated from the MS Excel linest() function.
| A coefficient value | B coefficient value | C coefficient value
| A standard error | B standard error | C standard error
| R2 coefficient of determination | Standard error of the y-estimate (i.e., RMSE)
| F-Stat | Degrees of freedom
| Regression sum of squares | Residual sum of squares
The quality of the model is broadly determined by looking at the R2 value and the RMSE. R2 compares estimated and actual y-values, and ranges in value from 0 to 1. If it is 1, there is a perfect correlation in the sample — there is no difference between the estimated y-value and the actual y-value. At the other extreme, if the coefficient of determination is 0, the regression equation is not helpful in predicting a y-value. The magnitude of RMSE should be much smaller than the actual y-values. Refer to MS Excel linest() help for further readings on the statistics.
If the model fits poorly, examine the scatter plots on this spreadsheet to see how well correlated power is to OAT. Look for outliers and other inexplicable patterns, such as due to motor start up conditions. Such irregular data points should be removed (or zeroed out) from the raw data set that is fed to the regression model.
4 | "Step 4. Runtime Calcs" tab - There are no inputs on this worksheet. The power data for both fans is analyzed to calculate runtime hours.
5 | "Step 5. Energy Calcs" tab – The energy consumption during each operating hour through the year is calculated on this worksheet. The columns are as follows: - Date Time – has every hour of the year for the weather normal year (8760 rows) - Fan % operating hrs – based on the runtime hours, each hour of the year is marked off with a “1”, if the fan is operating or a “0” if the fan is off - Normalized OAT – This column has the normalized OAT at LaGuardia Airport (NOAA). The normalized OAT represents the average temperature for a given hour, averaged over the last ten years. - Fan Energy – The energy for the given OAT at a given hour of the year. This value is generated from the regression equation but then multiplied by the fan % operating hours to set the energy to zero when the fans are turned off.
6 | "Step 6. Results" tab – The annual energy for both fans is calculated by summing the hourly energy. This spreadsheet also includes diagnostic charts on - Hours of Operation Per Day – Do the motor operating hours make sense with respect to the facility’s operating hours? - Modeled energy per day – for 365 days. Since the regression model is only representative of the period of the year when the measurements were taken, this plot may show when the model yields unreasonable values. For example, if the measurement is taken in the peak cooling season, then the values may not seem reasonable by the shoulder season. If this is the case, then additional measurements should be taken to fit regression models for other times of the year.

## Step 1.1 Supply Fan Power Data
Datetime | RMS Power (kW)
2022-03-11 09:00 | 12.0351
2022-03-11 10:00 | 12.0351
2022-03-11 11:00 | 12.0351
2022-03-11 12:00 | 12.0351
2022-03-11 13:00 | 12.0351
2022-03-11 14:00 | 12.0351
2022-03-11 15:00 | 12.0351
2022-03-11 16:00 | 12.0351
2022-03-11 17:00 | 12.0351
2022-03-11 18:00 | 12.0351
2022-03-11 19:00 | 6.2229
2022-03-11 20:00 | 4.8652
2022-03-11 21:00 | 4.8438
2022-03-11 22:00 | 4.8389
2022-03-11 23:00 | 4.8331
2022-03-12 | 4.7958
2022-03-12 01:00 | 4.8291
2022-03-12 02:00 | 4.8662
2022-03-12 03:00 | 4.9003
2022-03-12 04:00 | 4.8983
2022-03-12 05:00 | 4.8983
2022-03-12 06:00 | 4.906
2022-03-12 07:00 | 4.8954
2022-03-12 08:00 | 4.8964
2022-03-12 09:00 | 4.8643
2022-03-12 10:00 | 4.908
2022-03-12 11:00 | 4.8604
2022-03-12 12:00 | 4.8007
2022-03-12 13:00 | 4.8164
2022-03-12 14:00 | 4.832
2022-03-12 15:00 | 4.8379
2022-03-12 16:00 | 4.8457
2022-03-12 17:00 | 4.8428
2022-03-12 18:00 | 4.9022
2022-03-12 19:00 | 4.9408
2022-03-12 20:00 | 4.9225
2022-03-12 21:00 | 4.9031
2022-03-12 22:00 | 4.9486
2022-03-12 23:00 | 4.9303
2022-03-13 | 4.9283
2022-03-13 01:00 | 4.9755
2022-03-13 02:00 | 4.9745
2022-03-13 03:00 | 5.0215
2022-03-13 04:00 | 5.0224
2022-03-13 05:00 | 5.0424
2022-03-13 06:00 | 5.0138
2022-03-13 07:00 | 5.0596
2022-03-13 08:00 | 5.1304
2022-03-13 09:00 | 5.0785
2022-03-13 10:00 | 5.0794
2022-03-13 11:00 | 5.087
2022-03-13 12:00 | 5.0243
2022-03-13 13:00 | 4.9697
2022-03-13 14:00 | 4.9621
2022-03-13 15:00 | 4.9573
2022-03-13 16:00 | 4.9582
2022-03-13 17:00 | 4.9659
2022-03-13 18:00 | 4.9745
2022-03-13 19:00 | 4.9899
2022-03-13 20:00 | 5.0138
2022-03-13 21:00 | 5.0081
2022-03-13 22:00 | 4.9745
2022-03-13 23:00 | 5.0434
2022-03-14 | 5.0282
2022-03-14 01:00 | 5.0879
2022-03-14 02:00 | 5.0917
2022-03-14 03:00 | 5.0596
2022-03-14 04:00 | 5.0538
2022-03-14 05:00 | 6.4743
2022-03-14 06:00 | 12.0351
2022-03-14 07:00 | 12.0351
2022-03-14 08:00 | 12.0351
2022-03-14 09:00 | 12.0351
2022-03-14 10:00 | 12.0351
2022-03-14 11:00 | 12.0351
2022-03-14 12:00 | 12.0351
2022-03-14 13:00 | 12.0351
2022-03-14 14:00 | 12.0351
2022-03-14 15:00 | 12.0351
2022-03-14 16:00 | 12.0351
2022-03-14 17:00 | 12.0351
2022-03-14 18:00 | 12.0351
2022-03-14 19:00 | 4.8808
2022-03-14 20:00 | 4.834
2022-03-14 21:00 | 4.8457
2022-03-14 22:00 | 4.873
2022-03-14 23:00 | 4.9899
2022-03-15 | 5.0004
2022-03-15 01:00 | 5.0424
2022-03-15 02:00 | 5.0596
2022-03-15 03:00 | 5.0908
2022-03-15 04:00 | 5.0794
2022-03-15 05:00 | 5.1191
2022-03-15 06:00 | 12.0351
2022-03-15 07:00 | 12.0351
2022-03-15 08:00 | 12.0351
2022-03-15 09:00 | 12.0351
2022-03-15 10:00 | 12.0351
2022-03-15 11:00 | 12.0351
2022-03-15 12:00 | 12.0351
2022-03-15 13:00 | 12.0351
2022-03-15 14:00 | 12.0351
2022-03-15 15:00 | 12.0351
2022-03-15 16:00 | 12.0351
2022-03-15 17:00 | 12.0351
2022-03-15 18:00 | 0.87619
2022-03-15 19:00 | 0.91252
2022-03-15 20:00 | 0.90861
2022-03-15 21:00 | 0.89784
2022-03-15 22:00 | 0.89096
2022-03-15 23:00 | 0.88606
2022-03-16 | 0.9047
2022-03-16 01:00 | 0.92325
2022-03-16 02:00 | 0.90567
2022-03-16 03:00 | 0.90175
2022-03-16 04:00 | 0.92905
2022-03-16 05:00 | 0.93198
2022-03-16 06:00 | 11.5343
2022-03-16 07:00 | 12.0351
2022-03-16 08:00 | 12.0351
2022-03-16 09:00 | 12.0351
2022-03-16 10:00 | 12.0351
2022-03-16 11:00 | 12.0351
2022-03-16 12:00 | 12.0351
2022-03-16 13:00 | 12.0351
2022-03-16 14:00 | 12.0351
2022-03-16 15:00 | 12.0351
2022-03-16 16:00 | 12.0351
2022-03-16 17:00 | 7.7985
2022-03-16 18:00 | 4.7958
2022-03-16 19:00 | 4.8545
2022-03-16 20:00 | 4.8613
2022-03-16 21:00 | 4.8311
2022-03-16 22:00 | 4.8935
2022-03-16 23:00 | 4.9428
2022-03-17 | 4.9012
2022-03-17 01:00 | 4.9515
2022-03-17 02:00 | 4.988
2022-03-17 03:00 | 4.987
2022-03-17 04:00 | 5.0158
2022-03-17 05:00 | 4.9947
2022-03-17 06:00 | 12.0351
2022-03-17 07:00 | 12.0351
2022-03-17 08:00 | 12.0351
2022-03-17 09:00 | 12.0351
2022-03-17 10:00 | 12.0351
2022-03-17 11:00 | 12.0351
2022-03-17 12:00 | 12.0351
2022-03-17 13:00 | 12.0351
2022-03-17 14:00 | 12.0351
2022-03-17 15:00 | 12.0351
2022-03-17 16:00 | 12.0351
2022-03-17 17:00 | 9.9006
2022-03-17 18:00 | 4.788
2022-03-17 19:00 | 4.7948
2022-03-17 20:00 | 4.785
2022-03-17 21:00 | 4.8964
2022-03-17 22:00 | 4.9109
2022-03-17 23:00 | 4.9437
2022-03-18 | 4.9109
2022-03-18 01:00 | 4.9119
2022-03-18 02:00 | 4.8847
2022-03-18 03:00 | 4.9012
2022-03-18 04:00 | 4.9515
2022-03-18 05:00 | 4.9823
2022-03-18 06:00 | 12.0351
2022-03-18 07:00 | 12.0351
2022-03-18 08:00 | 12.0351
2022-03-18 09:00 | 12.0351
2022-03-18 10:00 | 12.0351
2022-03-18 11:00 | 12.0351
2022-03-18 12:00 | 12.0351
2022-03-18 13:00 | 12.0351
2022-03-18 14:00 | 12.0351
2022-03-18 15:00 | 12.0351
2022-03-18 16:00 | 12.0351
2022-03-18 17:00 | 12.0351
2022-03-18 18:00 | 7.2438
2022-03-18 19:00 | 4.8281
2022-03-18 20:00 | 4.8281
2022-03-18 21:00 | 4.8164
2022-03-18 22:00 | 4.8574
2022-03-18 23:00 | 4.908
2022-03-19 | 4.9534
2022-03-19 01:00 | 4.937
2022-03-19 02:00 | 4.9341
2022-03-19 03:00 | 4.9147
2022-03-19 04:00 | 4.9447
2022-03-19 05:00 | 4.9303
2022-03-19 06:00 | 4.9341
2022-03-19 07:00 | 4.9437
2022-03-19 08:00 | 4.9312
2022-03-19 09:00 | 4.8964
2022-03-19 10:00 | 4.8584
2022-03-19 11:00 | 4.8526
2022-03-19 12:00 | 4.8672
2022-03-19 13:00 | 4.8973
2022-03-19 14:00 | 4.8798
2022-03-19 15:00 | 4.8301
2022-03-19 16:00 | 4.8184
2022-03-19 17:00 | 4.834
2022-03-19 18:00 | 4.7781
2022-03-19 19:00 | 4.7663
2022-03-19 20:00 | 4.7762
2022-03-19 21:00 | 4.7525
2022-03-19 22:00 | 4.7584
2022-03-19 23:00 | 4.7958
2022-03-20 | 4.784
2022-03-20 01:00 | 4.8184
2022-03-20 02:00 | 4.834
2022-03-20 03:00 | 4.7948
2022-03-20 04:00 | 4.7909
2022-03-20 05:00 | 4.8193
2022-03-20 06:00 | 4.8281
2022-03-20 07:00 | 4.8682
2022-03-20 08:00 | 4.8584
2022-03-20 09:00 | 4.8252
2022-03-20 10:00 | 4.8438
2022-03-20 11:00 | 4.8027
2022-03-20 12:00 | 4.8076
2022-03-20 13:00 | 4.7801
2022-03-20 14:00 | 4.7594
2022-03-20 15:00 | 4.7466
2022-03-20 16:00 | 4.7771
2022-03-20 17:00 | 4.7396
2022-03-20 18:00 | 4.7545
2022-03-20 19:00 | 4.7663
2022-03-20 20:00 | 4.787
2022-03-20 21:00 | 4.7436
2022-03-20 22:00 | 4.7396
2022-03-20 23:00 | 4.7663
2022-03-21 | 4.7948
2022-03-21 01:00 | 4.8193
2022-03-21 02:00 | 4.8565
2022-03-21 03:00 | 4.8242
2022-03-21 04:00 | 4.8701
2022-03-21 05:00 | 6.7462
2022-03-21 06:00 | 12.0351
2022-03-21 07:00 | 12.0351
2022-03-21 08:00 | 12.0351
2022-03-21 09:00 | 12.0351
2022-03-21 10:00 | 12.0351
2022-03-21 11:00 | 12.0351
2022-03-21 12:00 | 12.0351
2022-03-21 13:00 | 12.0351
2022-03-21 14:00 | 12.0351
2022-03-21 15:00 | 12.0351
2022-03-21 16:00 | 12.0351
2022-03-21 17:00 | 12.0351
2022-03-21 18:00 | 4.7258
2022-03-21 19:00 | 4.7938
2022-03-21 20:00 | 4.711
2022-03-21 21:00 | 4.6812
2022-03-21 22:00 | 4.6901
2022-03-21 23:00 | 4.7357
2022-03-22 | 4.7317
2022-03-22 01:00 | 4.8418
2022-03-22 02:00 | 4.7899
2022-03-22 03:00 | 4.8487
2022-03-22 04:00 | 4.8672
2022-03-22 05:00 | 4.9138
2022-03-22 06:00 | 12.0351
2022-03-22 07:00 | 12.0351
2022-03-22 08:00 | 12.0351
2022-03-22 09:00 | 12.0351
2022-03-22 10:00 | 12.0351
2022-03-22 11:00 | 12.0351
2022-03-22 12:00 | 12.0351
2022-03-22 13:00 | 12.0351
2022-03-22 14:00 | 12.0351
2022-03-22 15:00 | 12.0351
2022-03-22 16:00 | 12.0351
2022-03-22 17:00 | 8.4296
2022-03-22 18:00 | 2.7152
2022-03-22 19:00 | 2.7661
2022-03-22 20:00 | 2.7421
2022-03-22 21:00 | 2.7601
2022-03-22 22:00 | 2.7301
2022-03-22 23:00 | 2.7142
2022-03-23 | 2.7511
2022-03-23 01:00 | 2.7972
2022-03-23 02:00 | 2.7431
2022-03-23 03:00 | 2.7751
2022-03-23 04:00 | 2.7871
2022-03-23 05:00 | 2.8042
2022-03-23 06:00 | 11.4901
2022-03-23 07:00 | 12.0351
2022-03-23 08:00 | 12.0351
2022-03-23 09:00 | 12.0351
2022-03-23 10:00 | 12.0351
2022-03-23 11:00 | 12.0351
2022-03-23 12:00 | 12.0351
2022-03-23 13:00 | 12.0351
2022-03-23 14:00 | 12.0351
2022-03-23 15:00 | 12.0351
2022-03-23 16:00 | 12.0351
2022-03-23 17:00 | 12.0351
2022-03-23 18:00 | 4.7238
2022-03-23 19:00 | 4.7396
2022-03-23 20:00 | 4.6921
2022-03-23 21:00 | 4.707
2022-03-23 22:00 | 4.7584
2022-03-23 23:00 | 4.7456
2022-03-24 | 4.8193
2022-03-24 01:00 | 4.8535
2022-03-24 02:00 | 4.8457
2022-03-24 03:00 | 4.8467
2022-03-24 04:00 | 4.873
2022-03-24 05:00 | 4.8886
2022-03-24 06:00 | 10.2971
2022-03-24 07:00 | 12.0351
2022-03-24 08:00 | 12.0351
2022-03-24 09:00 | 12.0351
2022-03-24 10:00 | 12.0351
2022-03-24 11:00 | 12.0351
2022-03-24 12:00 | 12.0351
2022-03-24 13:00 | 12.0351
2022-03-24 14:00 | 12.0351
2022-03-24 15:00 | 12.0351
2022-03-24 16:00 | 12.0351
2022-03-24 17:00 | 6.544
2022-03-24 18:00 | 4.7119
2022-03-24 19:00 | 4.7436
2022-03-24 20:00 | 4.6891
2022-03-24 21:00 | 4.706
2022-03-24 22:00 | 4.7406
2022-03-24 23:00 | 4.7525
2022-03-25 | 4.786
2022-03-25 01:00 | 4.8046
2022-03-25 02:00 | 4.8066
2022-03-25 03:00 | 4.837
2022-03-25 04:00 | 4.7988
2022-03-25 05:00 | 4.8242
2022-03-25 06:00 | 4.8652
2022-03-25 07:00 | 4.8242
2022-03-25 08:00 | 8.5391
2022-03-25 09:00 | 12.0351
2022-03-25 10:00 | 12.0351
2022-03-25 11:00 | 12.0351
2022-03-25 12:00 | 12.0351
2022-03-25 13:00 | 12.0351
2022-03-25 14:00 | 12.0351
2022-03-25 15:00 | 12.0351
2022-03-25 16:00 | 12.0351
2022-03-25 17:00 | 9.0628
2022-03-25 18:00 | 4.6971
2022-03-25 19:00 | 4.7001
2022-03-25 20:00 | 4.6632
2022-03-25 21:00 | 4.6533
2022-03-25 22:00 | 4.6623
2022-03-25 23:00 | 4.7387
2022-03-26 | 4.7801
2022-03-26 01:00 | 4.8154
2022-03-26 02:00 | 4.8721
2022-03-26 03:00 | 4.8857
2022-03-26 04:00 | 4.8526
2022-03-26 05:00 | 4.8721
2022-03-26 06:00 | 4.8886
2022-03-26 07:00 | 4.8448
2022-03-26 08:00 | 4.8535
2022-03-26 09:00 | 4.8584
2022-03-26 10:00 | 4.8359
2022-03-26 11:00 | 4.7948
2022-03-26 12:00 | 4.7317
2022-03-26 13:00 | 4.7169
2022-03-26 14:00 | 4.7119
2022-03-26 15:00 | 4.698
2022-03-26 16:00 | 4.704
2022-03-26 17:00 | 4.7208
2022-03-26 18:00 | 4.7771
2022-03-26 19:00 | 4.7308
2022-03-26 20:00 | 4.7288
2022-03-26 21:00 | 4.7495
2022-03-26 22:00 | 4.7426
2022-03-26 23:00 | 4.8085
2022-03-27 | 4.7948
2022-03-27 01:00 | 4.8604
2022-03-27 02:00 | 4.8964
2022-03-27 03:00 | 4.9206
2022-03-27 04:00 | 4.9003
2022-03-27 05:00 | 4.8886
2022-03-27 06:00 | 4.908
2022-03-27 07:00 | 4.9031
2022-03-27 08:00 | 4.9244
2022-03-27 09:00 | 4.8837
2022-03-27 10:00 | 4.8184
2022-03-27 11:00 | 4.7909
2022-03-27 12:00 | 4.788
2022-03-27 13:00 | 4.786
2022-03-27 14:00 | 4.7751
2022-03-27 15:00 | 4.7928
2022-03-27 16:00 | 4.7584
2022-03-27 17:00 | 4.783
2022-03-27 18:00 | 4.8115
2022-03-27 19:00 | 4.8331
2022-03-27 20:00 | 4.8262
2022-03-27 21:00 | 4.8017
2022-03-27 22:00 | 4.8007
2022-03-27 23:00 | 4.8213
2022-03-28 | 4.8496
2022-03-28 01:00 | 4.8555
2022-03-28 02:00 | 4.8701
2022-03-28 03:00 | 4.9031
2022-03-28 04:00 | 4.8867
2022-03-28 05:00 | 4.9128
2022-03-28 06:00 | 12.0351
2022-03-28 07:00 | 12.0351
2022-03-28 08:00 | 12.0351
2022-03-28 09:00 | 12.0351
2022-03-28 10:00 | 12.0351
2022-03-28 11:00 | 12.0351
2022-03-28 12:00 | 12.0351
2022-03-28 13:00 | 12.0351
2022-03-28 14:00 | 12.0351
2022-03-28 15:00 | 12.0351
2022-03-28 16:00 | 12.0351
2022-03-28 17:00 | 9.411
2022-03-28 18:00 | 4.6163
2022-03-28 19:00 | 4.6133
2022-03-28 20:00 | 4.6283
2022-03-28 21:00 | 4.6253
2022-03-28 22:00 | 4.6583
2022-03-28 23:00 | 4.6881
2022-03-29 | 4.7288
2022-03-29 01:00 | 4.7919
2022-03-29 02:00 | 4.8867
2022-03-29 03:00 | 4.9128
2022-03-29 04:00 | 4.9525
2022-03-29 05:00 | 4.9293
2022-03-29 06:00 | 12.0351
2022-03-29 07:00 | 12.0351
2022-03-29 08:00 | 12.0351
2022-03-29 09:00 | 12.0351
2022-03-29 10:00 | 12.0351
2022-03-29 11:00 | 12.0351
2022-03-29 12:00 | 12.0351
2022-03-29 13:00 | 12.0351
2022-03-29 14:00 | 12.0351
2022-03-29 15:00 | 12.0351
2022-03-29 16:00 | 12.0351
2022-03-29 17:00 | 12.0351
2022-03-29 18:00 | 9.7974
2022-03-29 19:00 | 4.8145
2022-03-29 20:00 | 4.7948
2022-03-29 21:00 | 4.8301
2022-03-29 22:00 | 4.8516
2022-03-29 23:00 | 4.8584
2022-03-30 | 4.8701
2022-03-30 01:00 | 4.9254
2022-03-30 02:00 | 4.9437
2022-03-30 03:00 | 4.9351
2022-03-30 04:00 | 4.9457
2022-03-30 05:00 | 4.9244
2022-03-30 06:00 | 12.0351
2022-03-30 07:00 | 12.0351
2022-03-30 08:00 | 12.0351
2022-03-30 09:00 | 12.0351
2022-03-30 10:00 | 12.0351
2022-03-30 11:00 | 12.0351
2022-03-30 12:00 | 12.0351
2022-03-30 13:00 | 12.0351
2022-03-30 14:00 | 12.0351
2022-03-30 15:00 | 12.0351
2022-03-30 16:00 | 12.0351
2022-03-30 17:00 | 12.0351
2022-03-30 18:00 | 12.0351
2022-03-30 19:00 | 12.0351
2022-03-30 20:00 | 8.5305
2022-03-30 21:00 | 4.3605
2022-03-30 22:00 | 4.7899
2022-03-30 23:00 | 4.8017
2022-03-31 | 4.8652
2022-03-31 01:00 | 4.8759
2022-03-31 02:00 | 4.8682
2022-03-31 03:00 | 4.8944
2022-03-31 04:00 | 4.9264
2022-03-31 05:00 | 4.9206
2022-03-31 06:00 | 12.0351
2022-03-31 07:00 | 12.0351
2022-03-31 08:00 | 12.0351
2022-03-31 09:00 | 12.0351
2022-03-31 10:00 | 12.0351
2022-03-31 11:00 | 12.0351
2022-03-31 12:00 | 12.0351
2022-03-31 13:00 | 12.0351
2022-03-31 14:00 | 12.0351
2022-03-31 15:00 | 12.0351
2022-03-31 16:00 | 12.0351
2022-03-31 17:00 | 8.6689
2022-03-31 18:00 | 4.6662
2022-03-31 19:00 | 4.698
2022-03-31 20:00 | 4.6722
2022-03-31 21:00 | 4.6842
2022-03-31 22:00 | 4.6891
2022-03-31 23:00 | 4.7919
2022-04-01 | 4.8203
2022-04-01 01:00 | 4.8711
2022-04-01 02:00 | 4.835
2022-04-01 03:00 | 4.837
2022-04-01 04:00 | 4.8604
2022-04-01 05:00 | 4.8818
2022-04-01 06:00 | 4.9303
2022-04-01 07:00 | 4.8555
2022-04-01 08:00 | 4.8154
2022-04-01 09:00 | 4.8174
2022-04-01 10:00 | 4.7357
2022-04-01 11:00 | 4.6692
2022-04-01 12:00 | 4.6662
2022-04-01 13:00 | 4.7258
2022-04-01 14:00 | 4.7238
2022-04-01 15:00 | 4.6553
2022-04-01 16:00 | 4.6831
2022-04-01 17:00 | 4.7623
2022-04-01 18:00 | 3.925
2022-04-01 19:00 | 0.8851
2022-04-01 20:00 | 0.89983
2022-04-01 21:00 | 0.8988
2022-04-01 22:00 | 0.86635
2022-04-01 23:00 | 0.87127
2022-04-02 | 0.88903
2022-04-02 01:00 | 0.88903
2022-04-02 02:00 | 0.88999
2022-04-02 03:00 | 0.89784
2022-04-02 04:00 | 0.91053
2022-04-02 05:00 | 0.90861
2022-04-02 06:00 | 0.89096
2022-04-02 07:00 | 0.92223
2022-04-02 08:00 | 0.90175
2022-04-02 09:00 | 0.89983
2022-04-02 10:00 | 0.90175
2022-04-02 11:00 | 0.90663
2022-04-02 12:00 | 0.90957
2022-04-02 13:00 | 0.91053
2022-04-02 14:00 | 0.90175
2022-04-02 15:00 | 0.8988
2022-04-02 16:00 | 0.89983
2022-04-02 17:00 | 0.89784
2022-04-02 18:00 | 0.89983
2022-04-02 19:00 | 0.888
2022-04-02 20:00 | 0.87819
2022-04-02 21:00 | 0.8703
2022-04-02 22:00 | 0.89295
2022-04-02 23:00 | 0.88013
2022-04-03 | 0.888
2022-04-03 01:00 | 0.87722
2022-04-03 02:00 | 0.87916
2022-04-03 03:00 | 0.88903
2022-04-03 04:00 | 0.88606
2022-04-03 05:00 | 0.8851
2022-04-03 06:00 | 0.89392
2022-04-03 07:00 | 0.89392
2022-04-03 08:00 | 0.90175
2022-04-03 09:00 | 0.87819
2022-04-03 10:00 | 0.87619
2022-04-03 11:00 | 0.85941
2022-04-03 12:00 | 0.86434
2022-04-03 13:00 | 0.88213
2022-04-03 14:00 | 0.88903
2022-04-03 15:00 | 0.90079
2022-04-03 16:00 | 0.89192
2022-04-03 17:00 | 0.8851
2022-04-03 18:00 | 0.90175
2022-04-03 19:00 | 0.90861
2022-04-03 20:00 | 0.90175
2022-04-03 21:00 | 0.91348
2022-04-03 22:00 | 0.89488
2022-04-03 23:00 | 0.87619
2022-04-04 | 0.89585
2022-04-04 01:00 | 0.88013
2022-04-04 02:00 | 0.90374
2022-04-04 03:00 | 0.89192
2022-04-04 04:00 | 0.89983
2022-04-04 05:00 | 0.91444
2022-04-04 06:00 | 12.0351
2022-04-04 07:00 | 12.0351
2022-04-04 08:00 | 12.0351
2022-04-04 09:00 | 12.0351
2022-04-04 10:00 | 12.0351
2022-04-04 11:00 | 12.0351
2022-04-04 12:00 | 12.0351
2022-04-04 13:00 | 12.0351
2022-04-04 14:00 | 12.0351
2022-04-04 15:00 | 12.0351
2022-04-04 16:00 | 12.0351
2022-04-04 17:00 | 0.8831
2022-04-04 18:00 | 0.8851
2022-04-04 19:00 | 0.86927
2022-04-04 20:00 | 0.88013
2022-04-04 21:00 | 0.88999
2022-04-04 22:00 | 0.89392
2022-04-04 23:00 | 0.87328
2022-04-05 | 0.8831
2022-04-05 01:00 | 0.87819
2022-04-05 02:00 | 0.88606
2022-04-05 03:00 | 0.91936
2022-04-05 04:00 | 0.91156
2022-04-05 05:00 | 0.92714
2022-04-05 06:00 | 12.0351
2022-04-05 07:00 | 12.0351
2022-04-05 08:00 | 12.0351
2022-04-05 09:00 | 12.0351
2022-04-05 10:00 | 12.0351
2022-04-05 11:00 | 12.0351
2022-04-05 12:00 | 12.0351
2022-04-05 13:00 | 12.0351
2022-04-05 14:00 | 12.0351
2022-04-05 15:00 | 12.0351
2022-04-05 16:00 | 12.0351
2022-04-05 17:00 | 0.89392
2022-04-05 18:00 | 0.9047
2022-04-05 19:00 | 0.91053
2022-04-05 20:00 | 0.90567
2022-04-05 21:00 | 0.90765
2022-04-05 22:00 | 0.91156
2022-04-05 23:00 | 0.90861
2022-04-06 | 0.91348
2022-04-06 01:00 | 0.92516
2022-04-06 02:00 | 0.9242
2022-04-06 03:00 | 0.92127
2022-04-06 04:00 | 0.95621
2022-04-06 05:00 | 0.94265
2022-04-06 06:00 | 12.0351
2022-04-06 07:00 | 12.0351
2022-04-06 08:00 | 12.0351
2022-04-06 09:00 | 12.0351
2022-04-06 10:00 | 8.9556
2022-04-06 11:00 | 12.0351
2022-04-06 12:00 | 12.0351
2022-04-06 13:00 | 12.0351
2022-04-06 14:00 | 12.0351
2022-04-06 15:00 | 12.0351
2022-04-06 16:00 | 12.0351
2022-04-06 17:00 | 4.8565
2022-04-06 18:00 | 4.8359
2022-04-06 19:00 | 4.8798
2022-04-06 20:00 | 4.8516
2022-04-06 21:00 | 4.8203
2022-04-06 22:00 | 4.8604
2022-04-06 23:00 | 4.8623
2022-04-07 | 4.8759
2022-04-07 01:00 | 4.9544
2022-04-07 02:00 | 4.9341
2022-04-07 03:00 | 4.9264
2022-04-07 04:00 | 4.9428
2022-04-07 05:00 | 4.9736
2022-04-07 06:00 | 9.8675
2022-04-07 07:00 | 12.0351
2022-04-07 08:00 | 12.0351
2022-04-07 09:00 | 12.0351
2022-04-07 10:00 | 12.0351
2022-04-07 11:00 | 7.3804
2022-04-07 12:00 | 12.0351
2022-04-07 13:00 | 2.1307
2022-04-07 14:00 | 2.1467
2022-04-07 15:00 | 9.1665
2022-04-07 16:00 | 11.8351
2022-04-07 17:00 | 5.2705
2022-04-07 18:00 | 4.7535
2022-04-07 19:00 | 4.8085
2022-04-07 20:00 | 4.8066
2022-04-07 21:00 | 4.7909
2022-04-07 22:00 | 4.8331
2022-04-07 23:00 | 4.7811
2022-04-08 | 4.8623
2022-04-08 01:00 | 4.7238
2022-04-08 02:00 | 4.7958
2022-04-08 03:00 | 4.8046
2022-04-08 04:00 | 4.8418
2022-04-08 05:00 | 4.8594
2022-04-08 06:00 | 7.898
2022-04-08 07:00 | 12.0351
2022-04-08 08:00 | 12.0351
2022-04-08 09:00 | 12.0351
2022-04-08 10:00 | 12.0351
2022-04-08 11:00 | 12.0351
2022-04-08 12:00 | 12.0351
2022-04-08 13:00 | 12.0351
2022-04-08 14:00 | 12.0351
2022-04-08 15:00 | 12.0351
2022-04-08 16:00 | 12.0351
2022-04-08 17:00 | 9.4172
2022-04-08 18:00 | 4.7899
2022-04-08 19:00 | 4.785
2022-04-08 20:00 | 4.7702
2022-04-08 21:00 | 4.7958
2022-04-08 22:00 | 4.7623
2022-04-08 23:00 | 4.787
2022-04-09 | 4.787
2022-04-09 01:00 | 4.8262
2022-04-09 02:00 | 4.8672
2022-04-09 03:00 | 4.9003
2022-04-09 04:00 | 4.8992
2022-04-09 05:00 | 4.8935
2022-04-09 06:00 | 4.908
2022-04-09 07:00 | 4.8896
2022-04-09 08:00 | 4.8281
2022-04-09 09:00 | 4.7997
2022-04-09 10:00 | 4.7811
2022-04-09 11:00 | 4.785
2022-04-09 12:00 | 4.7742
2022-04-09 13:00 | 4.7988
2022-04-09 14:00 | 4.7889
2022-04-09 15:00 | 4.782
2022-04-09 16:00 | 4.7623
2022-04-09 17:00 | 4.7218
2022-04-09 18:00 | 4.7258
2022-04-09 19:00 | 4.7297
2022-04-09 20:00 | 4.7238
2022-04-09 21:00 | 4.6871
2022-04-09 22:00 | 4.6861
2022-04-09 23:00 | 4.7633
2022-04-10 | 4.8954
2022-04-10 01:00 | 4.8896
2022-04-10 02:00 | 4.8818
2022-04-10 03:00 | 4.8905
2022-04-10 04:00 | 4.8857
2022-04-10 05:00 | 4.9022
2022-04-10 06:00 | 4.9099
2022-04-10 07:00 | 4.9611
2022-04-10 08:00 | 4.964
2022-04-10 09:00 | 4.9457
2022-04-10 10:00 | 4.906
2022-04-10 11:00 | 4.8389
2022-04-10 12:00 | 4.7919
2022-04-10 13:00 | 4.7889
2022-04-10 14:00 | 4.782
2022-04-10 15:00 | 4.7693
2022-04-10 16:00 | 4.7771
2022-04-10 17:00 | 4.782
2022-04-10 18:00 | 4.7938
2022-04-10 19:00 | 4.8232
2022-04-10 20:00 | 4.8115
2022-04-10 21:00 | 4.7928
2022-04-10 22:00 | 4.8398
2022-04-10 23:00 | 4.835
2022-04-11 | 4.8652
2022-04-11 01:00 | 4.8847
2022-04-11 02:00 | 4.8992
2022-04-11 03:00 | 4.9206
2022-04-11 04:00 | 4.9679
2022-04-11 05:00 | 4.9707
2022-04-11 06:00 | 9.7511
2022-04-11 07:00 | 12.0351
2022-04-11 08:00 | 12.0351
2022-04-11 09:00 | 12.0351
2022-04-11 10:00 | 12.0351
2022-04-11 11:00 | 12.0351
2022-04-11 12:00 | 12.0351
2022-04-11 13:00 | 12.0351
2022-04-11 14:00 | 12.0351
2022-04-11 15:00 | 12.0351
2022-04-11 16:00 | 12.0351
2022-04-11 17:00 | 8.4223
2022-04-11 18:00 | 4.6053
2022-04-11 19:00 | 4.908
2022-04-11 20:00 | 4.9254
2022-04-11 21:00 | 4.9408
2022-04-11 22:00 | 4.9109
2022-04-11 23:00 | 4.9003
2022-04-12 | 4.9051
2022-04-12 01:00 | 4.8613
2022-04-12 02:00 | 4.8594
2022-04-12 03:00 | 4.8818
2022-04-12 04:00 | 4.874
2022-04-12 05:00 | 4.9293
2022-04-12 06:00 | 4.9322
2022-04-12 07:00 | 4.6473
2022-04-12 08:00 | 4.6543
2022-04-12 09:00 | 4.6453
2022-04-12 10:00 | 4.6224
2022-04-12 11:00 | 4.6093
2022-04-12 12:00 | 4.6093
2022-04-12 13:00 | 4.5692
2022-04-12 14:00 | 4.5783
2022-04-12 15:00 | 4.5732
2022-04-12 16:00 | 4.5783
2022-04-12 17:00 | 4.6523
2022-04-12 18:00 | 4.5813
2022-04-12 19:00 | 4.8448
2022-04-12 20:00 | 4.873
2022-04-12 21:00 | 4.8301
2022-04-12 22:00 | 4.874
2022-04-12 23:00 | 4.8232
2022-04-13 | 4.8643
2022-04-13 01:00 | 4.908
2022-04-13 02:00 | 4.8905
2022-04-13 03:00 | 4.937
2022-04-13 04:00 | 4.8983
2022-04-13 05:00 | 4.9128
2022-04-13 06:00 | 4.9351
2022-04-13 07:00 | 4.702
2022-04-13 08:00 | 4.6543
2022-04-13 09:00 | 4.6293
2022-04-13 10:00 | 4.5601
2022-04-13 11:00 | 4.5149
2022-04-13 12:00 | 4.5088
2022-04-13 13:00 | 4.4663
2022-04-13 14:00 | 4.5088
2022-04-13 15:00 | 4.5098
2022-04-13 16:00 | 3.2035
2022-04-13 17:00 | 0.86434
2022-04-13 18:00 | 0.82855
2022-04-13 19:00 | 0.80545
2022-04-13 20:00 | 0.79837
2022-04-13 21:00 | 0.80849
2022-04-13 22:00 | 0.81046
2022-04-13 23:00 | 0.80043
2022-04-14 | 0.80142
2022-04-14 01:00 | 0.80644
2022-04-14 02:00 | 0.8185
2022-04-14 03:00 | 0.82356
2022-04-14 04:00 | 0.82756
2022-04-14 05:00 | 0.8385
2022-04-14 06:00 | 0.84548
2022-04-14 07:00 | 0.83254
2022-04-14 08:00 | 0.83451
2022-04-14 09:00 | 0.83451
2022-04-14 10:00 | 0.82855
2022-04-14 11:00 | 0.83451
2022-04-14 12:00 | 0.83451
2022-04-14 13:00 | 0.8185
2022-04-14 14:00 | 0.8385
2022-04-14 15:00 | 0.84052
2022-04-14 16:00 | 0.84052
2022-04-14 17:00 | 0.85245
2022-04-14 18:00 | 1.3322
2022-04-14 19:00 | 1.3267
2022-04-14 20:00 | 1.333
2022-04-14 21:00 | 1.3195
2022-04-14 22:00 | 1.3003
2022-04-14 23:00 | 1.3121
2022-04-15 | 1.3076
2022-04-15 01:00 | 1.3322
2022-04-15 02:00 | 1.3195
2022-04-15 03:00 | 1.324
2022-04-15 04:00 | 1.3304
2022-04-15 05:00 | 1.3485
2022-04-15 06:00 | 1.3449
2022-04-15 07:00 | 1.3285
2022-04-15 08:00 | 1.3322
2022-04-15 09:00 | 1.3394
2022-04-15 10:00 | 1.3131
2022-04-15 11:00 | 1.2821
2022-04-15 12:00 | 1.2803
2022-04-15 13:00 | 1.2584
2022-04-15 14:00 | 1.2593
2022-04-15 15:00 | 1.2547
2022-04-15 16:00 | 1.2703
2022-04-15 17:00 | 1.2812
2022-04-15 18:00 | 1.2547
2022-04-15 19:00 | 1.2529
2022-04-15 20:00 | 1.2547
2022-04-15 21:00 | 1.2602
2022-04-15 22:00 | 1.2519
2022-04-15 23:00 | 1.2648
2022-04-16 | 1.304
2022-04-16 01:00 | 1.3121
2022-04-16 02:00 | 1.3131
2022-04-16 03:00 | 1.3167
2022-04-16 04:00 | 1.3058
2022-04-16 05:00 | 1.304
2022-04-16 06:00 | 1.2867
2022-04-16 07:00 | 1.3276
2022-04-16 08:00 | 1.3012
2022-04-16 09:00 | 1.2976
2022-04-16 10:00 | 1.2885
2022-04-16 11:00 | 1.3003
2022-04-16 12:00 | 1.2885
2022-04-16 13:00 | 1.2684
2022-04-16 14:00 | 1.2766
2022-04-16 15:00 | 1.2785
2022-04-16 16:00 | 1.2547
2022-04-16 17:00 | 1.2958
2022-04-16 18:00 | 1.2967
2022-04-16 19:00 | 1.2994
2022-04-16 20:00 | 1.2703
2022-04-16 21:00 | 1.2939
2022-04-16 22:00 | 1.2939
2022-04-16 23:00 | 1.314
2022-04-17 | 1.3022
2022-04-17 01:00 | 1.3012
2022-04-17 02:00 | 1.2976
2022-04-17 03:00 | 1.3067
2022-04-17 04:00 | 1.3185
2022-04-17 05:00 | 1.3222
2022-04-17 06:00 | 1.3485
2022-04-17 07:00 | 1.3503
2022-04-17 08:00 | 1.3521
2022-04-17 09:00 | 1.3558
2022-04-17 10:00 | 1.3413
2022-04-17 11:00 | 1.3394
2022-04-17 12:00 | 1.3621
2022-04-17 13:00 | 1.3222
2022-04-17 14:00 | 1.3204
2022-04-17 15:00 | 1.3349
2022-04-17 16:00 | 1.3067
2022-04-17 17:00 | 1.3385
2022-04-17 18:00 | 1.3185
2022-04-17 19:00 | 1.3249
2022-04-17 20:00 | 1.3285
2022-04-17 21:00 | 1.3349
2022-04-17 22:00 | 1.3195
2022-04-17 23:00 | 1.3121
2022-04-18 | 1.3349
2022-04-18 01:00 | 1.2967
2022-04-18 02:00 | 1.3085
2022-04-18 03:00 | 1.2976
2022-04-18 04:00 | 1.3085
2022-04-18 05:00 | 1.3149
2022-04-18 06:00 | 7.3086
2022-04-18 07:00 | 9.2086
2022-04-18 08:00 | 9.1712
2022-04-18 09:00 | 9.0564
2022-04-18 10:00 | 8.9711
2022-04-18 11:00 | 8.9237
2022-04-18 12:00 | 8.8919
2022-04-18 13:00 | 8.8533
2022-04-18 14:00 | 8.8932
2022-04-18 15:00 | 8.929
2022-04-18 16:00 | 8.9303
2022-04-18 17:00 | 6.1446
2022-04-18 18:00 | 3.4573
2022-04-18 19:00 | 3.4614
2022-04-18 20:00 | 3.4687
2022-04-18 21:00 | 3.4937
2022-04-18 22:00 | 3.4759
2022-04-18 23:00 | 3.4915
2022-04-19 | 3.4843
2022-04-19 01:00 | 3.5291
2022-04-19 02:00 | 3.5228
2022-04-19 03:00 | 3.4687
2022-04-19 04:00 | 3.4999
2022-04-19 05:00 | 3.5113
2022-04-19 06:00 | 8.0566
2022-04-19 07:00 | 12.0351
2022-04-19 08:00 | 12.0351
2022-04-19 09:00 | 12.0351
2022-04-19 10:00 | 12.0351
2022-04-19 11:00 | 12.0351
2022-04-19 12:00 | 12.0351
2022-04-19 13:00 | 12.0351
2022-04-19 14:00 | 12.0351
2022-04-19 15:00 | 12.0351
2022-04-19 16:00 | 12.0351
2022-04-19 17:00 | 12.0351
2022-04-19 18:00 | 12.0351
2022-04-19 19:00 | 4.936
2022-04-19 20:00 | 4.9177
2022-04-19 21:00 | 4.9099
2022-04-19 22:00 | 4.8905
2022-04-19 23:00 | 4.9496
2022-04-20 | 4.9928
2022-04-20 01:00 | 5.0158
2022-04-20 02:00 | 5.151
2022-04-20 03:00 | 5.135
2022-04-20 04:00 | 5.1771
2022-04-20 05:00 | 5.1743
2022-04-20 06:00 | 12.0351
2022-04-20 07:00 | 12.0351
2022-04-20 08:00 | 12.0351
2022-04-20 09:00 | 12.0351
2022-04-20 10:00 | 12.0351
2022-04-20 11:00 | 12.0351
2022-04-20 12:00 | 12.0351
2022-04-20 13:00 | 12.0351
2022-04-20 14:00 | 12.0351
2022-04-20 15:00 | 12.0351
2022-04-20 16:00 | 12.0351
2022-04-20 17:00 | 12.0351
2022-04-20 18:00 | 11.9457
2022-04-20 19:00 | 4.9186
2022-04-20 20:00 | 4.9215
2022-04-20 21:00 | 4.938
2022-04-20 22:00 | 4.9196
2022-04-20 23:00 | 4.9688
2022-04-21 | 4.987
2022-04-21 01:00 | 5.0965
2022-04-21 02:00 | 5.1219
2022-04-21 03:00 | 5.1219
2022-04-21 04:00 | 5.1715
2022-04-21 05:00 | 5.1837
2022-04-21 06:00 | 7.8452
2022-04-21 07:00 | 12.0351
2022-04-21 08:00 | 12.0351
2022-04-21 09:00 | 12.0351
2022-04-21 10:00 | 12.0351
2022-04-21 11:00 | 12.0351
2022-04-21 12:00 | 12.0351
2022-04-21 13:00 | 12.0351
2022-04-21 14:00 | 12.0351
2022-04-21 15:00 | 12.0351
2022-04-21 16:00 | 12.0351
2022-04-21 17:00 | 12.0351
2022-04-21 18:00 | 12.0351
2022-04-21 19:00 | 4.9419
2022-04-21 20:00 | 4.9225
2022-04-21 21:00 | 4.9457
2022-04-21 22:00 | 4.8954
2022-04-21 23:00 | 4.8643
2022-04-22 | 4.8467
2022-04-22 01:00 | 4.8808
2022-04-22 02:00 | 4.9158
2022-04-22 03:00 | 4.9399
2022-04-22 04:00 | 4.9736
2022-04-22 05:00 | 5.0291
2022-04-22 06:00 | 12.0351
2022-04-22 07:00 | 12.0351
2022-04-22 08:00 | 12.0351
2022-04-22 09:00 | 12.0351
2022-04-22 10:00 | 12.0351
2022-04-22 11:00 | 12.0351
2022-04-22 12:00 | 12.0351
2022-04-22 13:00 | 12.0351
2022-04-22 14:00 | 12.0351
2022-04-22 15:00 | 12.0351
2022-04-22 16:00 | 12.0351
2022-04-22 17:00 | 12.0351
2022-04-22 18:00 | 8.1323
2022-04-22 19:00 | 4.8983
2022-04-22 20:00 | 4.8604
2022-04-22 21:00 | 4.907
2022-04-22 22:00 | 4.9351
2022-04-22 23:00 | 4.9235
2022-04-23 | 4.9322
2022-04-23 01:00 | 5.0548
2022-04-23 02:00 | 5.0339
2022-04-23 03:00 | 5.0415
2022-04-23 04:00 | 5.0462
2022-04-23 05:00 | 5.087
2022-04-23 06:00 | 5.0861
2022-04-23 07:00 | 5.0965
2022-04-23 08:00 | 5.0614
2022-04-23 09:00 | 5.0377
2022-04-23 10:00 | 5.012
2022-04-23 11:00 | 5.0081
2022-04-23 12:00 | 5.0091
2022-04-23 13:00 | 4.9563
2022-04-23 14:00 | 4.9765
2022-04-23 15:00 | 4.9823
2022-04-23 16:00 | 4.9679
2022-04-23 17:00 | 4.9592
2022-04-23 18:00 | 4.9823
2022-04-23 19:00 | 4.9602
2022-04-23 20:00 | 4.9688
2022-04-23 21:00 | 5.0091
2022-04-23 22:00 | 5.0004
2022-04-23 23:00 | 5.0004
2022-04-24 | 5.0091
2022-04-24 01:00 | 5.0158
2022-04-24 02:00 | 5.0033
2022-04-24 03:00 | 5.0196
2022-04-24 04:00 | 5.0253
2022-04-24 05:00 | 5.0167
2022-04-24 06:00 | 5.0253
2022-04-24 07:00 | 5.0301
2022-04-24 08:00 | 5.0415
2022-04-24 09:00 | 5.0405
2022-04-24 10:00 | 5.0329
2022-04-24 11:00 | 5.0148
2022-04-24 12:00 | 4.9437
2022-04-24 13:00 | 4.9956
2022-04-24 14:00 | 4.9679
2022-04-24 15:00 | 4.9389
2022-04-24 16:00 | 4.9525
2022-04-24 17:00 | 4.9928
2022-04-24 18:00 | 5.0014
2022-04-24 19:00 | 5.0033
2022-04-24 20:00 | 4.9889
2022-04-24 21:00 | 4.9457
2022-04-24 22:00 | 4.9745
2022-04-24 23:00 | 4.9563
2022-04-25 | 4.9899
2022-04-25 01:00 | 5.0415
2022-04-25 02:00 | 5.0681
2022-04-25 03:00 | 5.0974
2022-04-25 04:00 | 5.0993
2022-04-25 05:00 | 5.1144
2022-04-25 06:00 | 12.0351
2022-04-25 07:00 | 12.0351
2022-04-25 08:00 | 12.0351
2022-04-25 09:00 | 12.0351
2022-04-25 10:00 | 12.0351
2022-04-25 11:00 | 12.0351
2022-04-25 12:00 | 12.0351
2022-04-25 13:00 | 12.0351
2022-04-25 14:00 | 12.0351
2022-04-25 15:00 | 12.0351
2022-04-25 16:00 | 12.0351
2022-04-25 17:00 | 12.0351
2022-04-25 18:00 | 4.7683
2022-04-25 19:00 | 4.9399
2022-04-25 20:00 | 4.9186
2022-04-25 21:00 | 4.9138
2022-04-25 22:00 | 4.9861
2022-04-25 23:00 | 4.9602
2022-04-26 | 4.9515
2022-04-26 01:00 | 5.0272
2022-04-26 02:00 | 5.0205
2022-04-26 03:00 | 5.0205
2022-04-26 04:00 | 5.0538
2022-04-26 05:00 | 5.0785
2022-04-26 06:00 | 5.0396
2022-04-26 07:00 | 4.8379
2022-04-26 08:00 | 4.7683
2022-04-26 09:00 | 4.7762
2022-04-26 10:00 | 4.7693
2022-04-26 11:00 | 4.7327
2022-04-26 12:00 | 4.704
2022-04-26 13:00 | 4.6602
2022-04-26 14:00 | 4.6792
2022-04-26 15:00 | 4.6593
2022-04-26 16:00 | 4.8905
2022-04-26 17:00 | 4.964
2022-04-26 18:00 | 2.9721
2022-04-26 19:00 | 0.91738
2022-04-26 20:00 | 0.93878
2022-04-26 21:00 | 0.92127
2022-04-26 22:00 | 0.92714
2022-04-26 23:00 | 0.90861
2022-04-27 | 0.91833
2022-04-27 01:00 | 0.92905
2022-04-27 02:00 | 0.9436
2022-04-27 03:00 | 0.95425
2022-04-27 04:00 | 0.94652
2022-04-27 05:00 | 0.96196
2022-04-27 06:00 | 0.95716
2022-04-27 07:00 | 0.93783
2022-04-27 08:00 | 0.93681
2022-04-27 09:00 | 0.8988
2022-04-27 10:00 | 0.89585
2022-04-27 11:00 | 0.90861
2022-04-27 12:00 | 0.89585
2022-04-27 13:00 | 0.88999
2022-04-27 14:00 | 0.89585
2022-04-27 15:00 | 0.88116
2022-04-27 16:00 | 0.89983
2022-04-27 17:00 | 0.91833
2022-04-27 18:00 | 0.91348
2022-04-27 19:00 | 2.4501
2022-04-27 20:00 | 2.8677
2022-04-27 21:00 | 2.8123
2022-04-27 22:00 | 2.8304
2022-04-27 23:00 | 2.8636
2022-04-28 | 2.8606
2022-04-28 01:00 | 2.9081
2022-04-28 02:00 | 2.896
2022-04-28 03:00 | 2.9528
2022-04-28 04:00 | 2.9609
2022-04-28 05:00 | 3.0046
2022-04-28 06:00 | 12.0351
2022-04-28 07:00 | 12.0351
2022-04-28 08:00 | 12.0351
2022-04-28 09:00 | 12.0351
2022-04-28 10:00 | 12.0351
2022-04-28 11:00 | 12.0351
2022-04-28 12:00 | 12.0351
2022-04-28 13:00 | 12.0351
2022-04-28 14:00 | 12.0351
2022-04-28 15:00 | 12.0351
2022-04-28 16:00 | 12.0351
2022-04-28 17:00 | 12.0351
2022-04-28 18:00 | 12.0351
2022-04-28 19:00 | 7.6958
2022-04-28 20:00 | 4.8973
2022-04-28 21:00 | 4.9051
2022-04-28 22:00 | 4.8779
2022-04-28 23:00 | 4.9051
2022-04-29 | 4.937
2022-04-29 01:00 | 4.963
2022-04-29 02:00 | 4.964
2022-04-29 03:00 | 4.9918
2022-04-29 04:00 | 5.01
2022-04-29 05:00 | 5.0586
2022-04-29 06:00 | 12.0351
2022-04-29 07:00 | 12.0351
2022-04-29 08:00 | 12.0351
2022-04-29 09:00 | 12.0351
2022-04-29 10:00 | 12.0351
2022-04-29 11:00 | 12.0351
2022-04-29 12:00 | 12.0351
2022-04-29 13:00 | 12.0351
2022-04-29 14:00 | 12.0351
2022-04-29 15:00 | 12.0351
2022-04-29 16:00 | 12.0351
2022-04-29 17:00 | 9.8718
2022-04-29 18:00 | 4.6114
2022-04-29 19:00 | 4.8954
2022-04-29 20:00 | 4.8759
2022-04-29 21:00 | 4.9186
2022-04-29 22:00 | 4.9031
2022-04-29 23:00 | 4.938
2022-04-30 | 4.9726
2022-04-30 01:00 | 5.0291
2022-04-30 02:00 | 5.0301
2022-04-30 03:00 | 5.0443
2022-04-30 04:00 | 5.0215
2022-04-30 05:00 | 5.0415
2022-04-30 06:00 | 5.0766
2022-04-30 07:00 | 5.0662
2022-04-30 08:00 | 5.0176
2022-04-30 09:00 | 5.032
2022-04-30 10:00 | 5.0043
2022-04-30 11:00 | 4.9408
2022-04-30 12:00 | 4.9486
2022-04-30 13:00 | 4.9283
2022-04-30 14:00 | 4.9389
2022-04-30 15:00 | 4.9351
2022-04-30 16:00 | 4.9496
2022-04-30 17:00 | 4.9341
2022-04-30 18:00 | 4.8924
2022-04-30 19:00 | 4.965
2022-04-30 20:00 | 4.9668
2022-04-30 21:00 | 4.9947
2022-04-30 22:00 | 4.9813
2022-04-30 23:00 | 5.0071
2022-05-01 | 5.0186
2022-05-01 01:00 | 5.0358
2022-05-01 02:00 | 5.0158
2022-05-01 03:00 | 5.0138
2022-05-01 04:00 | 5.0955
2022-05-01 05:00 | 5.087
2022-05-01 06:00 | 5.0794
2022-05-01 07:00 | 5.0946
2022-05-01 08:00 | 4.9351
2022-05-01 09:00 | 4.9293
2022-05-01 10:00 | 4.9341
2022-05-01 11:00 | 4.9419
2022-05-01 12:00 | 4.964
2022-05-01 13:00 | 4.9196
2022-05-01 14:00 | 4.9022
2022-05-01 15:00 | 4.9109
2022-05-01 16:00 | 4.9177
2022-05-01 17:00 | 4.9206
2022-05-01 18:00 | 4.9235
2022-05-01 19:00 | 4.9177
2022-05-01 20:00 | 4.9534
2022-05-01 21:00 | 4.9525
2022-05-01 22:00 | 4.9774
2022-05-01 23:00 | 4.9457
2022-05-02 | 5.0329
2022-05-02 01:00 | 5.0282
2022-05-02 02:00 | 5.0148
2022-05-02 03:00 | 5.0205
2022-05-02 04:00 | 4.9976
2022-05-02 05:00 | 5.0234
2022-05-02 06:00 | 5.0955
2022-05-02 07:00 | 4.8242
2022-05-02 08:00 | 4.8223
2022-05-02 09:00 | 4.7614
2022-05-02 10:00 | 4.7297
2022-05-02 11:00 | 4.7169
2022-05-02 12:00 | 4.7574
2022-05-02 13:00 | 4.9592
2022-05-02 14:00 | 4.9553
2022-05-02 15:00 | 4.9437
2022-05-02 16:00 | 4.9389
2022-05-02 17:00 | 5.0004
2022-05-02 18:00 | 5.0109
2022-05-02 19:00 | 5.0176
2022-05-02 20:00 | 5.0472
2022-05-02 21:00 | 5.0443
2022-05-02 22:00 | 5.0215
2022-05-02 23:00 | 4.9947
2022-05-03 | 5.0415
2022-05-03 01:00 | 5.0908
2022-05-03 02:00 | 5.0681
2022-05-03 03:00 | 5.0983
2022-05-03 04:00 | 5.1219
2022-05-03 05:00 | 5.1049
2022-05-03 06:00 | 5.1191
2022-05-03 07:00 | 4.8944
2022-05-03 08:00 | 4.8301
2022-05-03 09:00 | 4.7702
2022-05-03 10:00 | 4.7387
2022-05-03 11:00 | 4.7426
2022-05-03 12:00 | 4.7446
2022-05-03 13:00 | 4.6961
2022-05-03 14:00 | 4.7258
2022-05-03 15:00 | 4.6931
2022-05-03 16:00 | 4.6871
2022-05-03 17:00 | 4.7771
2022-05-03 18:00 | 4.7456
2022-05-03 19:00 | 5.0358
2022-05-03 20:00 | 5.0071
2022-05-03 21:00 | 4.963
2022-05-03 22:00 | 4.9312
2022-05-03 23:00 | 4.9563
2022-05-04 | 5.0301
2022-05-04 01:00 | 5.0234
2022-05-04 02:00 | 5.0672
2022-05-04 03:00 | 5.0785
2022-05-04 04:00 | 5.1238
2022-05-04 05:00 | 5.1125
2022-05-04 06:00 | 5.1304
2022-05-04 07:00 | 4.8808
2022-05-04 08:00 | 4.8448
2022-05-04 09:00 | 4.7545
2022-05-04 10:00 | 4.7278
2022-05-04 11:00 | 4.7574
2022-05-04 12:00 | 4.7416
2022-05-04 13:00 | 4.7633
2022-05-04 14:00 | 4.7396
2022-05-04 15:00 | 4.7189
2022-05-04 16:00 | 4.7327
2022-05-04 17:00 | 4.7584
2022-05-04 18:00 | 4.7268
2022-05-04 19:00 | 4.9573
2022-05-04 20:00 | 4.9573
2022-05-04 21:00 | 4.9668
2022-05-04 22:00 | 4.9457
2022-05-04 23:00 | 4.9803
2022-05-05 | 5.0158
2022-05-05 01:00 | 4.9592
2022-05-05 02:00 | 5.0024
2022-05-05 03:00 | 4.987
2022-05-05 04:00 | 4.9899
2022-05-05 05:00 | 5.0205
2022-05-05 06:00 | 5.0491
2022-05-05 07:00 | 5.0453
2022-05-05 08:00 | 5.0196
2022-05-05 09:00 | 4.9486
2022-05-05 10:00 | 4.8759
2022-05-05 11:00 | 4.8672
2022-05-05 12:00 | 4.8759
2022-05-05 13:00 | 4.8506
2022-05-05 14:00 | 4.8565
2022-05-05 15:00 | 4.8526
2022-05-05 16:00 | 4.8184
2022-05-05 17:00 | 4.8701
2022-05-05 18:00 | 4.8389
2022-05-05 19:00 | 4.9158
2022-05-05 20:00 | 4.8896
2022-05-05 21:00 | 4.936
2022-05-05 22:00 | 4.9717
2022-05-05 23:00 | 4.907
2022-05-06 | 4.8924
2022-05-06 01:00 | 4.9486
2022-05-06 02:00 | 4.9167
2022-05-06 03:00 | 4.9621
2022-05-06 04:00 | 4.9947
2022-05-06 05:00 | 4.9803
2022-05-06 06:00 | 5.0062
2022-05-06 07:00 | 4.988
2022-05-06 08:00 | 4.9553
2022-05-06 09:00 | 4.9813
2022-05-06 10:00 | 4.9437
2022-05-06 11:00 | 4.9109
2022-05-06 12:00 | 4.8992
2022-05-06 13:00 | 4.9496
2022-05-06 14:00 | 4.9515
2022-05-06 15:00 | 4.8992
2022-05-06 16:00 | 4.9408
2022-05-06 17:00 | 4.9679
2022-05-06 18:00 | 4.9437
2022-05-06 19:00 | 4.9215
2022-05-06 20:00 | 4.9147
2022-05-06 21:00 | 4.9774
2022-05-06 22:00 | 4.9428
2022-05-06 23:00 | 4.9167
2022-05-07 | 4.9928
2022-05-07 01:00 | 5.0109
2022-05-07 02:00 | 5.0291
2022-05-07 03:00 | 5.0196
2022-05-07 04:00 | 5.0071
2022-05-07 05:00 | 5.012
2022-05-07 06:00 | 5.012
2022-05-07 07:00 | 5.05
2022-05-07 08:00 | 5.0766
2022-05-07 09:00 | 5.0681
2022-05-07 10:00 | 4.9938
2022-05-07 11:00 | 5.0091
2022-05-07 12:00 | 5.0091
2022-05-07 13:00 | 5.0282
2022-05-07 14:00 | 5.0109
2022-05-07 15:00 | 4.9794
2022-05-07 16:00 | 4.9918
2022-05-07 17:00 | 5.0062
2022-05-07 18:00 | 4.9985
2022-05-07 19:00 | 4.9889
2022-05-07 20:00 | 5.0033
2022-05-07 21:00 | 5.0062
2022-05-07 22:00 | 5.0129
2022-05-07 23:00 | 5.0081
2022-05-08 | 5.0291
2022-05-08 01:00 | 5.0993
2022-05-08 02:00 | 5.0728
2022-05-08 03:00 | 4.963
2022-05-08 04:00 | 5.0624
2022-05-08 05:00 | 5.0879
2022-05-08 06:00 | 5.1106
2022-05-08 07:00 | 5.1322
2022-05-08 08:00 | 5.1388
2022-05-08 09:00 | 5.1388
2022-05-08 10:00 | 5.0386
2022-05-08 11:00 | 4.9679
2022-05-08 12:00 | 4.9726
2022-05-08 13:00 | 4.9611
2022-05-08 14:00 | 4.9419
2022-05-08 15:00 | 4.9611
2022-05-08 16:00 | 4.9486
2022-05-08 17:00 | 4.9457
2022-05-08 18:00 | 4.9553
2022-05-08 19:00 | 5.0024
2022-05-08 20:00 | 5.0129
2022-05-08 21:00 | 4.9755
2022-05-08 22:00 | 4.9736
2022-05-08 23:00 | 5.0167
2022-05-09 | 5.0386
2022-05-09 01:00 | 4.9899
2022-05-09 02:00 | 4.9774
2022-05-09 03:00 | 5.1144
2022-05-09 04:00 | 5.0842
2022-05-09 05:00 | 5.1453
2022-05-09 06:00 | 5.1603
2022-05-09 07:00 | 8.0279
2022-05-09 08:00 | 12.0351
2022-05-09 09:00 | 12.0351
2022-05-09 10:00 | 12.0351
2022-05-09 11:00 | 12.0351
2022-05-09 12:00 | 12.0351
2022-05-09 13:00 | 12.0351
2022-05-09 14:00 | 12.0351
2022-05-09 15:00 | 12.0351
2022-05-09 16:00 | 12.0351
2022-05-09 17:00 | 12.0351
2022-05-09 18:00 | 7.1334
2022-05-09 19:00 | 4.964
2022-05-09 20:00 | 4.9976
2022-05-09 21:00 | 5.0109
2022-05-09 22:00 | 4.9697
2022-05-09 23:00 | 5.0262
2022-05-10 | 5.0205
2022-05-10 01:00 | 5.0453
2022-05-10 02:00 | 5.0519
2022-05-10 03:00 | 5.0681
2022-05-10 04:00 | 5.0643
2022-05-10 05:00 | 5.0917
2022-05-10 06:00 | 5.1219
2022-05-10 07:00 | 4.8944
2022-05-10 08:00 | 4.8983
2022-05-10 09:00 | 4.7889
2022-05-10 10:00 | 4.7238
2022-05-10 11:00 | 4.6921
2022-05-10 12:00 | 4.6782
2022-05-10 13:00 | 4.6742
2022-05-10 14:00 | 4.6861
2022-05-10 15:00 | 4.6752
2022-05-10 16:00 | 4.695
2022-05-10 17:00 | 4.695
2022-05-10 18:00 | 4.695
2022-05-10 19:00 | 5.0519
2022-05-10 20:00 | 5.0329
2022-05-10 21:00 | 5.0176
2022-05-10 22:00 | 5.0558
2022-05-10 23:00 | 5.0348
2022-05-11 | 5.1284
2022-05-11 01:00 | 5.1228
2022-05-11 02:00 | 5.1144
2022-05-11 03:00 | 5.0917
2022-05-11 04:00 | 5.1547
2022-05-11 05:00 | 5.1622
2022-05-11 06:00 | 5.1948
2022-05-11 07:00 | 4.834
2022-05-11 08:00 | 4.8223
2022-05-11 09:00 | 4.7889
2022-05-11 10:00 | 4.7406
2022-05-11 11:00 | 4.7525
2022-05-11 12:00 | 4.7347
2022-05-11 13:00 | 4.7771
2022-05-11 14:00 | 4.7485
2022-05-11 15:00 | 4.7426
2022-05-11 16:00 | 4.7367
2022-05-11 17:00 | 4.7653
2022-05-11 18:00 | 4.6871
2022-05-11 19:00 | 5.0367
2022-05-11 20:00 | 5.0224
2022-05-11 21:00 | 5.0424
2022-05-11 22:00 | 5.0757
2022-05-11 23:00 | 5.104
2022-05-12 | 5.103
2022-05-12 01:00 | 5.0936
2022-05-12 02:00 | 5.0367
2022-05-12 03:00 | 5.0737
2022-05-12 04:00 | 5.1106
2022-05-12 05:00 | 5.0946
2022-05-12 06:00 | 12.19
2022-05-12 07:00 | 12.0351
2022-05-12 08:00 | 12.0351
2022-05-12 09:00 | 12.0351
2022-05-12 10:00 | 12.0351
2022-05-12 11:00 | 12.0351
2022-05-12 12:00 | 12.0351
2022-05-12 13:00 | 12.0351
2022-05-12 14:00 | 12.0351
2022-05-12 15:00 | 12.0351
2022-05-12 16:00 | 12.0351
2022-05-12 17:00 | 12.0351
2022-05-12 18:00 | 7.6049
2022-05-12 19:00 | 0.96006
2022-05-12 20:00 | 0.96776
2022-05-12 21:00 | 0.98601
2022-05-12 22:00 | 0.97444
2022-05-12 23:00 | 0.98218
2022-05-13 | 0.97734
2022-05-13 01:00 | 0.98218
2022-05-13 02:00 | 0.985
2022-05-13 03:00 | 0.9706
2022-05-13 04:00 | 0.97161
2022-05-13 05:00 | 1.0051
2022-05-13 06:00 | 0.99366
2022-05-13 07:00 | 0.96006
2022-05-13 08:00 | 0.96291
2022-05-13 09:00 | 0.94068
2022-05-13 10:00 | 0.90861
2022-05-13 11:00 | 0.92618
2022-05-13 12:00 | 0.91936
2022-05-13 13:00 | 0.91642
2022-05-13 14:00 | 0.91833
2022-05-13 15:00 | 0.90374
2022-05-13 16:00 | 0.90957
2022-05-13 17:00 | 1.0582
2022-05-13 18:00 | 1.6142
2022-05-13 19:00 | 1.6413
2022-05-13 20:00 | 1.6241
2022-05-13 21:00 | 1.635
2022-05-13 22:00 | 1.6567
2022-05-13 23:00 | 1.6549
2022-05-14 | 1.6458
2022-05-14 01:00 | 1.644
2022-05-14 02:00 | 1.6639
2022-05-14 03:00 | 1.6575
2022-05-14 04:00 | 1.6367
2022-05-14 05:00 | 1.6395
2022-05-14 06:00 | 1.6449
2022-05-14 07:00 | 1.6467
2022-05-14 08:00 | 1.6386
2022-05-14 09:00 | 1.6494
2022-05-14 10:00 | 1.6694
2022-05-14 11:00 | 1.6838
2022-05-14 12:00 | 1.6503
2022-05-14 13:00 | 1.6612
2022-05-14 14:00 | 1.6539
2022-05-14 15:00 | 1.653
2022-05-14 16:00 | 1.6666
2022-05-14 17:00 | 1.6494
2022-05-14 18:00 | 1.6476
2022-05-14 19:00 | 1.6377
2022-05-14 20:00 | 1.6648
2022-05-14 21:00 | 1.6721
2022-05-14 22:00 | 1.6766
2022-05-14 23:00 | 1.6594
2022-05-15 | 1.644
2022-05-15 01:00 | 1.6205
2022-05-15 02:00 | 1.6232
2022-05-15 03:00 | 1.625
2022-05-15 04:00 | 1.6413
2022-05-15 05:00 | 1.6268
2022-05-15 06:00 | 1.6205
2022-05-15 07:00 | 1.6503
2022-05-15 08:00 | 1.6449
2022-05-15 09:00 | 1.6313
2022-05-15 10:00 | 1.6386
2022-05-15 11:00 | 1.6467
2022-05-15 12:00 | 1.6575
2022-05-15 13:00 | 1.6322
2022-05-15 14:00 | 1.6575
2022-05-15 15:00 | 1.6784
2022-05-15 16:00 | 1.6721
2022-05-15 17:00 | 1.6639
2022-05-15 18:00 | 1.6657
2022-05-15 19:00 | 1.6802
2022-05-15 20:00 | 1.6404
2022-05-15 21:00 | 1.6286
2022-05-15 22:00 | 1.6711
2022-05-15 23:00 | 1.6367
2022-05-16 | 1.6386
2022-05-16 01:00 | 1.6214
2022-05-16 02:00 | 1.6313
2022-05-16 03:00 | 1.6087
2022-05-16 04:00 | 1.6431
2022-05-16 05:00 | 1.6549
2022-05-16 06:00 | 4.5662
2022-05-16 07:00 | 12.0351
2022-05-16 08:00 | 12.0351
2022-05-16 09:00 | 12.0351
2022-05-16 10:00 | 12.0351
2022-05-16 11:00 | 12.0351
2022-05-16 12:00 | 12.0351
2022-05-16 13:00 | 12.0351
2022-05-16 14:00 | 12.0351
2022-05-16 15:00 | 12.0351
2022-05-16 16:00 | 12.0351
2022-05-16 17:00 | 12.0351
2022-05-16 18:00 | 4.9031
2022-05-16 19:00 | 4.8992
2022-05-16 20:00 | 4.9668
2022-05-16 21:00 | 4.909
2022-05-16 22:00 | 4.9457
2022-05-16 23:00 | 4.9283
2022-05-17 | 4.9947
2022-05-17 01:00 | 4.8944
2022-05-17 02:00 | 4.9707
2022-05-17 03:00 | 5.0224
2022-05-17 04:00 | 5.0329
2022-05-17 05:00 | 5.0158
2022-05-17 06:00 | 12.0351
2022-05-17 07:00 | 12.0351
2022-05-17 08:00 | 12.0351
2022-05-17 09:00 | 12.0351
2022-05-17 10:00 | 12.0351
2022-05-17 11:00 | 12.0351
2022-05-17 12:00 | 12.0351
2022-05-17 13:00 | 12.0351
2022-05-17 14:00 | 12.0351
2022-05-17 15:00 | 12.0351
2022-05-17 16:00 | 12.0351
2022-05-17 17:00 | 12.0351
2022-05-17 18:00 | 10.1685
2022-05-17 19:00 | 4.834
2022-05-17 20:00 | 4.8828
2022-05-17 21:00 | 4.8818
2022-05-17 22:00 | 4.8496
2022-05-17 23:00 | 4.8652
2022-05-18 | 4.937
2022-05-18 01:00 | 4.9322
2022-05-18 02:00 | 4.908
2022-05-18 03:00 | 4.9196
2022-05-18 04:00 | 4.9515
2022-05-18 05:00 | 4.9408
2022-05-18 06:00 | 12.0351
2022-05-18 07:00 | 12.0351
2022-05-18 08:00 | 12.0351
2022-05-18 09:00 | 12.0351
2022-05-18 10:00 | 12.0351
2022-05-18 11:00 | 12.0351
2022-05-18 12:00 | 12.0351
2022-05-18 13:00 | 12.0351
2022-05-18 14:00 | 2.9487
2022-05-18 15:00 | 12.0351
2022-05-18 16:00 | 12.0351
2022-05-18 17:00 | 0.90079
2022-05-18 18:00 | 0.89488
2022-05-18 19:00 | 0.93395
2022-05-18 20:00 | 0.91546
2022-05-18 21:00 | 0.93198
2022-05-18 22:00 | 0.91546
2022-05-18 23:00 | 0.88703
2022-05-19 | 0.91348
2022-05-19 01:00 | 0.92223
2022-05-19 02:00 | 0.90272
2022-05-19 03:00 | 0.89585
2022-05-19 04:00 | 0.91156
2022-05-19 05:00 | 0.9349
2022-05-19 06:00 | 12.0351
2022-05-19 07:00 | 12.0351
2022-05-19 08:00 | 12.0351
2022-05-19 09:00 | 12.0351
2022-05-19 10:00 | 12.0351
2022-05-19 11:00 | 12.0351
2022-05-19 12:00 | 12.0351
2022-05-19 13:00 | 12.0351
2022-05-19 14:00 | 12.0351
2022-05-19 15:00 | 12.0351
2022-05-19 16:00 | 12.0351
2022-05-19 17:00 | 12.0351
2022-05-19 18:00 | 2.7381
2022-05-19 19:00 | 2.897
2022-05-19 20:00 | 2.8667
2022-05-19 21:00 | 2.8899
2022-05-19 22:00 | 2.8606
2022-05-19 23:00 | 2.8515
2022-05-20 | 2.8606
2022-05-20 01:00 | 2.899
2022-05-20 02:00 | 2.9021
2022-05-20 03:00 | 2.9284
2022-05-20 04:00 | 2.9518
2022-05-20 05:00 | 2.9365
2022-05-20 06:00 | 12.0351
2022-05-20 07:00 | 12.0351
2022-05-20 08:00 | 12.0351
2022-05-20 09:00 | 12.0351
2022-05-20 10:00 | 12.0351
2022-05-20 11:00 | 12.0351
2022-05-20 12:00 | 12.0351
2022-05-20 13:00 | 12.0351
2022-05-20 14:00 | 12.0351
2022-05-20 15:00 | 12.0351
2022-05-20 16:00 | 12.0351
2022-05-20 17:00 | 12.0351
2022-05-20 18:00 | 11.5232
2022-05-20 19:00 | 2.9233
2022-05-20 20:00 | 2.894
2022-05-20 21:00 | 2.8657
2022-05-20 22:00 | 2.8738
2022-05-20 23:00 | 2.8364
2022-05-21 | 2.8354
2022-05-21 01:00 | 2.8667
2022-05-21 02:00 | 2.8364
2022-05-21 03:00 | 2.8536
2022-05-21 04:00 | 2.8727
2022-05-21 05:00 | 2.8606
2022-05-21 06:00 | 2.8687
2022-05-21 07:00 | 2.8859
2022-05-21 08:00 | 2.9314
2022-05-21 09:00 | 2.9081
2022-05-21 10:00 | 2.893
2022-05-21 11:00 | 2.8717
2022-05-21 12:00 | 2.8879
2022-05-21 13:00 | 2.8657
2022-05-21 14:00 | 2.8798
2022-05-21 15:00 | 2.8909
2022-05-21 16:00 | 2.8838
2022-05-21 17:00 | 2.8828
2022-05-21 18:00 | 2.8767
2022-05-21 19:00 | 2.8677
2022-05-21 20:00 | 2.8677
2022-05-21 21:00 | 2.8475
2022-05-21 22:00 | 2.8506
2022-05-21 23:00 | 2.8767
2022-05-22 | 2.8586
2022-05-22 01:00 | 2.8153
2022-05-22 02:00 | 2.8243
2022-05-22 03:00 | 2.7581
2022-05-22 04:00 | 2.7802
2022-05-22 05:00 | 2.7561
2022-05-22 06:00 | 2.7751
2022-05-22 07:00 | 2.8143
2022-05-22 08:00 | 2.8173
2022-05-22 09:00 | 2.7541
2022-05-22 10:00 | 2.7711
2022-05-22 11:00 | 2.7651
2022-05-22 12:00 | 2.7922
2022-05-22 13:00 | 2.8022
2022-05-22 14:00 | 2.8113
2022-05-22 15:00 | 2.8042
2022-05-22 16:00 | 2.8163
2022-05-22 17:00 | 2.8102
2022-05-22 18:00 | 2.7751
2022-05-22 19:00 | 2.8083
2022-05-22 20:00 | 2.7741
2022-05-22 21:00 | 2.7701
2022-05-22 22:00 | 2.7691
2022-05-22 23:00 | 2.7731
2022-05-23 | 2.7812
2022-05-23 01:00 | 2.7511
2022-05-23 02:00 | 2.7611
2022-05-23 03:00 | 2.7791
2022-05-23 04:00 | 2.7731
2022-05-23 05:00 | 2.8083
2022-05-23 06:00 | 11.5958
2022-05-23 07:00 | 12.0351
2022-05-23 08:00 | 12.0351
2022-05-23 09:00 | 12.0351
2022-05-23 10:00 | 12.0351
2022-05-23 11:00 | 12.0351
2022-05-23 12:00 | 12.0351
2022-05-23 13:00 | 12.0351
2022-05-23 14:00 | 12.0351
2022-05-23 15:00 | 12.0351
2022-05-23 16:00 | 12.0351
2022-05-23 17:00 | 12.0351
2022-05-23 18:00 | 2.7521
2022-05-23 19:00 | 2.7611
2022-05-23 20:00 | 2.7531
2022-05-23 21:00 | 2.7451
2022-05-23 22:00 | 2.8284
2022-05-23 23:00 | 2.8274
2022-05-24 | 2.8314
2022-05-24 01:00 | 2.8133
2022-05-24 02:00 | 2.7992
2022-05-24 03:00 | 2.8495
2022-05-24 04:00 | 2.8596
2022-05-24 05:00 | 2.8889
2022-05-24 06:00 | 12.0351
2022-05-24 07:00 | 12.0351
2022-05-24 08:00 | 12.0351
2022-05-24 09:00 | 12.0351
2022-05-24 10:00 | 12.0351
2022-05-24 11:00 | 12.0351
2022-05-24 12:00 | 12.0351
2022-05-24 13:00 | 12.0351
2022-05-24 14:00 | 12.0351
2022-05-24 15:00 | 12.0351
2022-05-24 16:00 | 12.0351
2022-05-24 17:00 | 5.1688
2022-05-24 18:00 | 0.89687
2022-05-24 19:00 | 0.89488
2022-05-24 20:00 | 0.89983
2022-05-24 21:00 | 0.91053
2022-05-24 22:00 | 0.91642
2022-05-24 23:00 | 0.92223
2022-05-25 | 0.90374
2022-05-25 01:00 | 0.92516
2022-05-25 02:00 | 0.93395
2022-05-25 03:00 | 0.94842
2022-05-25 04:00 | 0.98023
2022-05-25 05:00 | 0.98984
2022-05-25 06:00 | 12.0351
2022-05-25 07:00 | 12.0351
2022-05-25 08:00 | 12.0351
2022-05-25 09:00 | 12.0351
2022-05-25 10:00 | 12.0351
2022-05-25 11:00 | 12.0351
2022-05-25 12:00 | 12.0351
2022-05-25 13:00 | 12.0351
2022-05-25 14:00 | 12.0351
2022-05-25 15:00 | 12.0351
2022-05-25 16:00 | 12.0351
2022-05-25 17:00 | 12.0351
2022-05-25 18:00 | 7.3269
2022-05-25 19:00 | 2.97
2022-05-25 20:00 | 2.9741
2022-05-25 21:00 | 3.0516
2022-05-25 22:00 | 3.025
2022-05-25 23:00 | 3.0169
2022-05-26 | 3.0138
2022-05-26 01:00 | 2.97
2022-05-26 02:00 | 3.0261
2022-05-26 03:00 | 3.0373
2022-05-26 04:00 | 3.0444
2022-05-26 05:00 | 3.067
2022-05-26 06:00 | 12.0351
2022-05-26 07:00 | 12.0351
2022-05-26 08:00 | 12.0351
2022-05-26 09:00 | 12.0351
2022-05-26 10:00 | 12.0351
2022-05-26 11:00 | 12.0351
2022-05-26 12:00 | 12.0351
2022-05-26 13:00 | 12.0351
2022-05-26 14:00 | 12.0351
2022-05-26 15:00 | 12.0351
2022-05-26 16:00 | 12.0351
2022-05-26 17:00 | 12.0351
2022-05-26 18:00 | 2.8717
2022-05-26 19:00 | 2.9822
2022-05-26 20:00 | 2.9975
2022-05-26 21:00 | 2.9649
2022-05-26 22:00 | 2.9731
2022-05-26 23:00 | 2.9609
2022-05-27 | 2.9456
2022-05-27 01:00 | 2.9518
2022-05-27 02:00 | 2.904
2022-05-27 03:00 | 2.9244
2022-05-27 04:00 | 2.9244
2022-05-27 05:00 | 2.9325
2022-05-27 06:00 | 12.0351
2022-05-27 07:00 | 12.0351
2022-05-27 08:00 | 12.0351
2022-05-27 09:00 | 12.0351
2022-05-27 10:00 | 12.0351
2022-05-27 11:00 | 12.0351
2022-05-27 12:00 | 12.0351
2022-05-27 13:00 | 12.0351
2022-05-27 14:00 | 12.0351
2022-05-27 15:00 | 12.0351
2022-05-27 16:00 | 12.0351
2022-05-27 17:00 | 3.9582
2022-05-27 18:00 | 1.3494
2022-05-27 19:00 | 1.2903
2022-05-27 20:00 | 1.2812
2022-05-27 21:00 | 1.2858
2022-05-27 22:00 | 1.2922
2022-05-27 23:00 | 1.2785
2022-05-28 | 1.2849
2022-05-28 01:00 | 1.2794
2022-05-28 02:00 | 1.2529
2022-05-28 03:00 | 1.2666
2022-05-28 04:00 | 1.2538
2022-05-28 05:00 | 1.2493
2022-05-28 06:00 | 1.2812
2022-05-28 07:00 | 1.2538
2022-05-28 08:00 | 1.2803
2022-05-28 09:00 | 1.2931
2022-05-28 10:00 | 1.2858
2022-05-28 11:00 | 1.2876
2022-05-28 12:00 | 1.2922
2022-05-28 13:00 | 1.2684
2022-05-28 14:00 | 1.2511
2022-05-28 15:00 | 1.2812
2022-05-28 16:00 | 1.2456
2022-05-28 17:00 | 1.2675
2022-05-28 18:00 | 1.2483
2022-05-28 19:00 | 1.2757
2022-05-28 20:00 | 1.2867
2022-05-28 21:00 | 1.2812
2022-05-28 22:00 | 1.2584
2022-05-28 23:00 | 1.2748
2022-05-29 | 1.263
2022-05-29 01:00 | 1.2364
2022-05-29 02:00 | 1.2493
2022-05-29 03:00 | 1.2437
2022-05-29 04:00 | 1.2437
2022-05-29 05:00 | 1.2502
2022-05-29 06:00 | 1.2547
2022-05-29 07:00 | 1.2566
2022-05-29 08:00 | 1.2648
2022-05-29 09:00 | 1.2446
2022-05-29 10:00 | 1.2502
2022-05-29 11:00 | 1.2226
2022-05-29 12:00 | 1.23
2022-05-29 13:00 | 1.2309
2022-05-29 14:00 | 1.2593
2022-05-29 15:00 | 1.2474
2022-05-29 16:00 | 1.2493
2022-05-29 17:00 | 1.2611
2022-05-29 18:00 | 1.2547
2022-05-29 19:00 | 1.2419
2022-05-29 20:00 | 1.2593
2022-05-29 21:00 | 1.2666
2022-05-29 22:00 | 1.2291
2022-05-29 23:00 | 1.2235
2022-05-30 | 1.2345
2022-05-30 01:00 | 1.207
2022-05-30 02:00 | 1.2309
2022-05-30 03:00 | 1.2153
2022-05-30 04:00 | 1.196
2022-05-30 05:00 | 1.2144
2022-05-30 06:00 | 1.2245
2022-05-30 07:00 | 12.0351
2022-05-30 08:00 | 12.0351
2022-05-30 09:00 | 12.0351
2022-05-30 10:00 | 12.0351
2022-05-30 11:00 | 12.0351
2022-05-30 12:00 | 12.0351
2022-05-30 13:00 | 12.0351
2022-05-30 14:00 | 12.0351
2022-05-30 15:00 | 2.7231
2022-05-30 16:00 | 2.7701
2022-05-30 17:00 | 2.7571
2022-05-30 18:00 | 2.8042
2022-05-30 19:00 | 2.7791
2022-05-30 20:00 | 2.7561
2022-05-30 21:00 | 2.7932
2022-05-30 22:00 | 2.7842
2022-05-30 23:00 | 2.8163
2022-05-31 | 2.8193
2022-05-31 01:00 | 2.7611
2022-05-31 02:00 | 2.7992
2022-05-31 03:00 | 2.7701
2022-05-31 04:00 | 2.7812
2022-05-31 05:00 | 2.8073
2022-05-31 06:00 | 12.0351
2022-05-31 07:00 | 12.0351
2022-05-31 08:00 | 12.0351
2022-05-31 09:00 | 12.0351
2022-05-31 10:00 | 12.0351
2022-05-31 11:00 | 12.0351
2022-05-31 12:00 | 12.0351
2022-05-31 13:00 | 12.0351
2022-05-31 14:00 | 12.0351
2022-05-31 15:00 | 12.0351
2022-05-31 16:00 | 12.0351
2022-05-31 17:00 | 12.0351
2022-05-31 18:00 | 12.0351
2022-05-31 19:00 | 12.0351
2022-05-31 20:00 | 12.0351
2022-05-31 21:00 | 2.9021
2022-05-31 22:00 | 2.9183
2022-05-31 23:00 | 2.8515
2022-06-01 | 2.8304
2022-06-01 01:00 | 2.8143
2022-06-01 02:00 | 2.8304
2022-06-01 03:00 | 2.8748
2022-06-01 04:00 | 2.8314
2022-06-01 05:00 | 2.8203
2022-06-01 06:00 | 4.5128
2022-06-01 07:00 | 12.0351
2022-06-01 08:00 | 12.0351
2022-06-01 09:00 | 12.0351
2022-06-01 10:00 | 12.0351
2022-06-01 11:00 | 12.0351
2022-06-01 12:00 | 12.0351
2022-06-01 13:00 | 12.0351
2022-06-01 14:00 | 12.0351
2022-06-01 15:00 | 12.0351
2022-06-01 16:00 | 12.0351
2022-06-01 17:00 | 12.0351
2022-06-01 18:00 | 6.9225
2022-06-01 19:00 | 2.9325
2022-06-01 20:00 | 2.8354
2022-06-01 21:00 | 2.8506
2022-06-01 22:00 | 2.8304
2022-06-01 23:00 | 2.7842
2022-06-02 | 2.8012
2022-06-02 01:00 | 2.7731
2022-06-02 02:00 | 2.7892
2022-06-02 03:00 | 2.7871
2022-06-02 04:00 | 2.8042
2022-06-02 05:00 | 2.8234
2022-06-02 06:00 | 8.3996
2022-06-02 07:00 | 12.0351
2022-06-02 08:00 | 12.0351
2022-06-02 09:00 | 12.0351
2022-06-02 10:00 | 12.0351
2022-06-02 11:00 | 12.0351
2022-06-02 12:00 | 12.0351
2022-06-02 13:00 | 12.0351
2022-06-02 14:00 | 12.0351
2022-06-02 15:00 | 12.0351
2022-06-02 16:00 | 12.0351
2022-06-02 17:00 | 12.0351
2022-06-02 18:00 | 12.0351
2022-06-02 19:00 | 2.8033
2022-06-02 20:00 | 2.8042
2022-06-02 21:00 | 2.7962
2022-06-02 22:00 | 2.7992
2022-06-02 23:00 | 2.8183
2022-06-03 | 2.8002
2022-06-03 01:00 | 2.7842
2022-06-03 02:00 | 2.7831
2022-06-03 03:00 | 2.7531
2022-06-03 04:00 | 2.7621
2022-06-03 05:00 | 2.8073
2022-06-03 06:00 | 12.0351
2022-06-03 07:00 | 12.0351
2022-06-03 08:00 | 12.0351
2022-06-03 09:00 | 12.0351
2022-06-03 10:00 | 12.0351
2022-06-03 11:00 | 12.0351
2022-06-03 12:00 | 12.0351
2022-06-03 13:00 | 12.0351
2022-06-03 14:00 | 12.0351
2022-06-03 15:00 | 12.0351
2022-06-03 16:00 | 12.0351
2022-06-03 17:00 | 12.0351
2022-06-03 18:00 | 12.0351
2022-06-03 19:00 | 12.0351
2022-06-03 20:00 | 6.8727
2022-06-03 21:00 | 2.8485
2022-06-03 22:00 | 2.8606
2022-06-03 23:00 | 2.8435
2022-06-04 | 2.8113
2022-06-04 01:00 | 2.7501
2022-06-04 02:00 | 2.7912
2022-06-04 03:00 | 2.8243
2022-06-04 04:00 | 2.8033
2022-06-04 05:00 | 2.8033
2022-06-04 06:00 | 2.7871
2022-06-04 07:00 | 2.8203
2022-06-04 08:00 | 2.7791
2022-06-04 09:00 | 2.7842
2022-06-04 10:00 | 2.8042
2022-06-04 11:00 | 2.7751
2022-06-04 12:00 | 2.7711
2022-06-04 13:00 | 2.7952
2022-06-04 14:00 | 2.7762
2022-06-04 15:00 | 2.7641
2022-06-04 16:00 | 2.7722
2022-06-04 17:00 | 2.7401
2022-06-04 18:00 | 2.7351
2022-06-04 19:00 | 2.7331
2022-06-04 20:00 | 2.7561
2022-06-04 21:00 | 2.7301
2022-06-04 22:00 | 2.7311
2022-06-04 23:00 | 2.7371
2022-06-05 | 2.7831
2022-06-05 01:00 | 2.7631
2022-06-05 02:00 | 2.7852
2022-06-05 03:00 | 2.7621
2022-06-05 04:00 | 2.7701
2022-06-05 05:00 | 2.8002
2022-06-05 06:00 | 2.7992
2022-06-05 07:00 | 2.8133
2022-06-05 08:00 | 2.8123
2022-06-05 09:00 | 2.8294
2022-06-05 10:00 | 2.8284
2022-06-05 11:00 | 2.7731
2022-06-05 12:00 | 2.8052
2022-06-05 13:00 | 2.8264
2022-06-05 14:00 | 2.8062
2022-06-05 15:00 | 2.8062
2022-06-05 16:00 | 2.7831
2022-06-05 17:00 | 2.7551
2022-06-05 18:00 | 2.7601
2022-06-05 19:00 | 2.7491
2022-06-05 20:00 | 2.7661
2022-06-05 21:00 | 2.7651
2022-06-05 22:00 | 2.7571
2022-06-05 23:00 | 2.7251
2022-06-06 | 2.7922
2022-06-06 01:00 | 2.7751
2022-06-06 02:00 | 2.7902
2022-06-06 03:00 | 2.7972
2022-06-06 04:00 | 2.8223
2022-06-06 05:00 | 2.8102
2022-06-06 06:00 | 9.1642
2022-06-06 07:00 | 12.0351
2022-06-06 08:00 | 12.0351
2022-06-06 09:00 | 12.0351
2022-06-06 10:00 | 12.0351
2022-06-06 11:00 | 12.0351
2022-06-06 12:00 | 12.0351
2022-06-06 13:00 | 12.0351
2022-06-06 14:00 | 12.0351
2022-06-06 15:00 | 12.0351
2022-06-06 16:00 | 12.0351
2022-06-06 17:00 | 10.3876
2022-06-06 18:00 | 2.7421
2022-06-06 19:00 | 2.7741
2022-06-06 20:00 | 2.7952
2022-06-06 21:00 | 2.8012
2022-06-06 22:00 | 2.8536
2022-06-06 23:00 | 2.7781
2022-06-07 | 2.8223
2022-06-07 01:00 | 2.8143
2022-06-07 02:00 | 2.8033
2022-06-07 03:00 | 2.8274
2022-06-07 04:00 | 2.8223
2022-06-07 05:00 | 2.8667
2022-06-07 06:00 | 12.0351
2022-06-07 07:00 | 12.0351
2022-06-07 08:00 | 12.0351
2022-06-07 09:00 | 12.0351
2022-06-07 10:00 | 12.0351
2022-06-07 11:00 | 12.0351
2022-06-07 12:00 | 12.0351
2022-06-07 13:00 | 12.0351
2022-06-07 14:00 | 12.0351
2022-06-07 15:00 | 12.0351
2022-06-07 16:00 | 12.0351
2022-06-07 17:00 | 12.4137
2022-06-07 18:00 | 2.8445
2022-06-07 19:00 | 2.8062
2022-06-07 20:00 | 2.7681
2022-06-07 21:00 | 2.7611
2022-06-07 22:00 | 2.8102
2022-06-07 23:00 | 2.8133
2022-06-08 | 2.7762
2022-06-08 01:00 | 2.7491
2022-06-08 02:00 | 2.7391
2022-06-08 03:00 | 2.7281
2022-06-08 04:00 | 2.7671
2022-06-08 05:00 | 2.8033
2022-06-08 06:00 | 12.0351
2022-06-08 07:00 | 12.0351
2022-06-08 08:00 | 12.0351
2022-06-08 09:00 | 12.0351
2022-06-08 10:00 | 12.0351
2022-06-08 11:00 | 12.0351
2022-06-08 12:00 | 12.0351
2022-06-08 13:00 | 12.0351
2022-06-08 14:00 | 12.0351
2022-06-08 15:00 | 12.0351
2022-06-08 16:00 | 12.0351
2022-06-08 17:00 | 12.0351
2022-06-08 18:00 | 4.4683
2022-06-08 19:00 | 2.7962
2022-06-08 20:00 | 2.7791
2022-06-08 21:00 | 2.8002
2022-06-08 22:00 | 2.7601
2022-06-08 23:00 | 2.7411
2022-06-09 | 2.7842
2022-06-09 01:00 | 2.7581
2022-06-09 02:00 | 2.7301
2022-06-09 03:00 | 2.7491
2022-06-09 04:00 | 2.7391
2022-06-09 05:00 | 2.7611
2022-06-09 06:00 | 12.0351
2022-06-09 07:00 | 12.0351
2022-06-09 08:00 | 12.0351
2022-06-09 09:00 | 12.0351
2022-06-09 10:00 | 12.0351
2022-06-09 11:00 | 12.0351
2022-06-09 12:00 | 12.0351
2022-06-09 13:00 | 12.0351
2022-06-09 14:00 | 12.0351
2022-06-09 15:00 | 12.0351
2022-06-09 16:00 | 12.0351
2022-06-09 17:00 | 12.0351
2022-06-09 18:00 | 12.0351
2022-06-09 19:00 | 12.0351
2022-06-09 20:00 | 12.0351
2022-06-09 21:00 | 12.0351
2022-06-09 22:00 | 5.3226
2022-06-09 23:00 | 2.8414
2022-06-10 | 2.7762
2022-06-10 01:00 | 2.7802
2022-06-10 02:00 | 2.8304
2022-06-10 03:00 | 2.7942
2022-06-10 04:00 | 2.7731
2022-06-10 05:00 | 2.8193
2022-06-10 06:00 | 12.0351
2022-06-10 07:00 | 12.0351
2022-06-10 08:00 | 12.0351
2022-06-10 09:00 | 12.0351
2022-06-10 10:00 | 12.0351
2022-06-10 11:00 | 12.0351
2022-06-10 12:00 | 12.0351
2022-06-10 13:00 | 12.0351
2022-06-10 14:00 | 12.0351
2022-06-10 15:00 | 12.0351
2022-06-10 16:00 | 12.0351
2022-06-10 17:00 | 12.0351
2022-06-10 18:00 | 2.895
2022-06-10 19:00 | 2.8889
2022-06-10 20:00 | 2.8234
2022-06-10 21:00 | 2.8506
2022-06-10 22:00 | 2.8183
2022-06-10 23:00 | 2.7912
2022-06-11 | 2.7802
2022-06-11 01:00 | 2.7671
2022-06-11 02:00 | 2.7711
2022-06-11 03:00 | 2.7812
2022-06-11 04:00 | 2.7571
2022-06-11 05:00 | 2.7731
2022-06-11 06:00 | 2.7411
2022-06-11 07:00 | 2.7821
2022-06-11 08:00 | 2.8284
2022-06-11 09:00 | 2.8173
2022-06-11 10:00 | 2.7972
2022-06-11 11:00 | 2.8093
2022-06-11 12:00 | 2.8133
2022-06-11 13:00 | 2.7852
2022-06-11 14:00 | 2.8374
2022-06-11 15:00 | 2.8113
2022-06-11 16:00 | 2.7942
2022-06-11 17:00 | 2.8203
2022-06-11 18:00 | 2.7821
2022-06-11 19:00 | 2.8264
2022-06-11 20:00 | 2.8404
2022-06-11 21:00 | 2.8052
2022-06-11 22:00 | 2.8253
2022-06-11 23:00 | 2.7892
2022-06-12 | 2.7651
2022-06-12 01:00 | 2.7972
2022-06-12 02:00 | 2.7972
2022-06-12 03:00 | 2.8153
2022-06-12 04:00 | 2.8475
2022-06-12 05:00 | 2.8617
2022-06-12 06:00 | 2.8475
2022-06-12 07:00 | 2.8445
2022-06-12 08:00 | 2.8646
2022-06-12 09:00 | 2.8909
2022-06-12 10:00 | 2.8778
2022-06-12 11:00 | 2.8213
2022-06-12 12:00 | 2.8586
2022-06-12 13:00 | 2.8445
2022-06-12 14:00 | 2.8455
2022-06-12 15:00 | 2.8364
2022-06-12 16:00 | 2.8586
2022-06-12 17:00 | 2.8697
2022-06-12 18:00 | 2.8173
2022-06-12 19:00 | 2.8576
2022-06-12 20:00 | 2.8073
2022-06-12 21:00 | 2.8083
2022-06-12 22:00 | 2.8133
2022-06-12 23:00 | 2.7902
2022-06-13 | 2.8093
2022-06-13 01:00 | 2.8133
2022-06-13 02:00 | 2.7671
2022-06-13 03:00 | 2.8042
2022-06-13 04:00 | 2.8304
2022-06-13 05:00 | 2.8596
2022-06-13 06:00 | 12.0351
2022-06-13 07:00 | 12.0351
2022-06-13 08:00 | 12.0351
2022-06-13 09:00 | 12.0351
2022-06-13 10:00 | 12.0351
2022-06-13 11:00 | 12.0351
2022-06-13 12:00 | 12.0351
2022-06-13 13:00 | 12.0351
2022-06-13 14:00 | 12.0351
2022-06-13 15:00 | 12.0351
2022-06-13 16:00 | 12.0351
2022-06-13 17:00 | 12.0351
2022-06-13 18:00 | 12.0351
2022-06-13 19:00 | 7.7841
2022-06-13 20:00 | 3.6363
2022-06-13 21:00 | 3.6113
2022-06-13 22:00 | 3.5947
2022-06-13 23:00 | 3.554
2022-06-14 | 3.5676
2022-06-14 01:00 | 3.5592
2022-06-14 02:00 | 3.5467
2022-06-14 03:00 | 3.5489
2022-06-14 04:00 | 3.5394
2022-06-14 05:00 | 3.5811
2022-06-14 06:00 | 12.0351
2022-06-14 07:00 | 12.0351
2022-06-14 08:00 | 12.0351
2022-06-14 09:00 | 12.0351
2022-06-14 10:00 | 12.0351
2022-06-14 11:00 | 12.0351
2022-06-14 12:00 | 12.0351
2022-06-14 13:00 | 12.0351
2022-06-14 14:00 | 12.0351
2022-06-14 15:00 | 12.0351
2022-06-14 16:00 | 12.0351
2022-06-14 17:00 | 6.0663
2022-06-14 18:00 | 2.8838
2022-06-14 19:00 | 2.9031
2022-06-14 20:00 | 2.8566
2022-06-14 21:00 | 2.8536
2022-06-14 22:00 | 2.8264
2022-06-14 23:00 | 2.8203
2022-06-15 | 2.8556
2022-06-15 01:00 | 2.8073
2022-06-15 02:00 | 2.8213
2022-06-15 03:00 | 2.7982
2022-06-15 04:00 | 2.8243
2022-06-15 05:00 | 2.8586
2022-06-15 06:00 | 12.0351
2022-06-15 07:00 | 12.0351
2022-06-15 08:00 | 12.0351
2022-06-15 09:00 | 12.0351
2022-06-15 10:00 | 12.0351
2022-06-15 11:00 | 12.0351
2022-06-15 12:00 | 12.0351
2022-06-15 13:00 | 12.0351
2022-06-15 14:00 | 12.0351
2022-06-15 15:00 | 12.0351
2022-06-15 16:00 | 12.0351
2022-06-15 17:00 | 5.6591
2022-06-15 18:00 | 2.8566
2022-06-15 19:00 | 2.9021
2022-06-15 20:00 | 2.8506
2022-06-15 21:00 | 2.8828
2022-06-15 22:00 | 2.8767
2022-06-15 23:00 | 2.8617
2022-06-16 | 2.8717
2022-06-16 01:00 | 2.8687
2022-06-16 02:00 | 2.8234
2022-06-16 03:00 | 2.8445
2022-06-16 04:00 | 2.8324
2022-06-16 05:00 | 2.8536
2022-06-16 06:00 | 12.0351
2022-06-16 07:00 | 12.0351
2022-06-16 08:00 | 12.0351
2022-06-16 09:00 | 12.0351
2022-06-16 10:00 | 12.0351
2022-06-16 11:00 | 12.0351
2022-06-16 12:00 | 12.0351
2022-06-16 13:00 | 12.0351
2022-06-16 14:00 | 12.0351
2022-06-16 15:00 | 12.0351
2022-06-16 16:00 | 12.0351
2022-06-16 17:00 | 5.0719
2022-06-16 18:00 | 2.8173
2022-06-16 19:00 | 2.8617
2022-06-16 20:00 | 2.8425
2022-06-16 21:00 | 2.8123
2022-06-16 22:00 | 2.8617
2022-06-16 23:00 | 2.8304
2022-06-17 | 2.8435
2022-06-17 01:00 | 2.8012
2022-06-17 02:00 | 2.7882
2022-06-17 03:00 | 2.8002
2022-06-17 04:00 | 2.7992
2022-06-17 05:00 | 2.8536
2022-06-17 06:00 | 12.0351
2022-06-17 07:00 | 12.0351
2022-06-17 08:00 | 12.0351
2022-06-17 09:00 | 12.0351
2022-06-17 10:00 | 12.0351
2022-06-17 11:00 | 12.0351
2022-06-17 12:00 | 12.0351
2022-06-17 13:00 | 12.0351
2022-06-17 14:00 | 12.0351
2022-06-17 15:00 | 12.0351
2022-06-17 16:00 | 12.0351
2022-06-17 17:00 | 7.9093
2022-06-17 18:00 | 0.9533
2022-06-17 19:00 | 0.92809
2022-06-17 20:00 | 0.89392
2022-06-17 21:00 | 0.88213
2022-06-17 22:00 | 0.88903
2022-06-17 23:00 | 0.87328
2022-06-18 | 0.87127
2022-06-18 01:00 | 0.85343
2022-06-18 02:00 | 0.83254
2022-06-18 03:00 | 0.83254
2022-06-18 04:00 | 0.84352
2022-06-18 05:00 | 0.8385
2022-06-18 06:00 | 0.82356
2022-06-18 07:00 | 0.8185
2022-06-18 08:00 | 0.86337
2022-06-18 09:00 | 0.8415
2022-06-18 10:00 | 0.83752
2022-06-18 11:00 | 0.83352
2022-06-18 12:00 | 0.85447
2022-06-18 13:00 | 0.8445
2022-06-18 14:00 | 0.85447
2022-06-18 15:00 | 0.85447
2022-06-18 16:00 | 0.85447
2022-06-18 17:00 | 0.83051
2022-06-18 18:00 | 0.8445
2022-06-18 19:00 | 0.8475
2022-06-18 20:00 | 0.85245
2022-06-18 21:00 | 0.85545
2022-06-18 22:00 | 0.83352
2022-06-18 23:00 | 0.82855
2022-06-19 | 0.83156
2022-06-19 01:00 | 0.84352
2022-06-19 02:00 | 0.87225
2022-06-19 03:00 | 0.88606
2022-06-19 04:00 | 0.87722
2022-06-19 05:00 | 0.88116
2022-06-19 06:00 | 0.87819
2022-06-19 07:00 | 0.88213
2022-06-19 08:00 | 0.88606
2022-06-19 09:00 | 0.89096
2022-06-19 10:00 | 0.86337
2022-06-19 11:00 | 0.85941
2022-06-19 12:00 | 0.8683
2022-06-19 13:00 | 0.85343
2022-06-19 14:00 | 0.83555
2022-06-19 15:00 | 0.84653
2022-06-19 16:00 | 0.8624
2022-06-19 17:00 | 0.86136
2022-06-19 18:00 | 0.87522
2022-06-19 19:00 | 0.86532
2022-06-19 20:00 | 0.86434
2022-06-19 21:00 | 0.86635
2022-06-19 22:00 | 0.85148
2022-06-19 23:00 | 0.85844
2022-06-20 | 0.86635
2022-06-20 01:00 | 0.87225
2022-06-20 02:00 | 0.86038
2022-06-20 03:00 | 0.87619
2022-06-20 04:00 | 0.8851
2022-06-20 05:00 | 0.89585
2022-06-20 06:00 | 0.93102
2022-06-20 07:00 | 0.88903
2022-06-20 08:00 | 0.87819
2022-06-20 09:00 | 0.87819
2022-06-20 10:00 | 0.86136
2022-06-20 11:00 | 0.87225
2022-06-20 12:00 | 0.85148
2022-06-20 13:00 | 0.83954
2022-06-20 14:00 | 0.86434
2022-06-20 15:00 | 0.85447
2022-06-20 16:00 | 0.86532
2022-06-20 17:00 | 0.88116
2022-06-20 18:00 | 0.86532
2022-06-20 19:00 | 0.87522
2022-06-20 20:00 | 0.89192
2022-06-20 21:00 | 0.88013
2022-06-20 22:00 | 0.88213
2022-06-20 23:00 | 0.86927
2022-06-21 | 0.88013
2022-06-21 01:00 | 0.87916
2022-06-21 02:00 | 0.88213
2022-06-21 03:00 | 0.88116
2022-06-21 04:00 | 0.90175
2022-06-21 05:00 | 1.2345
2022-06-21 06:00 | 12.0351
2022-06-21 07:00 | 12.0351
2022-06-21 08:00 | 12.0351
2022-06-21 09:00 | 12.0351
2022-06-21 10:00 | 12.0351
2022-06-21 11:00 | 12.0351
2022-06-21 12:00 | 12.0351
2022-06-21 13:00 | 12.0351
2022-06-21 14:00 | 12.0351
2022-06-21 15:00 | 12.0351
2022-06-21 16:00 | 12.0351
2022-06-21 17:00 | 0.89784
2022-06-21 18:00 | 0.86434
2022-06-21 19:00 | 0.90272
2022-06-21 20:00 | 0.888
2022-06-21 21:00 | 0.92223
2022-06-21 22:00 | 0.92031
2022-06-21 23:00 | 0.92031
2022-06-22 | 0.91444
2022-06-22 01:00 | 0.89392
2022-06-22 02:00 | 0.90272
2022-06-22 03:00 | 0.8988
2022-06-22 04:00 | 0.91642
2022-06-22 05:00 | 0.92809
2022-06-22 06:00 | 12.0351
2022-06-22 07:00 | 12.0351
2022-06-22 08:00 | 12.0351
2022-06-22 09:00 | 12.0351
2022-06-22 10:00 | 12.0351
2022-06-22 11:00 | 12.0351
2022-06-22 12:00 | 12.0351
2022-06-22 13:00 | 12.0351
2022-06-22 14:00 | 12.0351
2022-06-22 15:00 | 12.0351
2022-06-22 16:00 | 12.0351
2022-06-22 17:00 | 4.7762
2022-06-22 18:00 | 2.898
2022-06-22 19:00 | 2.904
2022-06-22 20:00 | 2.898
2022-06-22 21:00 | 2.9142
2022-06-22 22:00 | 2.894
2022-06-22 23:00 | 2.8818
2022-06-23 | 2.8859
2022-06-23 01:00 | 2.9061
2022-06-23 02:00 | 2.898
2022-06-23 03:00 | 2.8707
2022-06-23 04:00 | 2.8738
2022-06-23 05:00 | 2.9142
2022-06-23 06:00 | 12.0351
2022-06-23 07:00 | 12.0351
2022-06-23 08:00 | 12.0351
2022-06-23 09:00 | 12.0351
2022-06-23 10:00 | 12.0351
2022-06-23 11:00 | 12.0351
2022-06-23 12:00 | 12.0351
2022-06-23 13:00 | 12.0351
2022-06-23 14:00 | 12.0351
2022-06-23 15:00 | 12.0351
2022-06-23 16:00 | 12.0351
2022-06-23 17:00 | 4.2602
2022-06-23 18:00 | 0.92809
2022-06-23 19:00 | 0.9706
2022-06-23 20:00 | 0.93395
2022-06-23 21:00 | 0.95621
2022-06-23 22:00 | 0.9417
2022-06-23 23:00 | 0.93102
2022-06-24 | 0.9242
2022-06-24 01:00 | 0.91738
2022-06-24 02:00 | 0.90765
2022-06-24 03:00 | 0.90957
2022-06-24 04:00 | 0.9242
2022-06-24 05:00 | 0.93681
2022-06-24 06:00 | 12.0351
2022-06-24 07:00 | 12.0351
2022-06-24 08:00 | 12.0351
2022-06-24 09:00 | 12.0351
2022-06-24 10:00 | 12.0351
2022-06-24 11:00 | 12.0351
2022-06-24 12:00 | 12.0351
2022-06-24 13:00 | 12.0351
2022-06-24 14:00 | 12.0351
2022-06-24 15:00 | 12.0351
2022-06-24 16:00 | 12.0351
2022-06-24 17:00 | 5.1911
2022-06-24 18:00 | 2.0557
2022-06-24 19:00 | 2.0417
2022-06-24 20:00 | 2.0212
2022-06-24 21:00 | 2.0287
2022-06-24 22:00 | 2.0641
2022-06-24 23:00 | 2.0306
2022-06-25 | 2.0055
2022-06-25 01:00 | 1.9656
2022-06-25 02:00 | 1.9924
2022-06-25 03:00 | 1.9952
2022-06-25 04:00 | 1.985
2022-06-25 05:00 | 2.0101
2022-06-25 06:00 | 2.0055
2022-06-25 07:00 | 1.998
2022-06-25 08:00 | 2.0036
2022-06-25 09:00 | 1.9933
2022-06-25 10:00 | 2.0073
2022-06-25 11:00 | 2.0184
2022-06-25 12:00 | 2.0157
2022-06-25 13:00 | 2.024
2022-06-25 14:00 | 2.0184
2022-06-25 15:00 | 2.0268
2022-06-25 16:00 | 2.0483
2022-06-25 17:00 | 2.0287
2022-06-25 18:00 | 2.024
2022-06-25 19:00 | 2.0138
2022-06-25 20:00 | 2.0222
2022-06-25 21:00 | 2.0427
2022-06-25 22:00 | 2.0083
2022-06-25 23:00 | 1.9915
2022-06-26 | 2.011
2022-06-26 01:00 | 2.0138
2022-06-26 02:00 | 1.9952
2022-06-26 03:00 | 1.9915
2022-06-26 04:00 | 2.0129
2022-06-26 05:00 | 2.0203
2022-06-26 06:00 | 1.9961
2022-06-26 07:00 | 2.0361
2022-06-26 08:00 | 2.0027
2022-06-26 09:00 | 2.0073
2022-06-26 10:00 | 1.9776
2022-06-26 11:00 | 2.0101
2022-06-26 12:00 | 1.9989
2022-06-26 13:00 | 2.0064
2022-06-26 14:00 | 2.0064
2022-06-26 15:00 | 2.0055
2022-06-26 16:00 | 2.0157
2022-06-26 17:00 | 2.0352
2022-06-26 18:00 | 2.0278
2022-06-26 19:00 | 2.0398
2022-06-26 20:00 | 2.0203
2022-06-26 21:00 | 2.0259
2022-06-26 22:00 | 2.011
2022-06-26 23:00 | 1.9702
2022-06-27 | 2.0138
2022-06-27 01:00 | 2.0045
2022-06-27 02:00 | 1.9943
2022-06-27 03:00 | 1.9961
2022-06-27 04:00 | 1.9906
2022-06-27 05:00 | 2.0138
2022-06-27 06:00 | 12.0351
2022-06-27 07:00 | 12.0351
2022-06-27 08:00 | 12.0351
2022-06-27 09:00 | 12.0351
2022-06-27 10:00 | 12.0351
2022-06-27 11:00 | 12.0351
2022-06-27 12:00 | 12.0351
2022-06-27 13:00 | 12.0351
2022-06-27 14:00 | 12.0351
2022-06-27 15:00 | 12.0351
2022-06-27 16:00 | 12.0351
2022-06-27 17:00 | 6.4801
2022-06-27 18:00 | 2.0324
2022-06-27 19:00 | 2.0613
2022-06-27 20:00 | 2.0595
2022-06-27 21:00 | 2.0371
2022-06-27 22:00 | 2.0408
2022-06-27 23:00 | 1.9711
2022-06-28 | 2.0352
2022-06-28 01:00 | 2.0268
2022-06-28 02:00 | 1.985
2022-06-28 03:00 | 2.011
2022-06-28 04:00 | 2.0203
2022-06-28 05:00 | 3.3306
2022-06-28 06:00 | 12.0351
2022-06-28 07:00 | 12.0351
2022-06-28 08:00 | 12.0351
2022-06-28 09:00 | 12.0351
2022-06-28 10:00 | 12.0351
2022-06-28 11:00 | 12.0351
2022-06-28 12:00 | 12.0351
2022-06-28 13:00 | 12.0351
2022-06-28 14:00 | 12.0351
2022-06-28 15:00 | 12.0351
2022-06-28 16:00 | 12.0351
2022-06-28 17:00 | 6.2393
2022-06-28 18:00 | 2.0184
2022-06-28 19:00 | 2.0688
2022-06-28 20:00 | 2.0129
2022-06-28 21:00 | 2.0259
2022-06-28 22:00 | 2.0055
2022-06-28 23:00 | 2.0101
2022-06-29 | 2.0157
2022-06-29 01:00 | 1.9841
2022-06-29 02:00 | 1.9758
2022-06-29 03:00 | 1.9832
2022-06-29 04:00 | 1.9887
2022-06-29 05:00 | 2.0203
2022-06-29 06:00 | 12.0351
2022-06-29 07:00 | 12.0351
2022-06-29 08:00 | 12.0351
2022-06-29 09:00 | 12.0351
2022-06-29 10:00 | 12.0351
2022-06-29 11:00 | 12.0351
2022-06-29 12:00 | 12.0351
2022-06-29 13:00 | 12.0351
2022-06-29 14:00 | 12.0351
2022-06-29 15:00 | 12.0351
2022-06-29 16:00 | 12.0351
2022-06-29 17:00 | 8.9074
2022-06-29 18:00 | 1.1664
2022-06-29 19:00 | 1.1886
2022-06-29 20:00 | 1.1664
2022-06-29 21:00 | 1.1553
2022-06-29 22:00 | 1.1322
2022-06-29 23:00 | 1.1451
2022-06-30 | 1.1387
2022-06-30 01:00 | 1.1312
2022-06-30 02:00 | 1.1173
2022-06-30 03:00 | 1.1516
2022-06-30 04:00 | 1.1572
2022-06-30 05:00 | 1.1738
2022-06-30 06:00 | 12.0351
2022-06-30 07:00 | 12.0351
2022-06-30 08:00 | 12.0351
2022-06-30 09:00 | 12.0351
2022-06-30 10:00 | 12.0351
2022-06-30 11:00 | 12.0351
2022-06-30 12:00 | 12.0351
2022-06-30 13:00 | 12.0351
2022-06-30 14:00 | 12.0351
2022-06-30 15:00 | 12.0351
2022-06-30 16:00 | 12.0351
2022-06-30 17:00 | 2.0548
2022-06-30 18:00 | 2.0464
2022-06-30 19:00 | 2.0567
2022-06-30 20:00 | 2.0613
2022-06-30 21:00 | 2.0464
2022-06-30 22:00 | 2.0483
2022-06-30 23:00 | 2.012
2022-07-01 | 2.0064
2022-07-01 01:00 | 2.012
2022-07-01 02:00 | 2.0147
2022-07-01 03:00 | 2.0138
2022-07-01 04:00 | 2.0212
2022-07-01 05:00 | 3.3929
2022-07-01 06:00 | 12.0351
2022-07-01 07:00 | 12.0351
2022-07-01 08:00 | 12.0351
2022-07-01 09:00 | 12.0351
2022-07-01 10:00 | 12.0351
2022-07-01 11:00 | 12.0351
2022-07-01 12:00 | 12.0351
2022-07-01 13:00 | 12.0351
2022-07-01 14:00 | 12.0351
2022-07-01 15:00 | 12.0351
2022-07-01 16:00 | 12.0351
2022-07-01 17:00 | 5.4092
2022-07-01 18:00 | 2.0576
2022-07-01 19:00 | 2.0427
2022-07-01 20:00 | 2.0203
2022-07-01 21:00 | 2.0361
2022-07-01 22:00 | 2.0259
2022-07-01 23:00 | 2.0064
2022-07-02 | 2.0092
2022-07-02 01:00 | 2.0045
2022-07-02 02:00 | 1.9971
2022-07-02 03:00 | 1.9804
2022-07-02 04:00 | 2.0212
2022-07-02 05:00 | 2.0147
2022-07-02 06:00 | 1.9915
2022-07-02 07:00 | 1.985
2022-07-02 08:00 | 2.0259
2022-07-02 09:00 | 2.0389
2022-07-02 10:00 | 2.0389
2022-07-02 11:00 | 2.0222
2022-07-02 12:00 | 2.0175
2022-07-02 13:00 | 2.0343
2022-07-02 14:00 | 2.0352
2022-07-02 15:00 | 2.0147
2022-07-02 16:00 | 2.0073
2022-07-02 17:00 | 1.9952
2022-07-02 18:00 | 2.0092
2022-07-02 19:00 | 2.0361
2022-07-02 20:00 | 2.0464
2022-07-02 21:00 | 2.0278
2022-07-02 22:00 | 2.0147
2022-07-02 23:00 | 1.9961
2022-07-03 | 1.9693
2022-07-03 01:00 | 1.9674
2022-07-03 02:00 | 1.9776
2022-07-03 03:00 | 1.9841
2022-07-03 04:00 | 1.9785
2022-07-03 05:00 | 1.9767
2022-07-03 06:00 | 1.9646
2022-07-03 07:00 | 1.9943
2022-07-03 08:00 | 1.9813
2022-07-03 09:00 | 1.9887
2022-07-03 10:00 | 1.9702
2022-07-03 11:00 | 1.9813
2022-07-03 12:00 | 1.9961
2022-07-03 13:00 | 1.9971
2022-07-03 14:00 | 1.9748
2022-07-03 15:00 | 1.9693
2022-07-03 16:00 | 1.9915
2022-07-03 17:00 | 1.9952
2022-07-03 18:00 | 1.9924
2022-07-03 19:00 | 2.0092
2022-07-03 20:00 | 1.9859
2022-07-03 21:00 | 2.0017
2022-07-03 22:00 | 1.9804
2022-07-03 23:00 | 1.9795
2022-07-04 | 1.985
2022-07-04 01:00 | 1.9795
2022-07-04 02:00 | 1.9609
2022-07-04 03:00 | 1.9841
2022-07-04 04:00 | 1.9943
2022-07-04 05:00 | 1.9878
2022-07-04 06:00 | 1.998
2022-07-04 07:00 | 2.0194
2022-07-04 08:00 | 1.9971
2022-07-04 09:00 | 2.0101
2022-07-04 10:00 | 1.9999
2022-07-04 11:00 | 2.0073
2022-07-04 12:00 | 2.0027
2022-07-04 13:00 | 2.0101
2022-07-04 14:00 | 2.0027
2022-07-04 15:00 | 1.998
2022-07-04 16:00 | 2.0147
2022-07-04 17:00 | 2.012
2022-07-04 18:00 | 2.0036
2022-07-04 19:00 | 2.0157
2022-07-04 20:00 | 2.0036
2022-07-04 21:00 | 2.0027
2022-07-04 22:00 | 1.9887
2022-07-04 23:00 | 2.024
2022-07-05 | 2.0315
2022-07-05 01:00 | 2.0212
2022-07-05 02:00 | 1.998
2022-07-05 03:00 | 1.9869
2022-07-05 04:00 | 1.9933
2022-07-05 05:00 | 2.0249
2022-07-05 06:00 | 12.0351
2022-07-05 07:00 | 12.0351
2022-07-05 08:00 | 12.0351
2022-07-05 09:00 | 12.0351
2022-07-05 10:00 | 12.0351
2022-07-05 11:00 | 12.0351
2022-07-05 12:00 | 12.0351
2022-07-05 13:00 | 12.0351
2022-07-05 14:00 | 12.0351
2022-07-05 15:00 | 12.0351
2022-07-05 16:00 | 12.0351
2022-07-05 17:00 | 12.0351
2022-07-05 18:00 | 7.5048
2022-07-05 19:00 | 2.0595
2022-07-05 20:00 | 2.038
2022-07-05 21:00 | 2.0231
2022-07-05 22:00 | 2.024
2022-07-05 23:00 | 2.0008
2022-07-06 | 1.9896
2022-07-06 01:00 | 2.0092
2022-07-06 02:00 | 2.0138
2022-07-06 03:00 | 2.0203
2022-07-06 04:00 | 2.0017
2022-07-06 05:00 | 2.0175
2022-07-06 06:00 | 12.0351
2022-07-06 07:00 | 12.0351
2022-07-06 08:00 | 12.0351
2022-07-06 09:00 | 12.0351
2022-07-06 10:00 | 12.0351
2022-07-06 11:00 | 12.0351
2022-07-06 12:00 | 12.0351
2022-07-06 13:00 | 12.0351
2022-07-06 14:00 | 12.0351
2022-07-06 15:00 | 12.0351
2022-07-06 16:00 | 12.0351
2022-07-06 17:00 | 9.4978
2022-07-06 18:00 | 1.6341
2022-07-06 19:00 | 1.6875
2022-07-06 20:00 | 1.6413
2022-07-06 21:00 | 1.6639
2022-07-06 22:00 | 1.6277
2022-07-06 23:00 | 1.6169
2022-07-07 | 1.635
2022-07-07 01:00 | 1.6413
2022-07-07 02:00 | 1.6331
2022-07-07 03:00 | 1.6277
2022-07-07 04:00 | 1.6286
2022-07-07 05:00 | 2.8073
2022-07-07 06:00 | 12.0351
2022-07-07 07:00 | 12.0351
2022-07-07 08:00 | 12.0351
2022-07-07 09:00 | 12.0351
2022-07-07 10:00 | 12.0351
2022-07-07 11:00 | 12.0351
2022-07-07 12:00 | 12.0351
2022-07-07 13:00 | 12.0351
2022-07-07 14:00 | 12.0351
2022-07-07 15:00 | 12.0351
2022-07-07 16:00 | 12.0351
2022-07-07 17:00 | 8.8652
2022-07-07 18:00 | 1.96
2022-07-07 19:00 | 2.0092
2022-07-07 20:00 | 2.0045
2022-07-07 21:00 | 1.998
2022-07-07 22:00 | 2.0036
2022-07-07 23:00 | 1.998
2022-07-08 | 1.9999
2022-07-08 01:00 | 1.9915
2022-07-08 02:00 | 2.0064
2022-07-08 03:00 | 2.0203
2022-07-08 04:00 | 2.0278
2022-07-08 05:00 | 2.0222
2022-07-08 06:00 | 12.0351
2022-07-08 07:00 | 12.0351
2022-07-08 08:00 | 12.0351
2022-07-08 09:00 | 12.0351
2022-07-08 10:00 | 12.0351
2022-07-08 11:00 | 12.0351
2022-07-08 12:00 | 12.0351
2022-07-08 13:00 | 12.0351
2022-07-08 14:00 | 12.0351
2022-07-08 15:00 | 12.0351
2022-07-08 16:00 | 12.0351
2022-07-08 17:00 | 7.2317
2022-07-08 18:00 | 2.0492
2022-07-08 19:00 | 2.024
2022-07-08 20:00 | 1.9656
2022-07-08 21:00 | 1.9971
2022-07-08 22:00 | 1.9971
2022-07-08 23:00 | 2.0036
2022-07-09 | 1.9952
2022-07-09 01:00 | 1.9933
2022-07-09 02:00 | 2.0027
2022-07-09 03:00 | 1.9739
2022-07-09 04:00 | 1.9887
2022-07-09 05:00 | 1.9841
2022-07-09 06:00 | 1.9878
2022-07-09 07:00 | 1.9915
2022-07-09 08:00 | 2.0101
2022-07-09 09:00 | 1.9869
2022-07-09 10:00 | 1.9915
2022-07-09 11:00 | 2.0027
2022-07-09 12:00 | 1.998
2022-07-09 13:00 | 2.0092
2022-07-09 14:00 | 2.0017
2022-07-09 15:00 | 2.0083
2022-07-09 16:00 | 1.9961
2022-07-09 17:00 | 1.9952
2022-07-09 18:00 | 1.9591
2022-07-09 19:00 | 1.9434
2022-07-09 20:00 | 1.9471
2022-07-09 21:00 | 1.9259
2022-07-09 22:00 | 1.9415
2022-07-09 23:00 | 1.9535
2022-07-10 | 1.9388
2022-07-10 01:00 | 1.9452
2022-07-10 02:00 | 1.9609
2022-07-10 03:00 | 1.9822
2022-07-10 04:00 | 1.9933
2022-07-10 05:00 | 1.985
2022-07-10 06:00 | 1.9915
2022-07-10 07:00 | 1.9896
2022-07-10 08:00 | 1.9684
2022-07-10 09:00 | 1.9989
2022-07-10 10:00 | 1.9711
2022-07-10 11:00 | 1.9832
2022-07-10 12:00 | 2.0092
2022-07-10 13:00 | 2.012
2022-07-10 14:00 | 1.9887
2022-07-10 15:00 | 1.9859
2022-07-10 16:00 | 2.0036
2022-07-10 17:00 | 1.9999
2022-07-10 18:00 | 1.9943
2022-07-10 19:00 | 1.9674
2022-07-10 20:00 | 1.9869
2022-07-10 21:00 | 1.9952
2022-07-10 22:00 | 1.9832
2022-07-10 23:00 | 1.9804
2022-07-11 | 1.9933
2022-07-11 01:00 | 1.9804
2022-07-11 02:00 | 1.9906
2022-07-11 03:00 | 2.0175
2022-07-11 04:00 | 1.9869
2022-07-11 05:00 | 5.7635
2022-07-11 06:00 | 12.0351
2022-07-11 07:00 | 12.0351
2022-07-11 08:00 | 12.0351
2022-07-11 09:00 | 12.0351
2022-07-11 10:00 | 12.0351
2022-07-11 11:00 | 12.0351
2022-07-11 12:00 | 12.0351
2022-07-11 13:00 | 12.0351
2022-07-11 14:00 | 12.0351
2022-07-11 15:00 | 12.0351
2022-07-11 16:00 | 12.0351
2022-07-11 17:00 | 12.0351
2022-07-11 18:00 | 6.731
2022-07-11 19:00 | 4.8691
2022-07-11 20:00 | 4.7948
2022-07-11 21:00 | 4.7446
2022-07-11 22:00 | 4.7475
2022-07-11 23:00 | 4.7159
2022-07-12 | 4.7396
2022-07-12 01:00 | 4.8164
2022-07-12 02:00 | 4.7948
2022-07-12 03:00 | 4.8154
2022-07-12 04:00 | 4.8232
2022-07-12 05:00 | 4.8125
2022-07-12 06:00 | 12.0351
2022-07-12 07:00 | 12.0351
2022-07-12 08:00 | 12.0351
2022-07-12 09:00 | 12.0351
2022-07-12 10:00 | 12.0351
2022-07-12 11:00 | 12.0351
2022-07-12 12:00 | 12.0351
2022-07-12 13:00 | 12.0351
2022-07-12 14:00 | 12.0351
2022-07-12 15:00 | 12.0351
2022-07-12 16:00 | 12.0351
2022-07-12 17:00 | 12.0351
2022-07-12 18:00 | 3.5499
2022-07-12 19:00 | 2.1016
2022-07-12 20:00 | 2.0885
2022-07-12 21:00 | 2.1204
2022-07-12 22:00 | 2.1109
2022-07-12 23:00 | 2.0988
2022-07-13 | 2.0988
2022-07-13 01:00 | 2.0988
2022-07-13 02:00 | 2.0885
2022-07-13 03:00 | 2.0847
2022-07-13 04:00 | 2.1016
2022-07-13 05:00 | 4.7278
2022-07-13 06:00 | 12.0351
2022-07-13 07:00 | 12.0351
2022-07-13 08:00 | 12.0351
2022-07-13 09:00 | 12.0351
2022-07-13 10:00 | 12.0351
2022-07-13 11:00 | 12.0351
2022-07-13 12:00 | 12.0351
2022-07-13 13:00 | 12.0351
2022-07-13 14:00 | 12.0351
2022-07-13 15:00 | 12.0351
2022-07-13 16:00 | 12.0351
2022-07-13 17:00 | 12.0351
2022-07-13 18:00 | 7.1532
2022-07-13 19:00 | 7.1915
2022-07-13 20:00 | 7.1777
2022-07-13 21:00 | 7.1545
2022-07-13 22:00 | 7.1603
2022-07-13 23:00 | 7.1595
2022-07-14 | 7.1818
2022-07-14 01:00 | 7.1591
2022-07-14 02:00 | 7.1507
2022-07-14 03:00 | 7.169
2022-07-14 04:00 | 7.1956
2022-07-14 05:00 | 7.8506
2022-07-14 06:00 | 12.0351
2022-07-14 07:00 | 12.0351
2022-07-14 08:00 | 12.0351
2022-07-14 09:00 | 12.0351
2022-07-14 10:00 | 12.0351
2022-07-14 11:00 | 12.0351
2022-07-14 12:00 | 12.0351
2022-07-14 13:00 | 12.0351
2022-07-14 14:00 | 12.0351
2022-07-14 15:00 | 12.0351
2022-07-14 16:00 | 12.0351
2022-07-14 17:00 | 8.3197
2022-07-14 18:00 | 7.3678
2022-07-14 19:00 | 7.3774
2022-07-14 20:00 | 7.3654
2022-07-14 21:00 | 7.3767
2022-07-14 22:00 | 7.3858
2022-07-14 23:00 | 7.3613
2022-07-15 | 7.3647
2022-07-15 01:00 | 7.3929
2022-07-15 02:00 | 7.3794
2022-07-15 03:00 | 7.4124
2022-07-15 04:00 | 7.4286
2022-07-15 05:00 | 7.435
2022-07-15 06:00 | 12.0351
2022-07-15 07:00 | 12.0351
2022-07-15 08:00 | 12.0351
2022-07-15 09:00 | 12.0351
2022-07-15 10:00 | 12.0351
2022-07-15 11:00 | 12.0351
2022-07-15 12:00 | 12.0351
2022-07-15 13:00 | 12.0351
2022-07-15 14:00 | 12.0351
2022-07-15 15:00 | 12.0351
2022-07-15 16:00 | 12.0351
2022-07-15 17:00 | 12.0351
2022-07-15 18:00 | 7.1325
2022-07-15 19:00 | 7.1595
2022-07-15 20:00 | 7.1423
2022-07-15 21:00 | 7.1359
2022-07-15 22:00 | 7.1364
2022-07-15 23:00 | 7.1019
2022-07-16 | 7.1478
2022-07-16 01:00 | 7.1637
2022-07-16 02:00 | 7.1699
2022-07-16 03:00 | 7.1678
2022-07-16 04:00 | 7.1465
2022-07-16 05:00 | 7.1482
2022-07-16 06:00 | 7.1515
2022-07-16 07:00 | 7.1948
2022-07-16 08:00 | 7.2172
2022-07-16 09:00 | 7.2
2022-07-16 10:00 | 7.1715
2022-07-16 11:00 | 7.1715
2022-07-16 12:00 | 7.2124
2022-07-16 13:00 | 7.1756
2022-07-16 14:00 | 7.1931
2022-07-16 15:00 | 7.1507
2022-07-16 16:00 | 7.204
2022-07-16 17:00 | 7.1968
2022-07-16 18:00 | 7.2004
2022-07-16 19:00 | 7.1557
2022-07-16 20:00 | 7.1557
2022-07-16 21:00 | 7.1515
2022-07-16 22:00 | 7.1201
2022-07-16 23:00 | 7.1244
2022-07-17 | 7.1119
2022-07-17 01:00 | 7.0958
2022-07-17 02:00 | 7.1136
2022-07-17 03:00 | 7.1515
2022-07-17 04:00 | 7.1607
2022-07-17 05:00 | 7.1474
2022-07-17 06:00 | 7.1448
2022-07-17 07:00 | 7.1355
2022-07-17 08:00 | 7.1537
2022-07-17 09:00 | 7.1715
2022-07-17 10:00 | 7.1461
2022-07-17 11:00 | 7.1469
2022-07-17 12:00 | 7.1574
2022-07-17 13:00 | 7.1313
2022-07-17 14:00 | 7.1381
2022-07-17 15:00 | 7.1261
2022-07-17 16:00 | 7.1313
2022-07-17 17:00 | 7.1278
2022-07-17 18:00 | 7.1054
2022-07-17 19:00 | 7.1274
2022-07-17 20:00 | 7.1478
2022-07-17 21:00 | 7.1557
2022-07-17 22:00 | 7.1325
2022-07-17 23:00 | 7.1119
2022-07-18 | 7.1287
2022-07-18 01:00 | 7.097
2022-07-18 02:00 | 7.1274
2022-07-18 03:00 | 7.1566
2022-07-18 04:00 | 7.1435
2022-07-18 05:00 | 7.4934
2022-07-18 06:00 | 12.0351
2022-07-18 07:00 | 12.0351
2022-07-18 08:00 | 12.0351
2022-07-18 09:00 | 12.0351
2022-07-18 10:00 | 12.0351
2022-07-18 11:00 | 12.0351
2022-07-18 12:00 | 12.0351
2022-07-18 13:00 | 12.0351
2022-07-18 14:00 | 12.0351
2022-07-18 15:00 | 12.0351
2022-07-18 16:00 | 1.6702
2022-07-18 17:00 | 1.692
2022-07-18 18:00 | 1.7029
2022-07-18 19:00 | 1.6902
2022-07-18 20:00 | 1.7192
2022-07-18 21:00 | 1.7256
2022-07-18 22:00 | 1.7228
2022-07-18 23:00 | 1.7083
2022-07-19 | 1.7128
2022-07-19 01:00 | 1.7111
2022-07-19 02:00 | 1.7038
2022-07-19 03:00 | 1.7192
2022-07-19 04:00 | 1.6992
2022-07-19 05:00 | 12.0351
2022-07-19 06:00 | 12.0351
2022-07-19 07:00 | 12.0351
2022-07-19 08:00 | 12.0351
2022-07-19 09:00 | 12.0351
2022-07-19 10:00 | 12.0351
2022-07-19 11:00 | 12.0351
2022-07-19 12:00 | 12.0351
2022-07-19 13:00 | 12.0351
2022-07-19 14:00 | 12.0351
2022-07-19 15:00 | 12.0351
2022-07-19 16:00 | 12.0351
2022-07-19 17:00 | 12.0351
2022-07-19 18:00 | 7.2836
2022-07-19 19:00 | 6.0941
2022-07-19 20:00 | 6.0851
2022-07-19 21:00 | 6.1165
2022-07-19 22:00 | 6.1172
2022-07-19 23:00 | 6.1357
2022-07-20 | 6.1276
2022-07-20 01:00 | 6.1269
2022-07-20 02:00 | 6.1009
2022-07-20 03:00 | 6.1401
2022-07-20 04:00 | 6.1416
2022-07-20 05:00 | 6.1948
2022-07-20 06:00 | 12.0351
2022-07-20 07:00 | 12.0351
2022-07-20 08:00 | 12.0351
2022-07-20 09:00 | 12.0351
2022-07-20 10:00 | 12.0351
2022-07-20 11:00 | 12.0351
2022-07-20 12:00 | 12.0351
2022-07-20 13:00 | 7.8951
2022-07-20 14:00 | 2.8354
2022-07-20 15:00 | 2.0334
2022-07-20 16:00 | 2.0222
2022-07-20 17:00 | 2.0707
2022-07-20 18:00 | 4.3779
2022-07-20 19:00 | 6.1313
2022-07-20 20:00 | 6.1556
2022-07-20 21:00 | 6.1702
2022-07-20 22:00 | 6.1731
2022-07-20 23:00 | 6.1364
2022-07-21 | 6.0836
2022-07-21 01:00 | 6.0828
2022-07-21 02:00 | 6.0971
2022-07-21 03:00 | 6.0776
2022-07-21 04:00 | 6.1254
2022-07-21 05:00 | 6.1009
2022-07-21 06:00 | 6.0874
2022-07-21 07:00 | 12.0351
2022-07-21 08:00 | 12.0351
2022-07-21 09:00 | 12.0351
2022-07-21 10:00 | 12.0351
2022-07-21 11:00 | 12.0351
2022-07-21 12:00 | 12.0351
2022-07-21 13:00 | 7.7139
2022-07-21 14:00 | 1.5997
2022-07-21 15:00 | 1.5889
2022-07-21 16:00 | 1.2015
2022-07-21 17:00 | 0.12155
2022-07-21 18:00 | 0.12155
2022-07-21 19:00 | 5.4181
2022-07-21 20:00 | 6.0053
2022-07-21 21:00 | 6.1083
2022-07-21 22:00 | 6.1083
2022-07-21 23:00 | 6.0844
2022-07-22 | 6.1357
2022-07-22 01:00 | 6.1578
2022-07-22 02:00 | 6.1157
2022-07-22 03:00 | 6.1342
2022-07-22 04:00 | 6.1811
2022-07-22 05:00 | 7.3661
2022-07-22 06:00 | 12.0351
2022-07-22 07:00 | 12.0351
2022-07-22 08:00 | 12.0351
2022-07-22 09:00 | 12.0351
2022-07-22 10:00 | 12.0351
2022-07-22 11:00 | 12.0351
2022-07-22 12:00 | 12.0351
2022-07-22 13:00 | 12.0351
2022-07-22 14:00 | 12.0351
2022-07-22 15:00 | 11.1771
2022-07-22 16:00 | 5.9945
2022-07-22 17:00 | 6.1283
2022-07-22 18:00 | 6.1083
2022-07-22 19:00 | 6.1416
2022-07-22 20:00 | 6.1379
2022-07-22 21:00 | 6.1607
2022-07-22 22:00 | 6.0851
2022-07-22 23:00 | 6.0971
2022-07-23 | 6.1157
2022-07-23 01:00 | 6.1009
2022-07-23 02:00 | 6.1031
2022-07-23 03:00 | 6.1053
2022-07-23 04:00 | 6.1053
2022-07-23 05:00 | 6.129
2022-07-23 06:00 | 6.1511
2022-07-23 07:00 | 6.132
2022-07-23 08:00 | 6.1394
2022-07-23 09:00 | 6.1165
2022-07-23 10:00 | 6.1651
2022-07-23 11:00 | 6.1075
2022-07-23 12:00 | 6.1497
2022-07-23 13:00 | 6.115
2022-07-23 14:00 | 6.1387
2022-07-23 15:00 | 6.1142
2022-07-23 16:00 | 6.1098
2022-07-23 17:00 | 6.0716
2022-07-23 18:00 | 6.1187
2022-07-23 19:00 | 6.1731
2022-07-23 20:00 | 6.1636
2022-07-23 21:00 | 6.1431
2022-07-23 22:00 | 6.1328
2022-07-23 23:00 | 6.0678
2022-07-24 | 6.0791
2022-07-24 01:00 | 6.1068
2022-07-24 02:00 | 6.1335
2022-07-24 03:00 | 6.1416
2022-07-24 04:00 | 6.1194
2022-07-24 05:00 | 6.0934
2022-07-24 06:00 | 6.1083
2022-07-24 07:00 | 6.1075
2022-07-24 08:00 | 6.1135
2022-07-24 09:00 | 6.1016
2022-07-24 10:00 | 6.1068
2022-07-24 11:00 | 6.1023
2022-07-24 12:00 | 6.1046
2022-07-24 13:00 | 6.1231
2022-07-24 14:00 | 6.1246
2022-07-24 15:00 | 6.0971
2022-07-24 16:00 | 6.1009
2022-07-24 17:00 | 6.1246
2022-07-24 18:00 | 6.1357
2022-07-24 19:00 | 6.1468
2022-07-24 20:00 | 6.1541
2022-07-24 21:00 | 6.1364
2022-07-24 22:00 | 6.1209
2022-07-24 23:00 | 6.0685
2022-07-25 | 6.0836
2022-07-25 01:00 | 6.0367
2022-07-25 02:00 | 6.0678
2022-07-25 03:00 | 6.0956
2022-07-25 04:00 | 6.0993
2022-07-25 05:00 | 6.0993
2022-07-25 06:00 | 12.0351
2022-07-25 07:00 | 12.0351
2022-07-25 08:00 | 12.0351
2022-07-25 09:00 | 12.0351
2022-07-25 10:00 | 12.0351
2022-07-25 11:00 | 12.0351
2022-07-25 12:00 | 12.0351
2022-07-25 13:00 | 12.0351
2022-07-25 14:00 | 12.0351
2022-07-25 15:00 | 12.0351
2022-07-25 16:00 | 12.0351
2022-07-25 17:00 | 12.0351
2022-07-25 18:00 | 6.0956
2022-07-25 19:00 | 6.0918
2022-07-25 20:00 | 6.055
2022-07-25 21:00 | 6.0413
2022-07-25 22:00 | 6.0716
2022-07-25 23:00 | 6.0489
2022-07-26 | 6.0776
2022-07-26 01:00 | 6.0253
2022-07-26 02:00 | 6.0245
2022-07-26 03:00 | 6.0798
2022-07-26 04:00 | 6.0918
2022-07-26 05:00 | 6.1098
2022-07-26 06:00 | 12.0351
2022-07-26 07:00 | 12.0351
2022-07-26 08:00 | 12.0351
2022-07-26 09:00 | 12.0351
2022-07-26 10:00 | 12.0351
2022-07-26 11:00 | 12.0351
2022-07-26 12:00 | 12.0351
2022-07-26 13:00 | 12.0351
2022-07-26 14:00 | 12.0351
2022-07-26 15:00 | 12.0351
2022-07-26 16:00 | 12.0351
2022-07-26 17:00 | 12.0351
2022-07-26 18:00 | 8.0535
2022-07-26 19:00 | 7.1448
2022-07-26 20:00 | 7.1231
2022-07-26 21:00 | 7.1132
2022-07-26 22:00 | 7.1197
2022-07-26 23:00 | 7.1503
2022-07-27 | 7.1528
2022-07-27 01:00 | 7.1566
2022-07-27 02:00 | 7.185
2022-07-27 03:00 | 7.1777
2022-07-27 04:00 | 7.2072
2022-07-27 05:00 | 7.57
2022-07-27 06:00 | 12.0351
2022-07-27 07:00 | 12.0351
2022-07-27 08:00 | 12.0351
2022-07-27 09:00 | 12.0351
2022-07-27 10:00 | 12.0351
2022-07-27 11:00 | 12.0351
2022-07-27 12:00 | 12.0351
2022-07-27 13:00 | 12.0351
2022-07-27 14:00 | 12.0351
2022-07-27 15:00 | 12.0351
2022-07-27 16:00 | 12.0351
2022-07-27 17:00 | 12.0351
2022-07-27 18:00 | 12.0351
2022-07-27 19:00 | 12.0351
2022-07-27 20:00 | 12.0351
2022-07-27 21:00 | 12.0351
2022-07-27 22:00 | 12.0351
2022-07-27 23:00 | 12.0351
2022-07-28 | 12.0351
2022-07-28 01:00 | 12.0351
2022-07-28 02:00 | 12.0351
2022-07-28 03:00 | 12.0351
2022-07-28 04:00 | 12.0351
2022-07-28 05:00 | 12.0351
2022-07-28 06:00 | 12.0351
2022-07-28 07:00 | 12.0351
2022-07-28 08:00 | 12.0351
2022-07-28 09:00 | 12.0351
2022-07-28 10:00 | 12.0351
2022-07-28 11:00 | 12.0351
2022-07-28 12:00 | 12.0351
2022-07-28 13:00 | 12.0351
2022-07-28 14:00 | 12.0351
2022-07-28 15:00 | 12.0351
2022-07-28 16:00 | 12.0351
2022-07-28 17:00 | 12.0351
2022-07-28 18:00 | 7.9809
2022-07-28 19:00 | 8.0008
2022-07-28 20:00 | 7.979
2022-07-28 21:00 | 7.9512
2022-07-28 22:00 | 7.9806
2022-07-28 23:00 | 7.9704
2022-07-29 | 7.9592
2022-07-29 01:00 | 7.9917
2022-07-29 02:00 | 7.9922
2022-07-29 03:00 | 7.9756
2022-07-29 04:00 | 7.9883
2022-07-29 05:00 | 8.3698
2022-07-29 06:00 | 12.0351
2022-07-29 07:00 | 12.0351
2022-07-29 08:00 | 12.0351
2022-07-29 09:00 | 12.0351
2022-07-29 10:00 | 12.0351
2022-07-29 11:00 | 12.0351
2022-07-29 12:00 | 12.0351
2022-07-29 13:00 | 12.0351
2022-07-29 14:00 | 12.0351
2022-07-29 15:00 | 12.0351
2022-07-29 16:00 | 12.0351
2022-07-29 17:00 | 12.0351
2022-07-29 18:00 | 8.0029
2022-07-29 19:00 | 8.0181
2022-07-29 20:00 | 7.992
2022-07-29 21:00 | 7.9933
2022-07-29 22:00 | 7.9875
2022-07-29 23:00 | 7.9654
2022-07-30 | 7.967
2022-07-30 01:00 | 7.9952
2022-07-30 02:00 | 8.0003
2022-07-30 03:00 | 8.007
2022-07-30 04:00 | 7.9941
2022-07-30 05:00 | 8.0129
2022-07-30 06:00 | 8.0124
2022-07-30 07:00 | 8.029
2022-07-30 08:00 | 8.0459
2022-07-30 09:00 | 8.0617
2022-07-30 10:00 | 8.0343
2022-07-30 11:00 | 8.0008
2022-07-30 12:00 | 8.0287
2022-07-30 13:00 | 8.0197
2022-07-30 14:00 | 8.0227
2022-07-30 15:00 | 8.0203
2022-07-30 16:00 | 8.0244
2022-07-30 17:00 | 8.0035
2022-07-30 18:00 | 7.9904
2022-07-30 19:00 | 7.9946
2022-07-30 20:00 | 7.9986
2022-07-30 21:00 | 8.0167
2022-07-30 22:00 | 8.0244
2022-07-30 23:00 | 8.0159
2022-07-31 | 7.9848
2022-07-31 01:00 | 8.0145
2022-07-31 02:00 | 8.0088
2022-07-31 03:00 | 8.0345
2022-07-31 04:00 | 8.0107
2022-07-31 05:00 | 8.0224
2022-07-31 06:00 | 8.0549
2022-07-31 07:00 | 8.0894
2022-07-31 08:00 | 8.0274
2022-07-31 09:00 | 8.039
2022-07-31 10:00 | 8.0274
2022-07-31 11:00 | 8.0118
2022-07-31 12:00 | 8.017
2022-07-31 13:00 | 8.0222
2022-07-31 14:00 | 8.0285
2022-07-31 15:00 | 8.0178
2022-07-31 16:00 | 7.9976
2022-07-31 17:00 | 7.9936
2022-07-31 18:00 | 7.9896
2022-07-31 19:00 | 8.0173
2022-07-31 20:00 | 8.0072
2022-07-31 21:00 | 10.967
2022-07-31 22:00 | 12.0351
2022-07-31 23:00 | 12.0351
2022-08-01 | 12.0351
2022-08-01 01:00 | 12.0351
2022-08-01 02:00 | 12.0351
2022-08-01 03:00 | 12.0351
2022-08-01 04:00 | 12.0351
2022-08-01 05:00 | 12.0351
2022-08-01 06:00 | 12.0351
2022-08-01 07:00 | 12.0351
2022-08-01 08:00 | 12.0351
2022-08-01 09:00 | 12.0351
2022-08-01 10:00 | 12.0351
2022-08-01 11:00 | 12.0351
2022-08-01 12:00 | 12.0351
2022-08-01 13:00 | 12.0351
2022-08-01 14:00 | 12.0351
2022-08-01 15:00 | 12.0351
2022-08-01 16:00 | 12.0351
2022-08-01 17:00 | 12.0351
2022-08-01 18:00 | 12.0351
2022-08-01 19:00 | 12.0351
2022-08-01 20:00 | 12.0351
2022-08-01 21:00 | 12.0351
2022-08-01 22:00 | 12.0351
2022-08-01 23:00 | 12.0351
2022-08-02 | 12.0351
2022-08-02 01:00 | 12.0351
2022-08-02 02:00 | 12.0351
2022-08-02 03:00 | 12.0351
2022-08-02 04:00 | 12.0351
2022-08-02 05:00 | 12.0351
2022-08-02 06:00 | 12.0351
2022-08-02 07:00 | 12.0351
2022-08-02 08:00 | 12.0351
2022-08-02 09:00 | 12.0351
2022-08-02 10:00 | 12.0351
2022-08-02 11:00 | 12.0351
2022-08-02 12:00 | 12.0351
2022-08-02 13:00 | 12.0351
2022-08-02 14:00 | 12.0351
2022-08-02 15:00 | 12.0351
2022-08-02 16:00 | 12.0351
2022-08-02 17:00 | 12.0351
2022-08-02 18:00 | 11.525
2022-08-02 19:00 | 11.525
2022-08-02 20:00 | 11.7917
2022-08-02 21:00 | 11.5939
2022-08-02 22:00 | 11.9274
2022-08-02 23:00 | 11.8054
2022-08-03 | 11.5996
2022-08-03 01:00 | 11.7468
2022-08-03 02:00 | 11.9497
2022-08-03 03:00 | 11.6754
2022-08-03 04:00 | 11.8193
2022-08-03 05:00 | 11.9824
2022-08-03 06:00 | 12.0351
2022-08-03 07:00 | 12.0351
2022-08-03 08:00 | 12.0351
2022-08-03 09:00 | 12.0351
2022-08-03 10:00 | 12.0351
2022-08-03 11:00 | 12.0351
2022-08-03 12:00 | 12.0351
2022-08-03 13:00 | 12.0351
2022-08-03 14:00 | 12.0351
2022-08-03 15:00 | 12.0351
2022-08-03 16:00 | 12.0351
2022-08-03 17:00 | 12.0351
2022-08-03 18:00 | 12.0351
2022-08-03 19:00 | 12.0351
2022-08-03 20:00 | 12.0351
2022-08-03 21:00 | 12.0351
2022-08-03 22:00 | 12.0351
2022-08-03 23:00 | 12.0351
2022-08-04 | 12.0351
2022-08-04 01:00 | 12.0351
2022-08-04 02:00 | 12.0351
2022-08-04 03:00 | 12.0351
2022-08-04 04:00 | 12.0351
2022-08-04 05:00 | 12.0351
2022-08-04 06:00 | 12.0351
2022-08-04 07:00 | 12.0351
2022-08-04 08:00 | 12.0351
2022-08-04 09:00 | 12.0351
2022-08-04 10:00 | 12.0351
2022-08-04 11:00 | 12.0351
2022-08-04 12:00 | 12.0351
2022-08-04 13:00 | 9.9006
2022-08-04 14:00 | 7.0159
2022-08-04 15:00 | 6.961
2022-08-04 16:00 | 6.9737
2022-08-04 17:00 | 6.6893
2022-08-04 18:00 | 9.5136
2022-08-04 19:00 | 12.0351
2022-08-04 20:00 | 12.0351
2022-08-04 21:00 | 12.0351
2022-08-04 22:00 | 7.9193
2022-08-04 23:00 | 7.9249
2022-08-05 | 7.9038
2022-08-05 01:00 | 7.9063
2022-08-05 02:00 | 7.9274
2022-08-05 03:00 | 7.9244
2022-08-05 04:00 | 7.9254
2022-08-05 05:00 | 8.1921
2022-08-05 06:00 | 12.0351
2022-08-05 07:00 | 12.0351
2022-08-05 08:00 | 12.0351
2022-08-05 09:00 | 12.0351
2022-08-05 10:00 | 12.0351
2022-08-05 11:00 | 12.0351
2022-08-05 12:00 | 12.0351
2022-08-05 13:00 | 12.0351
2022-08-05 14:00 | 4.8037
2022-08-05 15:00 | 4.7889
2022-08-05 16:00 | 2.4579
2022-08-05 17:00 | 0.12023
2022-08-05 18:00 | 0.12023
2022-08-05 19:00 | 6.8158
2022-08-05 20:00 | 8.62
2022-08-05 21:00 | 8.5945
2022-08-05 22:00 | 8.6324
2022-08-05 23:00 | 8.6169
2022-08-06 | 8.582
2022-08-06 01:00 | 8.5449
2022-08-06 02:00 | 8.5835
2022-08-06 03:00 | 8.597
2022-08-06 04:00 | 8.5981
2022-08-06 05:00 | 8.6031
2022-08-06 06:00 | 8.655
2022-08-06 07:00 | 8.6599
2022-08-06 08:00 | 8.6689
2022-08-06 09:00 | 8.6684
2022-08-06 10:00 | 8.6246
2022-08-06 11:00 | 8.6429
2022-08-06 12:00 | 8.6524
2022-08-06 13:00 | 8.6303
2022-08-06 14:00 | 8.6471
2022-08-06 15:00 | 8.633
2022-08-06 16:00 | 8.5329
2022-08-06 17:00 | 8.4997
2022-08-06 18:00 | 8.515
2022-08-06 19:00 | 8.5701
2022-08-06 20:00 | 8.5415
2022-08-06 21:00 | 8.5401
2022-08-06 22:00 | 8.5282
2022-08-06 23:00 | 8.468
2022-08-07 | 8.4464
2022-08-07 01:00 | 8.5178
2022-08-07 02:00 | 8.4965
2022-08-07 03:00 | 8.4645
2022-08-07 04:00 | 8.4649
2022-08-07 05:00 | 8.468
2022-08-07 06:00 | 8.4676
2022-08-07 07:00 | 8.4997
2022-08-07 08:00 | 8.4842
2022-08-07 09:00 | 8.4906
2022-08-07 10:00 | 8.4752
2022-08-07 11:00 | 8.4761
2022-08-07 12:00 | 8.4761
2022-08-07 13:00 | 8.4101
2022-08-07 14:00 | 8.4232
2022-08-07 15:00 | 8.3967
2022-08-07 16:00 | 8.4667
2022-08-07 17:00 | 8.4583
2022-08-07 18:00 | 8.4262
2022-08-07 19:00 | 8.4347
2022-08-07 20:00 | 8.4486
2022-08-07 21:00 | 8.4451
2022-08-07 22:00 | 8.4716
2022-08-07 23:00 | 8.4274
2022-08-08 | 8.433
2022-08-08 01:00 | 8.4067
2022-08-08 02:00 | 8.3996
2022-08-08 03:00 | 8.403
2022-08-08 04:00 | 8.4009
2022-08-08 05:00 | 8.416
2022-08-08 06:00 | 12.0351
2022-08-08 07:00 | 12.0351
2022-08-08 08:00 | 12.0351
2022-08-08 09:00 | 12.0351
2022-08-08 10:00 | 12.0351
2022-08-08 11:00 | 12.0351
2022-08-08 12:00 | 12.0351
2022-08-08 13:00 | 10.8992
2022-08-08 14:00 | 4.526
2022-08-08 15:00 | 4.5088
2022-08-08 16:00 | 4.532
2022-08-08 17:00 | 4.5532
2022-08-08 18:00 | 4.539
2022-08-08 19:00 | 4.6083
2022-08-08 20:00 | 4.6553
2022-08-08 21:00 | 4.6283
2022-08-08 22:00 | 4.6203
2022-08-08 23:00 | 4.5953
2022-08-09 | 4.6163
2022-08-09 01:00 | 4.6173
2022-08-09 02:00 | 4.6304
2022-08-09 03:00 | 4.6313
2022-08-09 04:00 | 4.6363
2022-08-09 05:00 | 6.3382
2022-08-09 06:00 | 12.0351
2022-08-09 07:00 | 12.0351
2022-08-09 08:00 | 12.0351
2022-08-09 09:00 | 12.0351
2022-08-09 10:00 | 12.0351
2022-08-09 11:00 | 12.0351
2022-08-09 12:00 | 12.0351
2022-08-09 13:00 | 7.4849
2022-08-09 14:00 | 4.382
2022-08-09 15:00 | 4.3707
2022-08-09 16:00 | 4.4906
2022-08-09 17:00 | 4.4997
2022-08-09 18:00 | 8.2478
2022-08-09 19:00 | 12.0351
2022-08-09 20:00 | 12.0351
2022-08-09 21:00 | 12.0351
2022-08-09 22:00 | 12.0351
2022-08-09 23:00 | 12.0351
2022-08-10 | 12.0351
2022-08-10 01:00 | 12.0351
2022-08-10 02:00 | 12.0351
2022-08-10 03:00 | 12.0351
2022-08-10 04:00 | 12.0351
2022-08-10 05:00 | 12.0351
2022-08-10 06:00 | 12.0351
2022-08-10 07:00 | 12.0351
2022-08-10 08:00 | 12.0351
2022-08-10 09:00 | 12.0351
2022-08-10 10:00 | 12.0351
2022-08-10 11:00 | 12.0351
2022-08-10 12:00 | 12.0351
2022-08-10 13:00 | 12.0351
2022-08-10 14:00 | 12.0351
2022-08-10 15:00 | 12.0351
2022-08-10 16:00 | 12.0351
2022-08-10 17:00 | 12.0351
2022-08-10 18:00 | 4.7762
2022-08-10 19:00 | 4.7317
2022-08-10 20:00 | 4.7357
2022-08-10 21:00 | 4.6692
2022-08-10 22:00 | 4.6313
2022-08-10 23:00 | 4.6123
2022-08-11 | 4.6123
2022-08-11 01:00 | 4.6163
2022-08-11 02:00 | 4.6583
2022-08-11 03:00 | 4.6613
2022-08-11 04:00 | 4.7258
2022-08-11 05:00 | 4.707
2022-08-11 06:00 | 12.0351
2022-08-11 07:00 | 12.0351
2022-08-11 08:00 | 12.0351
2022-08-11 09:00 | 12.0351
2022-08-11 10:00 | 12.0351
2022-08-11 11:00 | 12.0351
2022-08-11 12:00 | 12.0351
2022-08-11 13:00 | 12.0351
2022-08-11 14:00 | 12.0351
2022-08-11 15:00 | 12.0351
2022-08-11 16:00 | 12.0351
2022-08-11 17:00 | 10.3916
2022-08-11 18:00 | 5.9525
2022-08-11 19:00 | 5.947
2022-08-11 20:00 | 5.9478
2022-08-11 21:00 | 5.8877
2022-08-11 22:00 | 5.8941
2022-08-11 23:00 | 5.8322
2022-08-12 | 5.8909
2022-08-12 01:00 | 5.9274
2022-08-12 02:00 | 5.9281
2022-08-12 03:00 | 5.9242
2022-08-12 04:00 | 5.9697
2022-08-12 05:00 | 6.0061
2022-08-12 06:00 | 12.0351
2022-08-12 07:00 | 12.0351
2022-08-12 08:00 | 12.0351
2022-08-12 09:00 | 12.0351
2022-08-12 10:00 | 12.0351
2022-08-12 11:00 | 12.0351
2022-08-12 12:00 | 12.0351
2022-08-12 13:00 | 12.0351
2022-08-12 14:00 | 12.0351
2022-08-12 15:00 | 12.0351
2022-08-12 16:00 | 12.0351
2022-08-12 17:00 | 10.4077
2022-08-12 18:00 | 4.7367
2022-08-12 19:00 | 4.7367
2022-08-12 20:00 | 4.7554
2022-08-12 21:00 | 4.7179
2022-08-12 22:00 | 4.711
2022-08-12 23:00 | 4.7149
2022-08-13 | 4.7762
2022-08-13 01:00 | 4.788
2022-08-13 02:00 | 4.8115
2022-08-13 03:00 | 4.8066
2022-08-13 04:00 | 4.8281
2022-08-13 05:00 | 4.8154
2022-08-13 06:00 | 4.8203
2022-08-13 07:00 | 4.8555
2022-08-13 08:00 | 4.8076
2022-08-13 09:00 | 4.7535
2022-08-13 10:00 | 4.785
2022-08-13 11:00 | 4.8066
2022-08-13 12:00 | 4.8115
2022-08-13 13:00 | 4.7958
2022-08-13 14:00 | 4.8007
2022-08-13 15:00 | 4.7554
2022-08-13 16:00 | 4.7159
2022-08-13 17:00 | 4.7119
2022-08-13 18:00 | 4.6901
2022-08-13 19:00 | 4.7159
2022-08-13 20:00 | 4.7771
2022-08-13 21:00 | 4.7683
2022-08-13 22:00 | 4.7327
2022-08-13 23:00 | 4.7297
2022-08-14 | 4.7288
2022-08-14 01:00 | 4.7189
2022-08-14 02:00 | 4.7564
2022-08-14 03:00 | 4.7791
2022-08-14 04:00 | 4.8056
2022-08-14 05:00 | 4.7899
2022-08-14 06:00 | 4.8184
2022-08-14 07:00 | 4.8095
2022-08-14 08:00 | 4.7485
2022-08-14 09:00 | 4.7208
2022-08-14 10:00 | 4.7327
2022-08-14 11:00 | 4.7129
2022-08-14 12:00 | 4.6822
2022-08-14 13:00 | 4.701
2022-08-14 14:00 | 4.6812
2022-08-14 15:00 | 4.6672
2022-08-14 16:00 | 4.6573
2022-08-14 17:00 | 4.6553
2022-08-14 18:00 | 4.6413
2022-08-14 19:00 | 4.6253
2022-08-14 20:00 | 4.6653
2022-08-14 21:00 | 4.6842
2022-08-14 22:00 | 4.6473
2022-08-14 23:00 | 4.6931
2022-08-15 | 4.7377
2022-08-15 01:00 | 4.7515
2022-08-15 02:00 | 4.7387
2022-08-15 03:00 | 4.7229
2022-08-15 04:00 | 4.8046
2022-08-15 05:00 | 4.8037
2022-08-15 06:00 | 12.0351
2022-08-15 07:00 | 12.0351
2022-08-15 08:00 | 12.0351
2022-08-15 09:00 | 12.0351
2022-08-15 10:00 | 12.0351
2022-08-15 11:00 | 12.0351
2022-08-15 12:00 | 12.0351
2022-08-15 13:00 | 12.0351
2022-08-15 14:00 | 12.0351
2022-08-15 15:00 | 12.0351
2022-08-15 16:00 | 12.0351
2022-08-15 17:00 | 12.0351
2022-08-15 18:00 | 12.0351
2022-08-15 19:00 | 8.4797
2022-08-15 20:00 | 5.9572
2022-08-15 21:00 | 5.9297
2022-08-15 22:00 | 5.91
2022-08-15 23:00 | 5.9462
2022-08-16 | 5.9868
2022-08-16 01:00 | 6.023
2022-08-16 02:00 | 6.0045
2022-08-16 03:00 | 6.0191
2022-08-16 04:00 | 6.0474
2022-08-16 05:00 | 6.0443
2022-08-16 06:00 | 12.0351
2022-08-16 07:00 | 12.0351
2022-08-16 08:00 | 12.0351
2022-08-16 09:00 | 12.0351
2022-08-16 10:00 | 12.0351
2022-08-16 11:00 | 12.0351
2022-08-16 12:00 | 12.0351
2022-08-16 13:00 | 12.0351
2022-08-16 14:00 | 12.0351
2022-08-16 15:00 | 12.0351
2022-08-16 16:00 | 12.0351
2022-08-16 17:00 | 12.0351
2022-08-16 18:00 | 7.0108
2022-08-16 19:00 | 5.9384
2022-08-16 20:00 | 5.965
2022-08-16 21:00 | 5.925
2022-08-16 22:00 | 5.9187
2022-08-16 23:00 | 5.9556
2022-08-17 | 5.9813
2022-08-17 01:00 | 6.0145
2022-08-17 02:00 | 5.9844
2022-08-17 03:00 | 6.0298
2022-08-17 04:00 | 6.0489
2022-08-17 05:00 | 6.0761
2022-08-17 06:00 | 12.0351
2022-08-17 07:00 | 12.0351
2022-08-17 08:00 | 12.0351
2022-08-17 09:00 | 12.0351
2022-08-17 10:00 | 12.0351
2022-08-17 11:00 | 12.0351
2022-08-17 12:00 | 12.0351
2022-08-17 13:00 | 12.0351
2022-08-17 14:00 | 12.0351
2022-08-17 15:00 | 12.0351
2022-08-17 16:00 | 12.0351
2022-08-17 17:00 | 12.0351
2022-08-17 18:00 | 12.0351
2022-08-17 19:00 | 12.0351
2022-08-17 20:00 | 12.0351
2022-08-17 21:00 | 8.7912
2022-08-17 22:00 | 5.9837
2022-08-17 23:00 | 5.9991
2022-08-18 | 6.013
2022-08-18 01:00 | 5.9991
2022-08-18 02:00 | 6.0076
2022-08-18 03:00 | 6.039
2022-08-18 04:00 | 6.0708
2022-08-18 05:00 | 6.0678
2022-08-18 06:00 | 12.0351
2022-08-18 07:00 | 12.0351
2022-08-18 08:00 | 12.0351
2022-08-18 09:00 | 12.0351
2022-08-18 10:00 | 12.0351
2022-08-18 11:00 | 12.0351
2022-08-18 12:00 | 12.0351
2022-08-18 13:00 | 12.0351
2022-08-18 14:00 | 12.0351
2022-08-18 15:00 | 12.0351
2022-08-18 16:00 | 12.0351
2022-08-18 17:00 | 7.7981
2022-08-18 18:00 | 5.9976
2022-08-18 19:00 | 5.986
2022-08-18 20:00 | 5.9642
2022-08-18 21:00 | 5.9976
2022-08-18 22:00 | 5.9681
2022-08-18 23:00 | 5.986
2022-08-19 | 6.0222
2022-08-19 01:00 | 5.9704
2022-08-19 02:00 | 6.0314
2022-08-19 03:00 | 6.0161
2022-08-19 04:00 | 6.0625
2022-08-19 05:00 | 6.3511
2022-08-19 06:00 | 12.0351
2022-08-19 07:00 | 12.0351
2022-08-19 08:00 | 12.0351
2022-08-19 09:00 | 12.0351
2022-08-19 10:00 | 12.0351
2022-08-19 11:00 | 12.0351
2022-08-19 12:00 | 12.0351
2022-08-19 13:00 | 12.0351
2022-08-19 14:00 | 12.0351
2022-08-19 15:00 | 12.0351
2022-08-19 16:00 | 12.0351
2022-08-19 17:00 | 12.0351
2022-08-19 18:00 | 6.0161
2022-08-19 19:00 | 6.0352
2022-08-19 20:00 | 6.0176
2022-08-19 21:00 | 6.0107
2022-08-19 22:00 | 5.9744
2022-08-19 23:00 | 5.9439
2022-08-20 | 5.9767
2022-08-20 01:00 | 6.003
2022-08-20 02:00 | 5.9937
2022-08-20 03:00 | 6.0428
2022-08-20 04:00 | 6.0084
2022-08-20 05:00 | 6.0367
2022-08-20 06:00 | 6.0428
2022-08-20 07:00 | 6.0337
2022-08-20 08:00 | 6.0359
2022-08-20 09:00 | 6.0045
2022-08-20 10:00 | 6.0222
2022-08-20 11:00 | 5.9945
2022-08-20 12:00 | 5.9478
2022-08-20 13:00 | 5.9384
2022-08-20 14:00 | 5.9759
2022-08-20 15:00 | 5.9548
2022-08-20 16:00 | 5.9368
2022-08-20 17:00 | 5.9462
2022-08-20 18:00 | 5.9681
2022-08-20 19:00 | 5.9627
2022-08-20 20:00 | 6.0275
2022-08-20 21:00 | 6.0022
2022-08-20 22:00 | 5.9666
2022-08-20 23:00 | 5.9194
2022-08-21 | 5.986
2022-08-21 01:00 | 5.9759
2022-08-21 02:00 | 6.023
2022-08-21 03:00 | 5.9937
2022-08-21 04:00 | 6.0268
2022-08-21 05:00 | 6.0405
2022-08-21 06:00 | 6.0565
2022-08-21 07:00 | 6.0474
2022-08-21 08:00 | 6.0896
2022-08-21 09:00 | 6.0474
2022-08-21 10:00 | 6.0091
2022-08-21 11:00 | 5.9806
2022-08-21 12:00 | 5.9751
2022-08-21 13:00 | 5.9423
2022-08-21 14:00 | 5.9596
2022-08-21 15:00 | 5.9634
2022-08-21 16:00 | 5.9922
2022-08-21 17:00 | 5.9455
2022-08-21 18:00 | 5.9587
2022-08-21 19:00 | 5.9899
2022-08-21 20:00 | 5.979
2022-08-21 21:00 | 5.9844
2022-08-21 22:00 | 5.9392
2022-08-21 23:00 | 5.9187
2022-08-22 | 5.9525
2022-08-22 01:00 | 5.9548
2022-08-22 02:00 | 6.0176
2022-08-22 03:00 | 6.0099
2022-08-22 04:00 | 6.0321
2022-08-22 05:00 | 6.5804
2022-08-22 06:00 | 12.0351
2022-08-22 07:00 | 12.0351
2022-08-22 08:00 | 12.0351
2022-08-22 09:00 | 12.0351
2022-08-22 10:00 | 12.0351
2022-08-22 11:00 | 12.0351
2022-08-22 12:00 | 12.0351
2022-08-22 13:00 | 12.0351
2022-08-22 14:00 | 12.0351
2022-08-22 15:00 | 12.0351
2022-08-22 16:00 | 12.0351
2022-08-22 17:00 | 12.0351
2022-08-22 18:00 | 4.7119
2022-08-22 19:00 | 4.7297
2022-08-22 20:00 | 4.6891
2022-08-22 21:00 | 4.6931
2022-08-22 22:00 | 4.6523
2022-08-22 23:00 | 4.6443
2022-08-23 | 4.6742
2022-08-23 01:00 | 4.6921
2022-08-23 02:00 | 4.7218
2022-08-23 03:00 | 4.7001
2022-08-23 04:00 | 4.7139
2022-08-23 05:00 | 4.7614
2022-08-23 06:00 | 12.0351
2022-08-23 07:00 | 12.0351
2022-08-23 08:00 | 12.0351
2022-08-23 09:00 | 12.0351
2022-08-23 10:00 | 12.0351
2022-08-23 11:00 | 12.0351
2022-08-23 12:00 | 12.0351
2022-08-23 13:00 | 12.0351
2022-08-23 14:00 | 12.0351
2022-08-23 15:00 | 12.0351
2022-08-23 16:00 | 12.0351
2022-08-23 17:00 | 11.7079
2022-08-23 18:00 | 5.9036
2022-08-23 19:00 | 5.8989
2022-08-23 20:00 | 5.9392
2022-08-23 21:00 | 5.9123
2022-08-23 22:00 | 5.8805
2022-08-23 23:00 | 5.8581
2022-08-24 | 5.8733
2022-08-24 01:00 | 5.9021
2022-08-24 02:00 | 5.898
2022-08-24 03:00 | 5.9084
2022-08-24 04:00 | 5.9092
2022-08-24 05:00 | 7.3706
2022-08-24 06:00 | 12.0351
2022-08-24 07:00 | 12.0351
2022-08-24 08:00 | 12.0351
2022-08-24 09:00 | 12.0351
2022-08-24 10:00 | 12.0351
2022-08-24 11:00 | 12.0351
2022-08-24 12:00 | 12.0351
2022-08-24 13:00 | 7.955
2022-08-24 14:00 | 4.5742
2022-08-24 15:00 | 11.0526
2022-08-24 16:00 | 12.0351
2022-08-24 17:00 | 12.0351
2022-08-24 18:00 | 12.0351
2022-08-24 19:00 | 12.0351
2022-08-24 20:00 | 12.0351
2022-08-24 21:00 | 12.0351
2022-08-24 22:00 | 5.91
2022-08-24 23:00 | 5.8468
2022-08-25 | 5.8533
2022-08-25 01:00 | 5.929
2022-08-25 02:00 | 5.9782
2022-08-25 03:00 | 5.9945
2022-08-25 04:00 | 5.9837
2022-08-25 05:00 | 6.013
2022-08-25 06:00 | 12.0351
2022-08-25 07:00 | 12.0351
2022-08-25 08:00 | 12.0351
2022-08-25 09:00 | 12.0351
2022-08-25 10:00 | 12.0351
2022-08-25 11:00 | 12.0351
2022-08-25 12:00 | 12.0351
2022-08-25 13:00 | 12.0351
2022-08-25 14:00 | 12.0351
2022-08-25 15:00 | 12.0351
2022-08-25 16:00 | 12.0351
2022-08-25 17:00 | 12.0351
2022-08-25 18:00 | 6.7248
2022-08-25 19:00 | 6.7596
2022-08-25 20:00 | 6.7695
2022-08-25 21:00 | 6.7276
2022-08-25 22:00 | 6.7106
2022-08-25 23:00 | 6.6997
2022-08-26 | 6.6997
2022-08-26 01:00 | 6.7316
2022-08-26 02:00 | 6.7372
2022-08-26 03:00 | 6.7607
2022-08-26 04:00 | 6.7728
2022-08-26 05:00 | 7.7388
2022-08-26 06:00 | 12.0351
2022-08-26 07:00 | 12.0351
2022-08-26 08:00 | 12.0351
2022-08-26 09:00 | 12.0351
2022-08-26 10:00 | 12.0351
2022-08-26 11:00 | 12.0351
2022-08-26 12:00 | 12.0351
2022-08-26 13:00 | 12.0351
2022-08-26 14:00 | 12.0351
2022-08-26 15:00 | 12.0351
2022-08-26 16:00 | 12.0351
2022-08-26 17:00 | 7.7667
2022-08-26 18:00 | 5.2189
2022-08-26 19:00 | 5.1966
2022-08-26 20:00 | 5.1752
2022-08-26 21:00 | 5.1966
2022-08-26 22:00 | 5.1697
2022-08-26 23:00 | 5.1069
2022-08-27 | 5.1752
2022-08-27 01:00 | 5.1892
2022-08-27 02:00 | 5.1585
2022-08-27 03:00 | 5.192
2022-08-27 04:00 | 5.1688
2022-08-27 05:00 | 5.1957
2022-08-27 06:00 | 5.1855
2022-08-27 07:00 | 5.192
2022-08-27 08:00 | 5.2346
2022-08-27 09:00 | 5.1902
2022-08-27 10:00 | 5.2245
2022-08-27 11:00 | 5.1994
2022-08-27 12:00 | 5.2115
2022-08-27 13:00 | 5.1725
2022-08-27 14:00 | 5.1706
2022-08-27 15:00 | 5.1049
2022-08-27 16:00 | 5.1228
2022-08-27 17:00 | 5.1003
2022-08-27 18:00 | 5.1463
2022-08-27 19:00 | 5.1435
2022-08-27 20:00 | 5.1322
2022-08-27 21:00 | 5.1613
2022-08-27 22:00 | 5.1715
2022-08-27 23:00 | 5.1228
2022-08-28 | 5.1669
2022-08-28 01:00 | 5.1538
2022-08-28 02:00 | 5.1659
2022-08-28 03:00 | 5.1809
2022-08-28 04:00 | 5.1994
2022-08-28 05:00 | 5.1566
2022-08-28 06:00 | 5.2254
2022-08-28 07:00 | 5.1985
2022-08-28 08:00 | 5.2217
2022-08-28 09:00 | 5.2466
2022-08-28 10:00 | 5.23
2022-08-28 11:00 | 5.2208
2022-08-28 12:00 | 5.178
2022-08-28 13:00 | 5.1669
2022-08-28 14:00 | 5.1594
2022-08-28 15:00 | 5.1799
2022-08-28 16:00 | 5.1948
2022-08-28 17:00 | 5.2273
2022-08-28 18:00 | 5.2134
2022-08-28 19:00 | 5.242
2022-08-28 20:00 | 5.2346
2022-08-28 21:00 | 5.218
2022-08-28 22:00 | 5.1874
2022-08-28 23:00 | 5.1827
2022-08-29 | 5.1752
2022-08-29 01:00 | 5.1985
2022-08-29 02:00 | 5.2189
2022-08-29 03:00 | 5.2199
2022-08-29 04:00 | 5.2199
2022-08-29 05:00 | 5.2558
2022-08-29 06:00 | 12.0351
2022-08-29 07:00 | 12.0351
2022-08-29 08:00 | 12.0351
2022-08-29 09:00 | 12.0351
2022-08-29 10:00 | 12.0351
2022-08-29 11:00 | 12.0351
2022-08-29 12:00 | 12.0351
2022-08-29 13:00 | 12.0351
2022-08-29 14:00 | 12.0351
2022-08-29 15:00 | 12.0351
2022-08-29 16:00 | 12.0351
2022-08-29 17:00 | 12.0351
2022-08-29 18:00 | 5.3398
2022-08-29 19:00 | 2.7952
2022-08-29 20:00 | 2.7701
2022-08-29 21:00 | 2.8344
2022-08-29 22:00 | 2.8445
2022-08-29 23:00 | 2.7892
2022-08-30 | 2.7571
2022-08-30 01:00 | 2.8083
2022-08-30 02:00 | 2.8093
2022-08-30 03:00 | 2.8073
2022-08-30 04:00 | 2.8314
2022-08-30 05:00 | 6.539
2022-08-30 06:00 | 12.0351
2022-08-30 07:00 | 12.0351
2022-08-30 08:00 | 12.0351
2022-08-30 09:00 | 12.0351
2022-08-30 10:00 | 12.0351
2022-08-30 11:00 | 12.0351
2022-08-30 12:00 | 12.0351
2022-08-30 13:00 | 12.0351
2022-08-30 14:00 | 12.0351
2022-08-30 15:00 | 12.0351
2022-08-30 16:00 | 12.0351
2022-08-30 17:00 | 7.0975
2022-08-30 18:00 | 4.6143
2022-08-30 19:00 | 4.5903
2022-08-30 20:00 | 4.6043
2022-08-30 21:00 | 4.5662
2022-08-30 22:00 | 4.5692
2022-08-30 23:00 | 4.6133
2022-08-31 | 4.6053
2022-08-31 01:00 | 4.5983
2022-08-31 02:00 | 4.6114
2022-08-31 03:00 | 4.6802
2022-08-31 04:00 | 4.6613
2022-08-31 05:00 | 4.8779
2022-08-31 06:00 | 12.0351
2022-08-31 07:00 | 12.0351
2022-08-31 08:00 | 12.0351
2022-08-31 09:00 | 12.0351
2022-08-31 10:00 | 12.0351
2022-08-31 11:00 | 12.0351
2022-08-31 12:00 | 12.0351
2022-08-31 13:00 | 12.0351
2022-08-31 14:00 | 12.0351
2022-08-31 15:00 | 12.0351
2022-08-31 16:00 | 12.0351
2022-08-31 17:00 | 7.5635
2022-08-31 18:00 | 4.6931
2022-08-31 19:00 | 4.6812
2022-08-31 20:00 | 4.7001
2022-08-31 21:00 | 4.6573
2022-08-31 22:00 | 4.6961
2022-08-31 23:00 | 4.6782
2022-09-01 | 4.6971
2022-09-01 01:00 | 4.6742
2022-09-01 02:00 | 4.706
2022-09-01 03:00 | 4.705
2022-09-01 04:00 | 4.7238
2022-09-01 05:00 | 7.8604
2022-09-01 06:00 | 12.0351
2022-09-01 07:00 | 12.0351
2022-09-01 08:00 | 12.0351
2022-09-01 09:00 | 12.0351
2022-09-01 10:00 | 12.0351
2022-09-01 11:00 | 12.0351
2022-09-01 12:00 | 12.0351
2022-09-01 13:00 | 12.0351
2022-09-01 14:00 | 12.0351
2022-09-01 15:00 | 12.0351
2022-09-01 16:00 | 12.0351
2022-09-01 17:00 | 11.313
2022-09-01 18:00 | 4.7485
2022-09-01 19:00 | 4.7357
2022-09-01 20:00 | 4.7248
2022-09-01 21:00 | 4.6852
2022-09-01 22:00 | 4.705
2022-09-01 23:00 | 4.7791
2022-09-02 | 4.7928
2022-09-02 01:00 | 4.7643
2022-09-02 02:00 | 4.7889
2022-09-02 03:00 | 4.7958
2022-09-02 04:00 | 4.8301
2022-09-02 05:00 | 10.8311
2022-09-02 06:00 | 12.0351
2022-09-02 07:00 | 12.0351
2022-09-02 08:00 | 12.0351
2022-09-02 09:00 | 12.0351
2022-09-02 10:00 | 12.0351
2022-09-02 11:00 | 12.0351
2022-09-02 12:00 | 12.0351
2022-09-02 13:00 | 12.0351
2022-09-02 14:00 | 12.0351
2022-09-02 15:00 | 12.0351
2022-09-02 16:00 | 12.0351
2022-09-02 17:00 | 12.1794
2022-09-02 18:00 | 4.8174
2022-09-02 19:00 | 4.7977
2022-09-02 20:00 | 4.7712
2022-09-02 21:00 | 4.7288
2022-09-02 22:00 | 4.7149
2022-09-02 23:00 | 4.703
2022-09-03 | 4.6911
2022-09-03 01:00 | 4.7297
2022-09-03 02:00 | 4.7683
2022-09-03 03:00 | 4.7584
2022-09-03 04:00 | 4.7594
2022-09-03 05:00 | 4.785
2022-09-03 06:00 | 4.835
2022-09-03 07:00 | 4.8095
2022-09-03 08:00 | 4.8223
2022-09-03 09:00 | 4.7475
2022-09-03 10:00 | 4.7149
2022-09-03 11:00 | 4.7475
2022-09-03 12:00 | 4.7099
2022-09-03 13:00 | 4.7288
2022-09-03 14:00 | 4.7149
2022-09-03 15:00 | 4.7238
2022-09-03 16:00 | 4.7129
2022-09-03 17:00 | 4.704
2022-09-03 18:00 | 4.7229
2022-09-03 19:00 | 4.7584
2022-09-03 20:00 | 4.7406
2022-09-03 21:00 | 4.7149
2022-09-03 22:00 | 4.7139
2022-09-03 23:00 | 4.6901
2022-09-04 | 4.704
2022-09-04 01:00 | 4.703
2022-09-04 02:00 | 4.7466
2022-09-04 03:00 | 4.7416
2022-09-04 04:00 | 4.7554
2022-09-04 05:00 | 4.6921
2022-09-04 06:00 | 4.7297
2022-09-04 07:00 | 4.7199
2022-09-04 08:00 | 4.706
2022-09-04 09:00 | 4.7466
2022-09-04 10:00 | 4.7099
2022-09-04 11:00 | 4.6573
2022-09-04 12:00 | 4.6642
2022-09-04 13:00 | 4.6344
2022-09-04 14:00 | 4.6692
2022-09-04 15:00 | 4.6274
2022-09-04 16:00 | 4.6253
2022-09-04 17:00 | 4.5933
2022-09-04 18:00 | 4.6283
2022-09-04 19:00 | 4.5963
2022-09-04 20:00 | 4.5551
2022-09-04 21:00 | 4.5853
2022-09-04 22:00 | 4.5601
2022-09-04 23:00 | 4.5792
2022-09-05 | 4.6523
2022-09-05 01:00 | 4.6083
2022-09-05 02:00 | 4.6003
2022-09-05 03:00 | 4.5963
2022-09-05 04:00 | 4.6143
2022-09-05 05:00 | 4.6253
2022-09-05 06:00 | 4.6313
2022-09-05 07:00 | 4.6483
2022-09-05 08:00 | 5.0861
2022-09-05 09:00 | 6.7146
2022-09-05 10:00 | 6.6707
2022-09-05 11:00 | 6.6707
2022-09-05 12:00 | 6.6537
2022-09-05 13:00 | 6.606
2022-09-05 14:00 | 6.6011
2022-09-05 15:00 | 6.5871
2022-09-05 16:00 | 6.5774
2022-09-05 17:00 | 6.5731
2022-09-05 18:00 | 6.5847
2022-09-05 19:00 | 6.5823
2022-09-05 20:00 | 6.5712
2022-09-05 21:00 | 6.5829
2022-09-05 22:00 | 6.5963
2022-09-05 23:00 | 6.6017
2022-09-06 | 6.6084
2022-09-06 01:00 | 6.6324
2022-09-06 02:00 | 6.6413
2022-09-06 03:00 | 6.6997
2022-09-06 04:00 | 6.7254
2022-09-06 05:00 | 10.2868
2022-09-06 06:00 | 12.0351
2022-09-06 07:00 | 12.0351
2022-09-06 08:00 | 12.0351
2022-09-06 09:00 | 12.0351
2022-09-06 10:00 | 12.0351
2022-09-06 11:00 | 12.0351
2022-09-06 12:00 | 12.0351
2022-09-06 13:00 | 12.0351
2022-09-06 14:00 | 12.0351
2022-09-06 15:00 | 12.0351
2022-09-06 16:00 | 12.0351
2022-09-06 17:00 | 12.0351
2022-09-06 18:00 | 12.0351
2022-09-06 19:00 | 12.0351
2022-09-06 20:00 | 12.0351
2022-09-06 21:00 | 4.6881
2022-09-06 22:00 | 4.7149
2022-09-06 23:00 | 4.6443
2022-09-07 | 4.6702
2022-09-07 01:00 | 4.6602
2022-09-07 02:00 | 4.711
2022-09-07 03:00 | 4.702
2022-09-07 04:00 | 4.7119
2022-09-07 05:00 | 12.0351
2022-09-07 06:00 | 12.0351
2022-09-07 07:00 | 12.0351
2022-09-07 08:00 | 12.0351
2022-09-07 09:00 | 12.0351
2022-09-07 10:00 | 12.0351
2022-09-07 11:00 | 12.0351
2022-09-07 12:00 | 12.0351
2022-09-07 13:00 | 12.0351
2022-09-07 14:00 | 12.0351
2022-09-07 15:00 | 12.0351
2022-09-07 16:00 | 12.0351
2022-09-07 17:00 | 10.0955
2022-09-07 18:00 | 4.6772
2022-09-07 19:00 | 4.7099
2022-09-07 20:00 | 4.6871
2022-09-07 21:00 | 4.6623
2022-09-07 22:00 | 4.6613
2022-09-07 23:00 | 4.6523
2022-09-08 | 4.6792
2022-09-08 01:00 | 4.6533
2022-09-08 02:00 | 4.6822
2022-09-08 03:00 | 4.7357
2022-09-08 04:00 | 4.7099
2022-09-08 05:00 | 12.0351
2022-09-08 06:00 | 12.0351
2022-09-08 07:00 | 12.0351
2022-09-08 08:00 | 12.0351
2022-09-08 09:00 | 12.0351
2022-09-08 10:00 | 12.0351
2022-09-08 11:00 | 12.0351
2022-09-08 12:00 | 12.0351
2022-09-08 13:00 | 12.0351
2022-09-08 14:00 | 12.0351
2022-09-08 15:00 | 12.0351
2022-09-08 16:00 | 12.0351
2022-09-08 17:00 | 12.0351
2022-09-08 18:00 | 4.6752
2022-09-08 19:00 | 4.7396
2022-09-08 20:00 | 4.7001
2022-09-08 21:00 | 4.704
2022-09-08 22:00 | 4.6812
2022-09-08 23:00 | 4.6632
2022-09-09 | 4.6901
2022-09-09 01:00 | 4.7535
2022-09-09 02:00 | 4.7179
2022-09-09 03:00 | 4.7377
2022-09-09 04:00 | 4.7456
2022-09-09 05:00 | 12.0351
2022-09-09 06:00 | 12.0351
2022-09-09 07:00 | 12.0351
2022-09-09 08:00 | 12.0351
2022-09-09 09:00 | 12.0351
2022-09-09 10:00 | 12.0351
2022-09-09 11:00 | 12.0351
2022-09-09 12:00 | 12.0351
2022-09-09 13:00 | 12.0351
2022-09-09 14:00 | 12.0351
2022-09-09 15:00 | 12.0351
2022-09-09 16:00 | 12.0351
2022-09-09 17:00 | 4.7475
2022-09-09 18:00 | 4.7574
2022-09-09 19:00 | 4.7604
2022-09-09 20:00 | 4.6792
2022-09-09 21:00 | 4.695
2022-09-09 22:00 | 4.7367
2022-09-09 23:00 | 4.6831
2022-09-10 | 4.7179
2022-09-10 01:00 | 4.788
2022-09-10 02:00 | 4.8085
2022-09-10 03:00 | 4.7958
2022-09-10 04:00 | 4.7988
2022-09-10 05:00 | 4.784
2022-09-10 06:00 | 4.7988
2022-09-10 07:00 | 4.8242
2022-09-10 08:00 | 4.8232
2022-09-10 09:00 | 4.8262
2022-09-10 10:00 | 4.8066
2022-09-10 11:00 | 4.788
2022-09-10 12:00 | 4.7436
2022-09-10 13:00 | 4.7288
2022-09-10 14:00 | 4.7505
2022-09-10 15:00 | 4.7218
2022-09-10 16:00 | 4.7337
2022-09-10 17:00 | 4.7377
2022-09-10 18:00 | 4.6861
2022-09-10 19:00 | 4.7387
2022-09-10 20:00 | 4.7199
2022-09-10 21:00 | 4.7268
2022-09-10 22:00 | 4.7208
2022-09-10 23:00 | 4.702
2022-09-11 | 4.702
2022-09-11 01:00 | 4.7643
2022-09-11 02:00 | 4.7909
2022-09-11 03:00 | 4.7811
2022-09-11 04:00 | 4.786
2022-09-11 05:00 | 4.7673
2022-09-11 06:00 | 4.786
2022-09-11 07:00 | 4.8037
2022-09-11 08:00 | 4.8418
2022-09-11 09:00 | 4.7997
2022-09-11 10:00 | 4.782
2022-09-11 11:00 | 4.7515
2022-09-11 12:00 | 4.7663
2022-09-11 13:00 | 4.7554
2022-09-11 14:00 | 4.7791
2022-09-11 15:00 | 4.7732
2022-09-11 16:00 | 4.7594
2022-09-11 17:00 | 4.7139
2022-09-11 18:00 | 4.7387
2022-09-11 19:00 | 4.7258
2022-09-11 20:00 | 4.7466
2022-09-11 21:00 | 4.7119
2022-09-11 22:00 | 4.6642
2022-09-11 23:00 | 4.7268
2022-09-12 | 4.787
2022-09-12 01:00 | 4.7574
2022-09-12 02:00 | 4.7762
2022-09-12 03:00 | 4.7574
2022-09-12 04:00 | 4.7919
2022-09-12 05:00 | 8.9029
2022-09-12 06:00 | 12.0351
2022-09-12 07:00 | 12.0351
2022-09-12 08:00 | 12.0351
2022-09-12 09:00 | 12.0351
2022-09-12 10:00 | 12.0351
2022-09-12 11:00 | 12.0351
2022-09-12 12:00 | 12.0351
2022-09-12 13:00 | 12.0351
2022-09-12 14:00 | 12.0351
2022-09-12 15:00 | 12.0351
2022-09-12 16:00 | 12.0351
2022-09-12 17:00 | 7.2219
2022-09-12 18:00 | 6.6566
2022-09-12 19:00 | 6.6573
2022-09-12 20:00 | 6.6437
2022-09-12 21:00 | 6.6425
2022-09-12 22:00 | 6.6508
2022-09-12 23:00 | 6.6637
2022-09-13 | 6.6962
2022-09-13 01:00 | 6.7406
2022-09-13 02:00 | 6.7163
2022-09-13 03:00 | 6.7276
2022-09-13 04:00 | 6.731
2022-09-13 05:00 | 8.4404
2022-09-13 06:00 | 12.0351
2022-09-13 07:00 | 12.0351
2022-09-13 08:00 | 12.0351
2022-09-13 09:00 | 12.0351
2022-09-13 10:00 | 12.0351
2022-09-13 11:00 | 12.0351
2022-09-13 12:00 | 12.0351
2022-09-13 13:00 | 12.0351
2022-09-13 14:00 | 12.0351
2022-09-13 15:00 | 12.0351
2022-09-13 16:00 | 12.0351
2022-09-13 17:00 | 12.0351
2022-09-13 18:00 | 7.204
2022-09-13 19:00 | 4.5752
2022-09-13 20:00 | 4.5933
2022-09-13 21:00 | 4.6403
2022-09-13 22:00 | 4.5883
2022-09-13 23:00 | 4.6602
2022-09-14 | 4.6802
2022-09-14 01:00 | 4.706
2022-09-14 02:00 | 4.702
2022-09-14 03:00 | 4.7317
2022-09-14 04:00 | 4.7801
2022-09-14 05:00 | 7.334
2022-09-14 06:00 | 12.0351
2022-09-14 07:00 | 12.0351
2022-09-14 08:00 | 12.0351
2022-09-14 09:00 | 12.0351
2022-09-14 10:00 | 12.0351
2022-09-14 11:00 | 12.0351
2022-09-14 12:00 | 12.0351
2022-09-14 13:00 | 12.0351
2022-09-14 14:00 | 12.0351
2022-09-14 15:00 | 12.0351
2022-09-14 16:00 | 12.0351
2022-09-14 17:00 | 9.2047
2022-09-14 18:00 | 6.6126
2022-09-14 19:00 | 6.6672
2022-09-14 20:00 | 6.6502
2022-09-14 21:00 | 6.6514
2022-09-14 22:00 | 6.6372
2022-09-14 23:00 | 6.6573
2022-09-15 | 6.7191
2022-09-15 01:00 | 6.718
2022-09-15 02:00 | 6.7411
2022-09-15 03:00 | 6.7338
2022-09-15 04:00 | 6.7629
2022-09-15 05:00 | 8.2246
2022-09-15 06:00 | 12.0351
2022-09-15 07:00 | 12.0351
2022-09-15 08:00 | 12.0351
2022-09-15 09:00 | 12.0351
2022-09-15 10:00 | 12.0351
2022-09-15 11:00 | 12.0351
2022-09-15 12:00 | 12.0351
2022-09-15 13:00 | 12.0351
2022-09-15 14:00 | 12.0351
2022-09-15 15:00 | 12.0351
2022-09-15 16:00 | 12.0351
2022-09-15 17:00 | 4.7623
2022-09-15 18:00 | 4.7643
2022-09-15 19:00 | 4.8007
2022-09-15 20:00 | 4.7968
2022-09-15 21:00 | 4.8027
2022-09-15 22:00 | 4.8398
2022-09-15 23:00 | 4.8789
2022-09-16 | 4.9467
2022-09-16 01:00 | 4.8924
2022-09-16 02:00 | 4.9582
2022-09-16 03:00 | 4.9573
2022-09-16 04:00 | 4.9611
2022-09-16 05:00 | 8.597
2022-09-16 06:00 | 12.0351
2022-09-16 07:00 | 12.0351
2022-09-16 08:00 | 12.0351
2022-09-16 09:00 | 12.0351
2022-09-16 10:00 | 12.0351
2022-09-16 11:00 | 12.0351
2022-09-16 12:00 | 12.0351
2022-09-16 13:00 | 12.0351
2022-09-16 14:00 | 12.0351
2022-09-16 15:00 | 12.0351
2022-09-16 16:00 | 12.0351
2022-09-16 17:00 | 12.0351
2022-09-16 18:00 | 12.0351
2022-09-16 19:00 | 4.8252
2022-09-16 20:00 | 4.8027
2022-09-16 21:00 | 4.835
2022-09-16 22:00 | 4.8007
2022-09-16 23:00 | 4.8418
2022-09-17 | 4.8184
2022-09-17 01:00 | 4.8017
2022-09-17 02:00 | 4.8085
2022-09-17 03:00 | 4.7889
2022-09-17 04:00 | 4.7712
2022-09-17 05:00 | 4.8477
2022-09-17 06:00 | 4.8213
2022-09-17 07:00 | 4.8085
2022-09-17 08:00 | 4.8066
2022-09-17 09:00 | 4.8017
2022-09-17 10:00 | 4.8017
2022-09-17 11:00 | 4.8007
2022-09-17 12:00 | 4.8056
2022-09-17 13:00 | 4.7574
2022-09-17 14:00 | 4.7928
2022-09-17 15:00 | 4.8027
2022-09-17 16:00 | 4.7997
2022-09-17 17:00 | 4.786
2022-09-17 18:00 | 4.7515
2022-09-17 19:00 | 4.786
2022-09-17 20:00 | 4.7633
2022-09-17 21:00 | 4.7495
2022-09-17 22:00 | 4.7278
2022-09-17 23:00 | 4.701
2022-09-18 | 4.7179
2022-09-18 01:00 | 4.7584
2022-09-18 02:00 | 4.7485
2022-09-18 03:00 | 4.709
2022-09-18 04:00 | 4.8037
2022-09-18 05:00 | 4.7997
2022-09-18 06:00 | 4.7732
2022-09-18 07:00 | 4.7919
2022-09-18 08:00 | 4.8379
2022-09-18 09:00 | 4.8203
2022-09-18 10:00 | 4.7426
2022-09-18 11:00 | 4.699
2022-09-18 12:00 | 4.6941
2022-09-18 13:00 | 4.7139
2022-09-18 14:00 | 4.7149
2022-09-18 15:00 | 4.6602
2022-09-18 16:00 | 4.6363
2022-09-18 17:00 | 4.6523
2022-09-18 18:00 | 4.6503
2022-09-18 19:00 | 4.6752
2022-09-18 20:00 | 4.6901
2022-09-18 21:00 | 4.695
2022-09-18 22:00 | 4.6901
2022-09-18 23:00 | 4.6483
2022-09-19 | 4.705
2022-09-19 01:00 | 4.6344
2022-09-19 02:00 | 4.7446
2022-09-19 03:00 | 4.6852
2022-09-19 04:00 | 4.704
2022-09-19 05:00 | 10.3309
2022-09-19 06:00 | 12.0351
2022-09-19 07:00 | 12.0351
2022-09-19 08:00 | 12.0351
2022-09-19 09:00 | 12.0351
2022-09-19 10:00 | 12.0351
2022-09-19 11:00 | 12.0351
2022-09-19 12:00 | 12.0351
2022-09-19 13:00 | 12.0351
2022-09-19 14:00 | 12.0351
2022-09-19 15:00 | 12.0351
2022-09-19 16:00 | 12.0351
2022-09-19 17:00 | 12.0351
2022-09-19 18:00 | 4.6304
2022-09-19 19:00 | 4.6154
2022-09-19 20:00 | 4.5993
2022-09-19 21:00 | 4.6383
2022-09-19 22:00 | 4.5792
2022-09-19 23:00 | 4.6083
2022-09-20 | 4.6013
2022-09-20 01:00 | 4.5993
2022-09-20 02:00 | 4.7278
2022-09-20 03:00 | 4.703
2022-09-20 04:00 | 4.7129
2022-09-20 05:00 | 10.116
2022-09-20 06:00 | 12.0351
2022-09-20 07:00 | 12.0351
2022-09-20 08:00 | 12.0351
2022-09-20 09:00 | 12.0351
2022-09-20 10:00 | 12.0351
2022-09-20 11:00 | 12.0351
2022-09-20 12:00 | 12.0351
2022-09-20 13:00 | 12.0351
2022-09-20 14:00 | 12.0351
2022-09-20 15:00 | 12.0351
2022-09-20 16:00 | 12.0351
2022-09-20 17:00 | 12.0351
2022-09-20 18:00 | 6.669
2022-09-20 19:00 | 6.6341
2022-09-20 20:00 | 6.6372
2022-09-20 21:00 | 6.6514
2022-09-20 22:00 | 6.6602
2022-09-20 23:00 | 6.6502
2022-09-21 | 6.6707
2022-09-21 01:00 | 6.706
2022-09-21 02:00 | 6.6951
2022-09-21 03:00 | 6.6818
2022-09-21 04:00 | 6.7231
2022-09-21 05:00 | 12.0351
2022-09-21 06:00 | 12.0351
2022-09-21 07:00 | 12.0351
2022-09-21 08:00 | 12.0351
2022-09-21 09:00 | 12.0351
2022-09-21 10:00 | 12.0351
2022-09-21 11:00 | 12.0351
2022-09-21 12:00 | 12.0351
2022-09-21 13:00 | 12.0351
2022-09-21 14:00 | 12.0351
2022-09-21 15:00 | 12.0351
2022-09-21 16:00 | 12.0351
2022-09-21 17:00 | 10.5944
2022-09-21 18:00 | 4.6602
2022-09-21 19:00 | 4.6224
2022-09-21 20:00 | 4.6154
2022-09-21 21:00 | 4.6363
2022-09-21 22:00 | 4.6323
2022-09-21 23:00 | 4.5943
2022-09-22 | 4.6722
2022-09-22 01:00 | 4.6752
2022-09-22 02:00 | 4.6503
2022-09-22 03:00 | 4.6463
2022-09-22 04:00 | 4.6243
2022-09-22 05:00 | 8.8396
2022-09-22 06:00 | 12.0351
2022-09-22 07:00 | 12.0351
2022-09-22 08:00 | 12.0351
2022-09-22 09:00 | 12.0351
2022-09-22 10:00 | 12.0351
2022-09-22 11:00 | 12.0351
2022-09-22 12:00 | 12.0351
2022-09-22 13:00 | 12.0351
2022-09-22 14:00 | 12.0351
2022-09-22 15:00 | 12.0351
2022-09-22 16:00 | 12.0351
2022-09-22 17:00 | 12.0351
2022-09-22 18:00 | 4.6103
2022-09-22 19:00 | 4.707
2022-09-22 20:00 | 4.6692
2022-09-22 21:00 | 4.6682
2022-09-22 22:00 | 4.695
2022-09-22 23:00 | 4.7977
2022-09-23 | 4.7545
2022-09-23 01:00 | 4.783
2022-09-23 02:00 | 4.7387
2022-09-23 03:00 | 4.7367
2022-09-23 04:00 | 4.7732
2022-09-23 05:00 | 8.5599
2022-09-23 06:00 | 12.0351
2022-09-23 07:00 | 12.0351
2022-09-23 08:00 | 12.0351
2022-09-23 09:00 | 12.0351
2022-09-23 10:00 | 12.0351
2022-09-23 11:00 | 12.0351
2022-09-23 12:00 | 12.0351
2022-09-23 13:00 | 12.0351
2022-09-23 14:00 | 12.0351
2022-09-23 15:00 | 12.0351
2022-09-23 16:00 | 12.0351
2022-09-23 17:00 | 12.0351
2022-09-23 18:00 | 12.0351
2022-09-23 19:00 | 12.0351
2022-09-23 20:00 | 12.0351
2022-09-23 21:00 | 12.0351
2022-09-23 22:00 | 12.0351
2022-09-23 23:00 | 6.9325
2022-09-24 | 6.9404
2022-09-24 01:00 | 6.9557
2022-09-24 02:00 | 6.9419
2022-09-24 03:00 | 6.9493
2022-09-24 04:00 | 6.9674
2022-09-24 05:00 | 6.9493
2022-09-24 06:00 | 6.9454
2022-09-24 07:00 | 6.9885
2022-09-24 08:00 | 6.9606
2022-09-24 09:00 | 6.9547
2022-09-24 10:00 | 6.91
2022-09-24 11:00 | 6.8937
2022-09-24 12:00 | 6.8628
2022-09-24 13:00 | 6.8555
2022-09-24 14:00 | 6.938
2022-09-24 15:00 | 6.9095
2022-09-24 16:00 | 6.8508
2022-09-24 17:00 | 6.8675
2022-09-24 18:00 | 6.8686
2022-09-24 19:00 | 6.8581
2022-09-24 20:00 | 6.8206
2022-09-24 21:00 | 6.8077
2022-09-24 22:00 | 6.8056
2022-09-24 23:00 | 6.868
2022-09-25 | 6.8244
2022-09-25 01:00 | 6.8147
2022-09-25 02:00 | 6.8286
2022-09-25 03:00 | 6.805
2022-09-25 04:00 | 6.8275
2022-09-25 05:00 | 6.8168
2022-09-25 06:00 | 6.8238
2022-09-25 07:00 | 6.8206
2022-09-25 08:00 | 6.8217
2022-09-25 09:00 | 6.792
2022-09-25 10:00 | 6.805
2022-09-25 11:00 | 6.7866
2022-09-25 12:00 | 6.7434
2022-09-25 13:00 | 6.764
2022-09-25 14:00 | 6.7434
2022-09-25 15:00 | 6.706
2022-09-25 16:00 | 6.6801
2022-09-25 17:00 | 6.7008
2022-09-25 18:00 | 6.6853
2022-09-25 19:00 | 6.6566
2022-09-25 20:00 | 6.6324
2022-09-25 21:00 | 6.6537
2022-09-25 22:00 | 6.6905
2022-09-25 23:00 | 6.7049
2022-09-26 | 6.7174
2022-09-26 01:00 | 6.718
2022-09-26 02:00 | 6.7203
2022-09-26 03:00 | 6.7163
2022-09-26 04:00 | 6.7304
2022-09-26 05:00 | 8.555
2022-09-26 06:00 | 12.0351
2022-09-26 07:00 | 12.0351
2022-09-26 08:00 | 12.0351
2022-09-26 09:00 | 12.0351
2022-09-26 10:00 | 12.0351
2022-09-26 11:00 | 12.0351
2022-09-26 12:00 | 12.0351
2022-09-26 13:00 | 12.0351
2022-09-26 14:00 | 12.0351
2022-09-26 15:00 | 12.0351
2022-09-26 16:00 | 12.0351
2022-09-26 17:00 | 7.3841
2022-09-26 18:00 | 6.5031
2022-09-26 19:00 | 6.6806
2022-09-26 20:00 | 6.6997
2022-09-26 21:00 | 6.7134
2022-09-26 22:00 | 6.7361
2022-09-26 23:00 | 6.7163
2022-09-27 | 6.744
2022-09-27 01:00 | 6.8168
2022-09-27 02:00 | 6.8147
2022-09-27 03:00 | 6.8408
2022-09-27 04:00 | 6.8281
2022-09-27 05:00 | 11.1789
2022-09-27 06:00 | 12.0351
2022-09-27 07:00 | 12.0351
2022-09-27 08:00 | 12.0351
2022-09-27 09:00 | 12.0351
2022-09-27 10:00 | 12.0351
2022-09-27 11:00 | 12.0351
2022-09-27 12:00 | 12.0351
2022-09-27 13:00 | 12.0351
2022-09-27 14:00 | 12.0351
2022-09-27 15:00 | 12.0351
2022-09-27 16:00 | 12.0351
2022-09-27 17:00 | 12.0351
2022-09-27 18:00 | 4.4825
2022-09-27 19:00 | 4.7396
2022-09-27 20:00 | 4.7179
2022-09-27 21:00 | 4.7456
2022-09-27 22:00 | 4.7288
2022-09-27 23:00 | 4.8184
2022-09-28 | 4.782
2022-09-28 01:00 | 4.8076
2022-09-28 02:00 | 4.8545
2022-09-28 03:00 | 4.8565
2022-09-28 04:00 | 4.8779
2022-09-28 05:00 | 7.2671
2022-09-28 06:00 | 12.0351
2022-09-28 07:00 | 12.0351
2022-09-28 08:00 | 12.0351
2022-09-28 09:00 | 12.0351
2022-09-28 10:00 | 12.0351
2022-09-28 11:00 | 12.0351
2022-09-28 12:00 | 12.0351
2022-09-28 13:00 | 12.0351
2022-09-28 14:00 | 12.0351
2022-09-28 15:00 | 12.0351
2022-09-28 16:00 | 12.0351
2022-09-28 17:00 | 7.7694
2022-09-28 18:00 | 4.5139
2022-09-28 19:00 | 4.7919
2022-09-28 20:00 | 4.7317
2022-09-28 21:00 | 4.7899
2022-09-28 22:00 | 4.8496
2022-09-28 23:00 | 4.8428
2022-09-29 | 4.9031
2022-09-29 01:00 | 4.8487
2022-09-29 02:00 | 4.8652
2022-09-29 03:00 | 4.8983
2022-09-29 04:00 | 4.8798
2022-09-29 05:00 | 9.002
2022-09-29 06:00 | 12.0351
2022-09-29 07:00 | 12.0351
2022-09-29 08:00 | 12.0351
2022-09-29 09:00 | 12.0351
2022-09-29 10:00 | 12.0351
2022-09-29 11:00 | 12.0351
2022-09-29 12:00 | 12.0351
2022-09-29 13:00 | 12.0351
2022-09-29 14:00 | 12.0351
2022-09-29 15:00 | 12.0351
2022-09-29 16:00 | 12.0351
2022-09-29 17:00 | 6.5233
2022-09-29 18:00 | 4.5461
2022-09-29 19:00 | 4.7732
2022-09-29 20:00 | 4.7988
2022-09-29 21:00 | 4.7623
2022-09-29 22:00 | 4.8662
2022-09-29 23:00 | 4.8983
2022-09-30 | 4.9206
2022-09-30 01:00 | 4.9293
2022-09-30 02:00 | 4.909
2022-09-30 03:00 | 4.9331
2022-09-30 04:00 | 4.9505
2022-09-30 05:00 | 6.2328
2022-09-30 06:00 | 12.0351
2022-09-30 07:00 | 12.0351
2022-09-30 08:00 | 12.0351
2022-09-30 09:00 | 12.0351
2022-09-30 10:00 | 12.0351
2022-09-30 11:00 | 12.0351
2022-09-30 12:00 | 12.0351
2022-09-30 13:00 | 12.0351
2022-09-30 14:00 | 12.0351
2022-09-30 15:00 | 12.0351
2022-09-30 16:00 | 12.0351
2022-09-30 17:00 | 7.7993
2022-09-30 18:00 | 4.7495
2022-09-30 19:00 | 4.702
2022-09-30 20:00 | 4.7199
2022-09-30 21:00 | 4.8174
2022-09-30 22:00 | 4.7928
2022-09-30 23:00 | 4.8017
2022-10-01 | 4.7781
2022-10-01 01:00 | 4.8535
2022-10-01 02:00 | 4.7899
2022-10-01 03:00 | 4.8272
2022-10-01 04:00 | 4.8223
2022-10-01 05:00 | 4.8242
2022-10-01 06:00 | 4.874
2022-10-01 07:00 | 4.8535
2022-10-01 08:00 | 4.8134
2022-10-01 09:00 | 4.837
2022-10-01 10:00 | 4.785
2022-10-01 11:00 | 4.7357
2022-10-01 12:00 | 4.7406
2022-10-01 13:00 | 4.6712
2022-10-01 14:00 | 4.6792
2022-10-01 15:00 | 4.6403
2022-10-01 16:00 | 4.6453
2022-10-01 17:00 | 4.6344
2022-10-01 18:00 | 4.6253
2022-10-01 19:00 | 4.5963
2022-10-01 20:00 | 4.5863
2022-10-01 21:00 | 4.5923
2022-10-01 22:00 | 4.6533
2022-10-01 23:00 | 4.6393
2022-10-02 | 4.7367
2022-10-02 01:00 | 4.7199
2022-10-02 02:00 | 4.7466
2022-10-02 03:00 | 4.7416
2022-10-02 04:00 | 4.7396
2022-10-02 05:00 | 4.782
2022-10-02 06:00 | 4.8154
2022-10-02 07:00 | 4.8398
2022-10-02 08:00 | 4.8105
2022-10-02 09:00 | 4.8164
2022-10-02 10:00 | 4.7968
2022-10-02 11:00 | 4.6961
2022-10-02 12:00 | 4.6842
2022-10-02 13:00 | 4.699
2022-10-02 14:00 | 4.6971
2022-10-02 15:00 | 4.7149
2022-10-02 16:00 | 4.6802
2022-10-02 17:00 | 4.787
2022-10-02 18:00 | 4.7466
2022-10-02 19:00 | 4.8291
2022-10-02 20:00 | 4.8428
2022-10-02 21:00 | 4.8272
2022-10-02 22:00 | 4.8145
2022-10-02 23:00 | 4.8291
2022-10-03 | 4.8389
2022-10-03 01:00 | 4.8203
2022-10-03 02:00 | 4.9099
2022-10-03 03:00 | 4.8555
2022-10-03 04:00 | 4.8818
2022-10-03 05:00 | 7.2663
2022-10-03 06:00 | 12.0351
2022-10-03 07:00 | 11.2972
2022-10-03 08:00 | 10.2007
2022-10-03 09:00 | 10.6145
2022-10-03 10:00 | 11.3765
2022-10-03 11:00 | 10.1476
2022-10-03 12:00 | 10.9528
2022-10-03 13:00 | 11.4086
2022-10-03 14:00 | 11.4302
2022-10-03 15:00 | 11.2955
2022-10-03 16:00 | 7.2418
2022-10-03 17:00 | 0.80142
2022-10-03 18:00 | 0.90663
2022-10-03 19:00 | 0.90175
2022-10-03 20:00 | 0.8703
2022-10-03 21:00 | 0.89585
2022-10-03 22:00 | 0.90567
2022-10-03 23:00 | 0.89687
2022-10-04 | 0.92127
2022-10-04 01:00 | 0.90567
2022-10-04 02:00 | 0.91833
2022-10-04 03:00 | 0.92618
2022-10-04 04:00 | 0.93681
2022-10-04 05:00 | 1.5563
2022-10-04 06:00 | 5.6667
2022-10-04 07:00 | 5.6642
2022-10-04 08:00 | 5.6438
2022-10-04 09:00 | 5.5675
2022-10-04 10:00 | 5.5415
2022-10-04 11:00 | 5.531
2022-10-04 12:00 | 5.4226
2022-10-04 13:00 | 5.4092
2022-10-04 14:00 | 5.4234
2022-10-04 15:00 | 5.4136
2022-10-04 16:00 | 5.4011
2022-10-04 17:00 | 5.3984
2022-10-04 18:00 | 4.5873
2022-10-04 19:00 | 4.6194
2022-10-04 20:00 | 4.5903
2022-10-04 21:00 | 4.5732
2022-10-04 22:00 | 4.5773
2022-10-04 23:00 | 4.6183
2022-10-05 | 4.5592
2022-10-05 01:00 | 4.5742
2022-10-05 02:00 | 4.6053
2022-10-05 03:00 | 4.5692
2022-10-05 04:00 | 4.6283
2022-10-05 05:00 | 7.7817
2022-10-05 06:00 | 12.0351
2022-10-05 07:00 | 12.0351
2022-10-05 08:00 | 12.0351
2022-10-05 09:00 | 12.0351
2022-10-05 10:00 | 12.0351
2022-10-05 11:00 | 12.0351
2022-10-05 12:00 | 12.0351
2022-10-05 13:00 | 12.0351
2022-10-05 14:00 | 12.0351
2022-10-05 15:00 | 12.0351
2022-10-05 16:00 | 12.0351
2022-10-05 17:00 | 12.0351
2022-10-05 18:00 | 12.0351
2022-10-05 19:00 | 12.0351
2022-10-05 20:00 | 12.0351
2022-10-05 21:00 | 12.0351
2022-10-05 22:00 | 12.0351
2022-10-05 23:00 | 12.0351
2022-10-06 | 12.0351
2022-10-06 01:00 | 12.0351
2022-10-06 02:00 | 12.0351
2022-10-06 03:00 | 12.0351
2022-10-06 04:00 | 12.0351
2022-10-06 05:00 | 12.0351
2022-10-06 06:00 | 12.0351
2022-10-06 07:00 | 12.0351
2022-10-06 08:00 | 12.0351
2022-10-06 09:00 | 12.0351
2022-10-06 10:00 | 12.0351
2022-10-06 11:00 | 12.0351
2022-10-06 12:00 | 12.0351
2022-10-06 13:00 | 12.0351
2022-10-06 14:00 | 12.0351
2022-10-06 15:00 | 12.0351
2022-10-06 16:00 | 12.0351
2022-10-06 17:00 | 12.0351
2022-10-06 18:00 | 12.0351
2022-10-06 19:00 | 12.0351
2022-10-06 20:00 | 12.0351
2022-10-06 21:00 | 12.0351
2022-10-06 22:00 | 12.0351
2022-10-06 23:00 | 12.0351
2022-10-07 | 12.0351
2022-10-07 01:00 | 12.0351
2022-10-07 02:00 | 12.0351
2022-10-07 03:00 | 12.0351
2022-10-07 04:00 | 12.0351
2022-10-07 05:00 | 12.0351
2022-10-07 06:00 | 12.0351
2022-10-07 07:00 | 12.0351
2022-10-07 08:00 | 12.0351
2022-10-07 09:00 | 12.0351
2022-10-07 10:00 | 12.0351
2022-10-07 11:00 | 12.0351
2022-10-07 12:00 | 12.0351
2022-10-07 13:00 | 12.0351
2022-10-07 14:00 | 12.0351
2022-10-07 15:00 | 12.0351
2022-10-07 16:00 | 12.0351
2022-10-07 17:00 | 12.0351
2022-10-07 18:00 | 12.0351
2022-10-07 19:00 | 4.5773
2022-10-07 20:00 | 4.6213
2022-10-07 21:00 | 4.6513
2022-10-07 22:00 | 4.6543
2022-10-07 23:00 | 4.6433
2022-10-08 | 4.6732
2022-10-08 01:00 | 4.6742
2022-10-08 02:00 | 4.7387
2022-10-08 03:00 | 4.7485
2022-10-08 04:00 | 4.7535
2022-10-08 05:00 | 4.8154
2022-10-08 06:00 | 4.8203
2022-10-08 07:00 | 4.8134
2022-10-08 08:00 | 4.8428
2022-10-08 09:00 | 4.7938
2022-10-08 10:00 | 4.7377
2022-10-08 11:00 | 4.6003
2022-10-08 12:00 | 4.6034
2022-10-08 13:00 | 4.5953
2022-10-08 14:00 | 4.5903
2022-10-08 15:00 | 4.5923
2022-10-08 16:00 | 4.5943
2022-10-08 17:00 | 4.5672
2022-10-08 18:00 | 4.5893
2022-10-08 19:00 | 4.6243
2022-10-08 20:00 | 4.6173
2022-10-08 21:00 | 4.6213
2022-10-08 22:00 | 4.5763
2022-10-08 23:00 | 4.6143
2022-10-09 | 4.6363
2022-10-09 01:00 | 4.6593
2022-10-09 02:00 | 4.6742
2022-10-09 03:00 | 4.6842
2022-10-09 04:00 | 4.6722
2022-10-09 05:00 | 4.6971
2022-10-09 06:00 | 4.706
2022-10-09 07:00 | 4.708
2022-10-09 08:00 | 4.7278
2022-10-09 09:00 | 4.7248
2022-10-09 10:00 | 4.7099
2022-10-09 11:00 | 4.704
2022-10-09 12:00 | 4.6891
2022-10-09 13:00 | 4.6802
2022-10-09 14:00 | 4.6921
2022-10-09 15:00 | 4.6623
2022-10-09 16:00 | 4.6443
2022-10-09 17:00 | 4.6383
2022-10-09 18:00 | 4.6433
2022-10-09 19:00 | 4.6453
2022-10-09 20:00 | 4.6413
2022-10-09 21:00 | 4.6053
2022-10-09 22:00 | 4.6243
2022-10-09 23:00 | 4.6453
2022-10-10 | 4.6264
2022-10-10 01:00 | 4.6812
2022-10-10 02:00 | 4.6871
2022-10-10 03:00 | 4.6822
2022-10-10 04:00 | 4.6901
2022-10-10 05:00 | 4.711
2022-10-10 06:00 | 4.7337
2022-10-10 07:00 | 4.5551
2022-10-10 08:00 | 4.6742
2022-10-10 09:00 | 4.6732
2022-10-10 10:00 | 4.5923
2022-10-10 11:00 | 4.5521
2022-10-10 12:00 | 4.5078
2022-10-10 13:00 | 4.5179
2022-10-10 14:00 | 4.4663
2022-10-10 15:00 | 4.4764
2022-10-10 16:00 | 4.4764
2022-10-10 17:00 | 4.4855
2022-10-10 18:00 | 4.4552
2022-10-10 19:00 | 4.6662
2022-10-10 20:00 | 4.6413
2022-10-10 21:00 | 4.6642
2022-10-10 22:00 | 4.6732
2022-10-10 23:00 | 4.6852
2022-10-11 | 4.7139
2022-10-11 01:00 | 4.7229
2022-10-11 02:00 | 4.7278
2022-10-11 03:00 | 4.7278
2022-10-11 04:00 | 4.7377
2022-10-11 05:00 | 4.7633
2022-10-11 06:00 | 4.835
2022-10-11 07:00 | 4.6034
2022-10-11 08:00 | 4.8154
2022-10-11 09:00 | 4.7248
2022-10-11 10:00 | 4.6822
2022-10-11 11:00 | 4.6264
2022-10-11 12:00 | 4.6513
2022-10-11 13:00 | 4.6304
2022-10-11 14:00 | 4.6483
2022-10-11 15:00 | 4.6293
2022-10-11 16:00 | 4.6093
2022-10-11 17:00 | 4.6283
2022-10-11 18:00 | 4.6234
2022-10-11 19:00 | 4.6533
2022-10-11 20:00 | 4.6063
2022-10-11 21:00 | 4.6013
2022-10-11 22:00 | 4.6123
2022-10-11 23:00 | 4.6114
2022-10-12 | 4.6213
2022-10-12 01:00 | 4.6602
2022-10-12 02:00 | 4.6563
2022-10-12 03:00 | 4.6831
2022-10-12 04:00 | 4.7288
2022-10-12 05:00 | 4.7545
2022-10-12 06:00 | 4.7574
2022-10-12 07:00 | 4.7554
2022-10-12 08:00 | 7.955
2022-10-12 09:00 | 8.4587
2022-10-12 10:00 | 8.416
2022-10-12 11:00 | 8.413
2022-10-12 12:00 | 8.3901
2022-10-12 13:00 | 8.3947
2022-10-12 14:00 | 8.3503
2022-10-12 15:00 | 8.3293
2022-10-12 16:00 | 8.1687
2022-10-12 17:00 | 4.5783
2022-10-12 18:00 | 4.5783
2022-10-12 19:00 | 4.5732
2022-10-12 20:00 | 4.5843
2022-10-12 21:00 | 4.5953
2022-10-12 22:00 | 4.5903
2022-10-12 23:00 | 4.5742
2022-10-13 | 4.5913
2022-10-13 01:00 | 4.6103
2022-10-13 02:00 | 4.6173
2022-10-13 03:00 | 4.6123
2022-10-13 04:00 | 4.6083
2022-10-13 05:00 | 12.0351
2022-10-13 06:00 | 12.0351
2022-10-13 07:00 | 12.0351
2022-10-13 08:00 | 12.0351
2022-10-13 09:00 | 12.0351
2022-10-13 10:00 | 12.0351
2022-10-13 11:00 | 12.0351
2022-10-13 12:00 | 12.0351
2022-10-13 13:00 | 12.0351
2022-10-13 14:00 | 12.0351
2022-10-13 15:00 | 12.0351
2022-10-13 16:00 | 12.0351
2022-10-13 17:00 | 12.0351
2022-10-13 18:00 | 12.0351
2022-10-13 19:00 | 12.0351
2022-10-13 20:00 | 12.0351
2022-10-13 21:00 | 12.0351
2022-10-13 22:00 | 12.0351
2022-10-13 23:00 | 12.0351
2022-10-14 | 12.0351
2022-10-14 01:00 | 12.0351
2022-10-14 02:00 | 12.0351
2022-10-14 03:00 | 12.0351
2022-10-14 04:00 | 12.0351
2022-10-14 05:00 | 12.0351
2022-10-14 06:00 | 12.0351
2022-10-14 07:00 | 12.0351
2022-10-14 08:00 | 12.0351
2022-10-14 09:00 | 12.0351
2022-10-14 10:00 | 12.0351
2022-10-14 11:00 | 12.0351
2022-10-14 12:00 | 12.0351
2022-10-14 13:00 | 9.4922
2022-10-14 14:00 | 4.6443
2022-10-14 15:00 | 4.6353
2022-10-14 16:00 | 4.6133
2022-10-14 17:00 | 4.6593
2022-10-14 18:00 | 4.6163
2022-10-14 19:00 | 4.537
2022-10-14 20:00 | 4.5601
2022-10-14 21:00 | 4.6093
2022-10-14 22:00 | 4.6613
2022-10-14 23:00 | 4.6732
2022-10-15 | 4.6213
2022-10-15 01:00 | 4.6653
2022-10-15 02:00 | 4.708
2022-10-15 03:00 | 4.6971
2022-10-15 04:00 | 4.7218
2022-10-15 05:00 | 4.7623
2022-10-15 06:00 | 4.784
2022-10-15 07:00 | 4.7505
2022-10-15 08:00 | 4.7139
2022-10-15 09:00 | 4.7129
2022-10-15 10:00 | 4.709
2022-10-15 11:00 | 4.701
2022-10-15 12:00 | 4.6842
2022-10-15 13:00 | 4.6563
2022-10-15 14:00 | 4.6393
2022-10-15 15:00 | 4.6702
2022-10-15 16:00 | 4.6373
2022-10-15 17:00 | 4.6383
2022-10-15 18:00 | 4.6373
2022-10-15 19:00 | 4.6224
2022-10-15 20:00 | 4.6103
2022-10-15 21:00 | 4.6123
2022-10-15 22:00 | 4.6333
2022-10-15 23:00 | 4.6383
2022-10-16 | 4.6253
2022-10-16 01:00 | 4.6712
2022-10-16 02:00 | 4.6662
2022-10-16 03:00 | 4.706
2022-10-16 04:00 | 4.695
2022-10-16 05:00 | 4.7169
2022-10-16 06:00 | 4.706
2022-10-16 07:00 | 4.7308
2022-10-16 08:00 | 4.6961
2022-10-16 09:00 | 4.7248
2022-10-16 10:00 | 4.7189
2022-10-16 11:00 | 4.6363
2022-10-16 12:00 | 4.6133
2022-10-16 13:00 | 4.5943
2022-10-16 14:00 | 4.5803
2022-10-16 15:00 | 4.5692
2022-10-16 16:00 | 4.5883
2022-10-16 17:00 | 4.6043
2022-10-16 18:00 | 4.5933
2022-10-16 19:00 | 4.5923
2022-10-16 20:00 | 4.6283
2022-10-16 21:00 | 4.6403
2022-10-16 22:00 | 4.6003
2022-10-16 23:00 | 4.6802
2022-10-17 | 4.6891
2022-10-17 01:00 | 4.6772
2022-10-17 02:00 | 4.705
2022-10-17 03:00 | 4.6911
2022-10-17 04:00 | 4.707
2022-10-17 05:00 | 4.7297
2022-10-17 06:00 | 4.7179
2022-10-17 07:00 | 11.8372
2022-10-17 08:00 | 12.0351
2022-10-17 09:00 | 12.0351
2022-10-17 10:00 | 12.0351
2022-10-17 11:00 | 12.0351
2022-10-17 12:00 | 12.0351
2022-10-17 13:00 | 12.0351
2022-10-17 14:00 | 12.0351
2022-10-17 15:00 | 12.0351
2022-10-17 16:00 | 12.0351
2022-10-17 17:00 | 6.7871
2022-10-17 18:00 | 5.0024
2022-10-17 19:00 | 5.0109
2022-10-17 20:00 | 5.0766
2022-10-17 21:00 | 5.0728
2022-10-17 22:00 | 5.0434
2022-10-17 23:00 | 5.0842
2022-10-18 | 5.1266
2022-10-18 01:00 | 5.1613
2022-10-18 02:00 | 5.1818
2022-10-18 03:00 | 5.218
2022-10-18 04:00 | 5.2171
2022-10-18 05:00 | 7.3144
2022-10-18 06:00 | 11.1856
2022-10-18 07:00 | 11.1285
2022-10-18 08:00 | 11.1402
2022-10-18 09:00 | 11.0396
2022-10-18 10:00 | 10.8727
2022-10-18 11:00 | 10.8711
2022-10-18 12:00 | 10.8634
2022-10-18 13:00 | 10.9101
2022-10-18 14:00 | 10.8126
2022-10-18 15:00 | 10.7975
2022-10-18 16:00 | 10.8603
2022-10-18 17:00 | 10.9054
2022-10-18 18:00 | 10.7778
2022-10-18 19:00 | 8.7502
2022-10-18 20:00 | 4.5993
2022-10-18 21:00 | 4.6423
2022-10-18 22:00 | 4.6304
2022-10-18 23:00 | 4.6423
2022-10-19 | 4.7327
2022-10-19 01:00 | 4.7337
2022-10-19 02:00 | 4.7643
2022-10-19 03:00 | 4.7702
2022-10-19 04:00 | 4.7505
2022-10-19 05:00 | 4.7977
2022-10-19 06:00 | 4.8448
2022-10-19 07:00 | 4.8164
2022-10-19 08:00 | 4.788
2022-10-19 09:00 | 4.7229
2022-10-19 10:00 | 4.695
2022-10-19 11:00 | 4.6752
2022-10-19 12:00 | 4.6413
2022-10-19 13:00 | 4.6313
2022-10-19 14:00 | 4.5893
2022-10-19 15:00 | 4.5702
2022-10-19 16:00 | 4.5832
2022-10-19 17:00 | 4.6043
2022-10-19 18:00 | 4.5792
2022-10-19 19:00 | 4.6293
2022-10-19 20:00 | 4.3268
2022-10-19 21:00 | 2.6992
2022-10-19 22:00 | 2.7022
2022-10-19 23:00 | 2.6873
2022-10-20 | 2.7142
2022-10-20 01:00 | 2.7461
2022-10-20 02:00 | 2.7531
2022-10-20 03:00 | 2.7591
2022-10-20 04:00 | 2.7651
2022-10-20 05:00 | 2.8123
2022-10-20 06:00 | 4.786
2022-10-20 07:00 | 4.7327
2022-10-20 08:00 | 4.782
2022-10-20 09:00 | 4.705
2022-10-20 10:00 | 4.6692
2022-10-20 11:00 | 4.6383
2022-10-20 12:00 | 4.6463
2022-10-20 13:00 | 4.6593
2022-10-20 14:00 | 4.6123
2022-10-20 15:00 | 4.6353
2022-10-20 16:00 | 4.6213
2022-10-20 17:00 | 4.6473
2022-10-20 18:00 | 4.6143
2022-10-20 19:00 | 4.5692
2022-10-20 20:00 | 4.5832
2022-10-20 21:00 | 4.6053
2022-10-20 22:00 | 4.6043
2022-10-20 23:00 | 4.6901
2022-10-21 | 4.6463
2022-10-21 01:00 | 4.6353
2022-10-21 02:00 | 4.6483
2022-10-21 03:00 | 4.6752
2022-10-21 04:00 | 4.6831
2022-10-21 05:00 | 4.7584
2022-10-21 06:00 | 4.7762
2022-10-21 07:00 | 4.7673
2022-10-21 08:00 | 4.7337
2022-10-21 09:00 | 4.698
2022-10-21 10:00 | 4.6861
2022-10-21 11:00 | 4.6672
2022-10-21 12:00 | 4.6642
2022-10-21 13:00 | 4.6602
2022-10-21 14:00 | 4.6213
2022-10-21 15:00 | 4.6323
2022-10-21 16:00 | 4.6363
2022-10-21 17:00 | 4.6333
2022-10-21 18:00 | 4.6213
2022-10-21 19:00 | 4.6083
2022-10-21 20:00 | 4.6003
2022-10-21 21:00 | 4.6513
2022-10-21 22:00 | 4.6283
2022-10-21 23:00 | 4.6313
2022-10-22 | 4.6583
2022-10-22 01:00 | 4.7119
2022-10-22 02:00 | 4.7387
2022-10-22 03:00 | 4.6871
2022-10-22 04:00 | 4.7099
2022-10-22 05:00 | 4.709
2022-10-22 06:00 | 4.7673
2022-10-22 07:00 | 4.7495
2022-10-22 08:00 | 4.7938
2022-10-22 09:00 | 4.7653
2022-10-22 10:00 | 4.7702
2022-10-22 11:00 | 4.7199
2022-10-22 12:00 | 4.6613
2022-10-22 13:00 | 4.6642
2022-10-22 14:00 | 4.6852
2022-10-22 15:00 | 4.695
2022-10-22 16:00 | 4.6971
2022-10-22 17:00 | 4.6812
2022-10-22 18:00 | 4.6941
2022-10-22 19:00 | 4.6861
2022-10-22 20:00 | 4.6921
2022-10-22 21:00 | 4.6891
2022-10-22 22:00 | 4.6772
2022-10-22 23:00 | 4.6802
2022-10-23 | 4.6782
2022-10-23 01:00 | 4.6692
2022-10-23 02:00 | 4.7367
2022-10-23 03:00 | 4.7327
2022-10-23 04:00 | 4.7377
2022-10-23 05:00 | 4.7643
2022-10-23 06:00 | 4.7466
2022-10-23 07:00 | 4.7889
2022-10-23 08:00 | 4.8359
2022-10-23 09:00 | 4.8164
2022-10-23 10:00 | 4.7594
2022-10-23 11:00 | 4.7594
2022-10-23 12:00 | 4.708
2022-10-23 13:00 | 4.7288
2022-10-23 14:00 | 4.7327
2022-10-23 15:00 | 4.711
2022-10-23 16:00 | 4.7278
2022-10-23 17:00 | 4.7771
2022-10-23 18:00 | 4.7278
2022-10-23 19:00 | 4.7327
2022-10-23 20:00 | 4.7485
2022-10-23 21:00 | 4.7169
2022-10-23 22:00 | 4.707
2022-10-23 23:00 | 4.7317
2022-10-24 | 4.6861
2022-10-24 01:00 | 4.7308
2022-10-24 02:00 | 4.7406
2022-10-24 03:00 | 4.7446
2022-10-24 04:00 | 4.7308
2022-10-24 05:00 | 4.7751
2022-10-24 06:00 | 4.7693
2022-10-24 07:00 | 4.7702
2022-10-24 08:00 | 7.6256
2022-10-24 09:00 | 11.0657
2022-10-24 10:00 | 10.7899
2022-10-24 11:00 | 10.8233
2022-10-24 12:00 | 10.9353
2022-10-24 13:00 | 9.6325
2022-10-24 14:00 | 10.9464
2022-10-24 15:00 | 10.8233
2022-10-24 16:00 | 7.6986
2022-10-24 17:00 | 4.705
2022-10-24 18:00 | 4.6323
2022-10-24 19:00 | 4.6383
2022-10-24 20:00 | 4.6143
2022-10-24 21:00 | 4.6353
2022-10-24 22:00 | 4.6563
2022-10-24 23:00 | 4.6941
2022-10-25 | 4.6463
2022-10-25 01:00 | 4.6852
2022-10-25 02:00 | 4.6901
2022-10-25 03:00 | 4.6692
2022-10-25 04:00 | 4.6772
2022-10-25 05:00 | 4.7159
2022-10-25 06:00 | 12.0351
2022-10-25 07:00 | 12.0351
2022-10-25 08:00 | 12.0351
2022-10-25 09:00 | 12.0351
2022-10-25 10:00 | 12.0351
2022-10-25 11:00 | 12.0351
2022-10-25 12:00 | 12.0351
2022-10-25 13:00 | 12.0351
2022-10-25 14:00 | 12.0351
2022-10-25 15:00 | 12.0351
2022-10-25 16:00 | 12.0351
2022-10-25 17:00 | 12.0351
2022-10-25 18:00 | 12.0351
2022-10-25 19:00 | 12.0351
2022-10-25 20:00 | 12.0351
2022-10-25 21:00 | 12.0351
2022-10-25 22:00 | 12.0351
2022-10-25 23:00 | 12.0351
2022-10-26 | 12.0351
2022-10-26 01:00 | 12.0351
2022-10-26 02:00 | 12.0351
2022-10-26 03:00 | 12.0351
2022-10-26 04:00 | 12.0351
2022-10-26 05:00 | 12.0351
2022-10-26 06:00 | 12.0351
2022-10-26 07:00 | 12.0351
2022-10-26 08:00 | 12.0351
2022-10-26 09:00 | 12.0351
2022-10-26 10:00 | 12.0351
2022-10-26 11:00 | 12.0351
2022-10-26 12:00 | 12.0351
2022-10-26 13:00 | 12.0351
2022-10-26 14:00 | 12.0351
2022-10-26 15:00 | 12.0351
2022-10-26 16:00 | 12.0351
2022-10-26 17:00 | 12.0351
2022-10-26 18:00 | 12.0351
2022-10-26 19:00 | 12.0351
2022-10-26 20:00 | 8.2436
2022-10-26 21:00 | 4.6861
2022-10-26 22:00 | 4.6961
2022-10-26 23:00 | 4.7308
2022-10-27 | 4.7614
2022-10-27 01:00 | 4.7732
2022-10-27 02:00 | 4.7604
2022-10-27 03:00 | 4.7919
2022-10-27 04:00 | 4.8379
2022-10-27 05:00 | 8.7111
2022-10-27 06:00 | 12.0351
2022-10-27 07:00 | 12.0351
2022-10-27 08:00 | 12.0351
2022-10-27 09:00 | 12.0351
2022-10-27 10:00 | 12.0351
2022-10-27 11:00 | 12.0351
2022-10-27 12:00 | 12.0351
2022-10-27 13:00 | 12.0351
2022-10-27 14:00 | 12.0351
2022-10-27 15:00 | 12.0351
2022-10-27 16:00 | 12.0351
2022-10-27 17:00 | 12.0351
2022-10-27 18:00 | 12.0351
2022-10-27 19:00 | 12.0351
2022-10-27 20:00 | 12.0351
2022-10-27 21:00 | 12.0351
2022-10-27 22:00 | 12.0351
2022-10-27 23:00 | 12.0351
2022-10-28 | 12.0351
2022-10-28 01:00 | 12.0351
2022-10-28 02:00 | 12.0351
2022-10-28 03:00 | 12.0351
2022-10-28 04:00 | 12.0351
2022-10-28 05:00 | 12.0351
2022-10-28 06:00 | 6.2386
2022-10-28 07:00 | 5.9619
2022-10-28 08:00 | 5.9821
2022-10-28 09:00 | 5.9611
2022-10-28 10:00 | 5.925
2022-10-28 11:00 | 5.8845
2022-10-28 12:00 | 6.064
2022-10-28 13:00 | 6.0443
2022-10-28 14:00 | 6.0061
2022-10-28 15:00 | 5.9984
2022-10-28 16:00 | 6.0084
2022-10-28 17:00 | 5.9108
2022-10-28 18:00 | 0.92618
2022-10-28 19:00 | 0.93293
2022-10-28 20:00 | 0.9242
2022-10-28 21:00 | 0.92127
2022-10-28 22:00 | 0.91053
2022-10-28 23:00 | 0.90861
2022-10-29 | 0.91252
2022-10-29 01:00 | 0.95039
2022-10-29 02:00 | 0.9349
2022-10-29 03:00 | 0.9242
2022-10-29 04:00 | 0.92516
2022-10-29 05:00 | 0.94652
2022-10-29 06:00 | 0.96776
2022-10-29 07:00 | 0.97255
2022-10-29 08:00 | 0.96101
2022-10-29 09:00 | 0.97161
2022-10-29 10:00 | 0.93586
2022-10-29 11:00 | 0.94068
2022-10-29 12:00 | 0.9735
2022-10-29 13:00 | 0.96101
2022-10-29 14:00 | 0.95716
2022-10-29 15:00 | 0.94842
2022-10-29 16:00 | 0.94944
2022-10-29 17:00 | 0.95621
2022-10-29 18:00 | 0.93681
2022-10-29 19:00 | 0.94455
2022-10-29 20:00 | 0.93198
2022-10-29 21:00 | 0.9436
2022-10-29 22:00 | 0.92325
2022-10-29 23:00 | 0.93586
2022-10-30 | 0.9533
2022-10-30 01:00 | 0.9552
2022-10-30 02:00 | 0.95134
2022-10-30 03:00 | 0.95425
2022-10-30 04:00 | 0.96101
2022-10-30 05:00 | 0.95716
2022-10-30 06:00 | 0.96871
2022-10-30 07:00 | 0.97929
2022-10-30 08:00 | 0.96965
2022-10-30 09:00 | 0.97639
2022-10-30 10:00 | 0.96776
2022-10-30 11:00 | 0.94068
2022-10-30 12:00 | 0.95134
2022-10-30 13:00 | 0.94747
2022-10-30 14:00 | 0.9349
2022-10-30 15:00 | 0.93878
2022-10-30 16:00 | 0.93973
2022-10-30 17:00 | 0.9417
2022-10-30 18:00 | 0.93586
2022-10-30 19:00 | 0.95134
2022-10-30 20:00 | 0.94747
2022-10-30 21:00 | 0.94265
2022-10-30 22:00 | 0.94557
2022-10-30 23:00 | 0.93586
2022-10-31 | 0.9417
2022-10-31 01:00 | 0.95039
2022-10-31 02:00 | 0.94455
2022-10-31 03:00 | 0.95039
2022-10-31 04:00 | 0.9552
2022-10-31 05:00 | 2.8687
2022-10-31 06:00 | 8.5795
2022-10-31 07:00 | 8.2738
2022-10-31 08:00 | 8.2655
2022-10-31 09:00 | 8.4356
2022-10-31 10:00 | 8.4219
2022-10-31 11:00 | 8.4151
2022-10-31 12:00 | 8.4215
2022-10-31 13:00 | 8.416
2022-10-31 14:00 | 8.416
2022-10-31 15:00 | 8.3942
2022-10-31 16:00 | 8.3803
2022-10-31 17:00 | 8.0343
2022-10-31 18:00 | 3.0475
2022-10-31 19:00 | 2.9945
2022-10-31 20:00 | 2.9894
2022-10-31 21:00 | 3.022
2022-10-31 22:00 | 3.0751
2022-10-31 23:00 | 3.023
2022-11-01 | 3.0864
2022-11-01 01:00 | 3.072
2022-11-01 02:00 | 3.0506
2022-11-01 03:00 | 3.0475
2022-11-01 04:00 | 3.0854
2022-11-01 05:00 | 3.1018
2022-11-01 06:00 | 6.2257
2022-11-01 07:00 | 12.0351
2022-11-01 08:00 | 12.0351
2022-11-01 09:00 | 12.0351
2022-11-01 10:00 | 12.0351
2022-11-01 11:00 | 12.0351
2022-11-01 12:00 | 12.0351
2022-11-01 13:00 | 12.0351
2022-11-01 14:00 | 12.0351
2022-11-01 15:00 | 12.0351
2022-11-01 16:00 | 12.0351
2022-11-01 17:00 | 12.0351
2022-11-01 18:00 | 4.6103
2022-11-01 19:00 | 4.5792
2022-11-01 20:00 | 4.6143
2022-11-01 21:00 | 4.6363
2022-11-01 22:00 | 4.6632
2022-11-01 23:00 | 4.6503
2022-11-02 | 4.6881
2022-11-02 01:00 | 4.7732
2022-11-02 02:00 | 4.7771
2022-11-02 03:00 | 4.7948
2022-11-02 04:00 | 4.7643
2022-11-02 05:00 | 7.5304
2022-11-02 06:00 | 12.0351
2022-11-02 07:00 | 12.0351
2022-11-02 08:00 | 12.0351
2022-11-02 09:00 | 12.0351
2022-11-02 10:00 | 12.0351
2022-11-02 11:00 | 12.0351
2022-11-02 12:00 | 12.0351
2022-11-02 13:00 | 12.0351
2022-11-02 14:00 | 12.0351
2022-11-02 15:00 | 12.0351
2022-11-02 16:00 | 12.0351
2022-11-02 17:00 | 12.0351
2022-11-02 18:00 | 8.8926
2022-11-02 19:00 | 4.6453
2022-11-02 20:00 | 4.6901
2022-11-02 21:00 | 4.6901
2022-11-02 22:00 | 4.699
2022-11-02 23:00 | 4.7119
2022-11-03 | 4.7406
2022-11-03 01:00 | 4.7771
2022-11-03 02:00 | 4.784
2022-11-03 03:00 | 4.7693
2022-11-03 04:00 | 4.8095
2022-11-03 05:00 | 4.8389
2022-11-03 06:00 | 4.8604
2022-11-03 07:00 | 4.8242
2022-11-03 08:00 | 4.8115
2022-11-03 09:00 | 4.7751
2022-11-03 10:00 | 4.7129
2022-11-03 11:00 | 4.7238
2022-11-03 12:00 | 4.6692
2022-11-03 13:00 | 4.6712
2022-11-03 14:00 | 4.6782
2022-11-03 15:00 | 4.6183
2022-11-03 16:00 | 4.6093
2022-11-03 17:00 | 4.6881
2022-11-03 18:00 | 4.6842
2022-11-03 19:00 | 4.6712
2022-11-03 20:00 | 4.7179
2022-11-03 21:00 | 4.7456
2022-11-03 22:00 | 4.7337
2022-11-03 23:00 | 4.7149
2022-11-04 | 4.7426
2022-11-04 01:00 | 4.7938
2022-11-04 02:00 | 4.8066
2022-11-04 03:00 | 4.782
2022-11-04 04:00 | 4.8134
2022-11-04 05:00 | 12.0351
2022-11-04 06:00 | 12.0351
2022-11-04 07:00 | 12.0351
2022-11-04 08:00 | 12.0351
2022-11-04 09:00 | 12.0351
2022-11-04 10:00 | 12.0351
2022-11-04 11:00 | 12.0351
2022-11-04 12:00 | 12.0351
2022-11-04 13:00 | 12.0351
2022-11-04 14:00 | 12.0351
2022-11-04 15:00 | 12.0351
2022-11-04 16:00 | 12.0351
2022-11-04 17:00 | 12.0351
2022-11-04 18:00 | 12.0351
2022-11-04 19:00 | 9.8718
2022-11-04 20:00 | 4.787
2022-11-04 21:00 | 4.7515
2022-11-04 22:00 | 4.698
2022-11-04 23:00 | 4.695
2022-11-05 | 4.7159
2022-11-05 01:00 | 4.6861
2022-11-05 02:00 | 4.7317
2022-11-05 03:00 | 4.7347
2022-11-05 04:00 | 4.7377
2022-11-05 05:00 | 4.7288
2022-11-05 06:00 | 4.7525
2022-11-05 07:00 | 4.7505
2022-11-05 08:00 | 4.7584
2022-11-05 09:00 | 4.7387
2022-11-05 10:00 | 4.7396
2022-11-05 11:00 | 4.7554
2022-11-05 12:00 | 4.6513
2022-11-05 13:00 | 4.6762
2022-11-05 14:00 | 4.6293
2022-11-05 15:00 | 4.6642
2022-11-05 16:00 | 4.6463
2022-11-05 17:00 | 4.6213
2022-11-05 18:00 | 4.7396
2022-11-05 19:00 | 4.7367
2022-11-05 20:00 | 4.7159
2022-11-05 21:00 | 4.7169
2022-11-05 22:00 | 4.6602
2022-11-05 23:00 | 4.6623
2022-11-06 | 4.6463
2022-11-06 01:00 | 4.6662
2022-11-06 02:00 | 4.6822
2022-11-06 03:00 | 4.6802
2022-11-06 04:00 | 4.6911
2022-11-06 05:00 | 4.6852
2022-11-06 06:00 | 4.7001
2022-11-06 07:00 | 4.704
2022-11-06 08:00 | 4.7229
2022-11-06 09:00 | 4.7525
2022-11-06 10:00 | 4.709
2022-11-06 11:00 | 4.7387
2022-11-06 12:00 | 4.7001
2022-11-06 13:00 | 4.706
2022-11-06 14:00 | 4.6333
2022-11-06 15:00 | 4.6224
2022-11-06 16:00 | 4.6642
2022-11-06 17:00 | 4.6812
2022-11-06 18:00 | 4.695
2022-11-06 19:00 | 4.6782
2022-11-06 20:00 | 4.6822
2022-11-06 21:00 | 4.6861
2022-11-06 22:00 | 4.6941
2022-11-06 23:00 | 4.6742
2022-11-07 | 4.6682
2022-11-07 01:00 | 4.6383
2022-11-07 02:00 | 4.6553
2022-11-07 03:00 | 4.6513
2022-11-07 04:00 | 4.7129
2022-11-07 05:00 | 4.6623
2022-11-07 06:00 | 11.5939
2022-11-07 07:00 | 12.0351
2022-11-07 08:00 | 12.0351
2022-11-07 09:00 | 12.0351
2022-11-07 10:00 | 12.0351
2022-11-07 11:00 | 12.0351
2022-11-07 12:00 | 12.0351
2022-11-07 13:00 | 12.0351
2022-11-07 14:00 | 12.0351
2022-11-07 15:00 | 12.0351
2022-11-07 16:00 | 12.0351
2022-11-07 17:00 | 12.0351
2022-11-07 18:00 | 12.0351
2022-11-07 19:00 | 2.5922
2022-11-07 20:00 | 2.608
2022-11-07 21:00 | 2.6089
2022-11-07 22:00 | 2.8385
2022-11-07 23:00 | 2.7902
2022-11-08 | 2.8374
2022-11-08 01:00 | 2.8515
2022-11-08 02:00 | 2.8697
2022-11-08 03:00 | 2.8727
2022-11-08 04:00 | 2.8667
2022-11-08 05:00 | 2.8909
2022-11-08 06:00 | 2.9051
2022-11-08 07:00 | 2.9213
2022-11-08 08:00 | 2.9264
2022-11-08 09:00 | 2.9599
2022-11-08 10:00 | 2.9345
2022-11-08 11:00 | 2.9021
2022-11-08 12:00 | 2.894
2022-11-08 13:00 | 2.8738
2022-11-08 14:00 | 2.8738
2022-11-08 15:00 | 2.8717
2022-11-08 16:00 | 2.8243
2022-11-08 17:00 | 2.8183
2022-11-08 18:00 | 2.8113
2022-11-08 19:00 | 2.8052
2022-11-08 20:00 | 2.7271
2022-11-08 21:00 | 2.7902
2022-11-08 22:00 | 2.8556
2022-11-08 23:00 | 2.8385
2022-11-09 | 2.8344
2022-11-09 01:00 | 2.8234
2022-11-09 02:00 | 2.8576
2022-11-09 03:00 | 2.8808
2022-11-09 04:00 | 2.8475
2022-11-09 05:00 | 2.8748
2022-11-09 06:00 | 2.9122
2022-11-09 07:00 | 2.9477
2022-11-09 08:00 | 2.9254
2022-11-09 09:00 | 2.9466
2022-11-09 10:00 | 2.8798
2022-11-09 11:00 | 2.893
2022-11-09 12:00 | 2.8385
2022-11-09 13:00 | 2.8193
2022-11-09 14:00 | 2.8314
2022-11-09 15:00 | 2.8515
2022-11-09 16:00 | 2.8274
2022-11-09 17:00 | 2.8506
2022-11-09 18:00 | 2.8646
2022-11-09 19:00 | 2.8364
2022-11-09 20:00 | 2.8324
2022-11-09 21:00 | 2.7772
2022-11-09 22:00 | 2.8364
2022-11-09 23:00 | 2.8143
2022-11-10 | 2.8183
2022-11-10 01:00 | 2.8364
2022-11-10 02:00 | 2.8364
2022-11-10 03:00 | 2.8455
2022-11-10 04:00 | 2.8485
2022-11-10 05:00 | 2.8546
2022-11-10 06:00 | 2.8818
2022-11-10 07:00 | 2.9375
2022-11-10 08:00 | 2.8123
2022-11-10 09:00 | 2.8485
2022-11-10 10:00 | 2.8657
2022-11-10 11:00 | 2.8123
2022-11-10 12:00 | 2.7962
2022-11-10 13:00 | 2.7661
2022-11-10 14:00 | 2.7722
2022-11-10 15:00 | 2.7501
2022-11-10 16:00 | 2.7521
2022-11-10 17:00 | 2.7441
2022-11-10 18:00 | 2.8073
2022-11-10 19:00 | 2.7631
2022-11-10 20:00 | 2.6843
2022-11-10 21:00 | 2.6873
2022-11-10 22:00 | 2.6803
2022-11-10 23:00 | 2.6992
2022-11-11 | 2.6843
2022-11-11 01:00 | 2.6743
2022-11-11 02:00 | 2.7321
2022-11-11 03:00 | 2.7361
2022-11-11 04:00 | 2.7182
2022-11-11 05:00 | 2.7411
2022-11-11 06:00 | 2.7351
2022-11-11 07:00 | 2.8002
2022-11-11 08:00 | 2.7731
2022-11-11 09:00 | 2.8033
2022-11-11 10:00 | 2.7641
2022-11-11 11:00 | 2.7621
2022-11-11 12:00 | 2.7271
2022-11-11 13:00 | 2.7371
2022-11-11 14:00 | 2.7211
2022-11-11 15:00 | 2.7122
2022-11-11 16:00 | 2.6962
2022-11-11 17:00 | 2.6793
2022-11-11 18:00 | 2.6892
2022-11-11 19:00 | 2.6445
2022-11-11 20:00 | 2.6257
2022-11-11 21:00 | 2.611
2022-11-11 22:00 | 2.6347
2022-11-11 23:00 | 2.6119
2022-11-12 | 2.6902
2022-11-12 01:00 | 2.6445
2022-11-12 02:00 | 2.5932
2022-11-12 03:00 | 2.6159
2022-11-12 04:00 | 2.5764
2022-11-12 05:00 | 2.6119
2022-11-12 06:00 | 2.6129
2022-11-12 07:00 | 2.6535
2022-11-12 08:00 | 2.6317
2022-11-12 09:00 | 2.6833
2022-11-12 10:00 | 2.6892
2022-11-12 11:00 | 2.6952
2022-11-12 12:00 | 2.7281
2022-11-12 13:00 | 2.6724
2022-11-12 14:00 | 2.7122
2022-11-12 15:00 | 2.6902
2022-11-12 16:00 | 2.6892
2022-11-12 17:00 | 2.6853
2022-11-12 18:00 | 2.7092
2022-11-12 19:00 | 2.6575
2022-11-12 20:00 | 2.7022
2022-11-12 21:00 | 2.6713
2022-11-12 22:00 | 2.6783
2022-11-12 23:00 | 2.6892
2022-11-13 | 2.6287
2022-11-13 01:00 | 2.6783
2022-11-13 02:00 | 2.6704
2022-11-13 03:00 | 2.7012
2022-11-13 04:00 | 2.6902
2022-11-13 05:00 | 2.7171
2022-11-13 06:00 | 2.7381
2022-11-13 07:00 | 2.7411
2022-11-13 08:00 | 2.7471
2022-11-13 09:00 | 2.7481
2022-11-13 10:00 | 2.7651
2022-11-13 11:00 | 2.7691
2022-11-13 12:00 | 2.7381
2022-11-13 13:00 | 2.7631
2022-11-13 14:00 | 2.7751
2022-11-13 15:00 | 2.7561
2022-11-13 16:00 | 2.7762
2022-11-13 17:00 | 2.7591
2022-11-13 18:00 | 2.7821
2022-11-13 19:00 | 2.7451
2022-11-13 20:00 | 2.7651
2022-11-13 21:00 | 2.7541
2022-11-13 22:00 | 2.7471
2022-11-13 23:00 | 2.7741
2022-11-14 | 2.7762
2022-11-14 01:00 | 2.8002
2022-11-14 02:00 | 2.8002
2022-11-14 03:00 | 2.8395
2022-11-14 04:00 | 2.8687
2022-11-14 05:00 | 2.8556
2022-11-14 06:00 | 2.9061
2022-11-14 07:00 | 2.8899
2022-11-14 08:00 | 2.8879
2022-11-14 09:00 | 3.5687
2022-11-14 10:00 | 3.5478
2022-11-14 11:00 | 3.4988
2022-11-14 12:00 | 3.4583
2022-11-14 13:00 | 3.4261
2022-11-14 14:00 | 3.4344
2022-11-14 15:00 | 3.449
2022-11-14 16:00 | 3.4063
2022-11-14 17:00 | 3.424
2022-11-14 18:00 | 3.4885
2022-11-14 19:00 | 3.4635
2022-11-14 20:00 | 1.824
2022-11-14 21:00 | 1.8167
2022-11-14 22:00 | 1.7984
2022-11-14 23:00 | 1.8066
2022-11-15 | 1.8066
2022-11-15 01:00 | 1.8505
2022-11-15 02:00 | 1.824
2022-11-15 03:00 | 1.824
2022-11-15 04:00 | 1.8514
2022-11-15 05:00 | 1.856
2022-11-15 06:00 | 1.8725
2022-11-15 07:00 | 1.8982
2022-11-15 08:00 | 1.8909
2022-11-15 09:00 | 1.8762
2022-11-15 10:00 | 1.8432
2022-11-15 11:00 | 1.8377
2022-11-15 12:00 | 1.8148
2022-11-15 13:00 | 1.8231
2022-11-15 14:00 | 1.8167
2022-11-15 15:00 | 1.8331
2022-11-15 16:00 | 1.8285
2022-11-15 17:00 | 1.8249
2022-11-15 18:00 | 1.8642
2022-11-15 19:00 | 1.8377
2022-11-15 20:00 | 1.8249
2022-11-15 21:00 | 1.8331
2022-11-15 22:00 | 1.7847
2022-11-15 23:00 | 1.7838
2022-11-16 | 1.8194
2022-11-16 01:00 | 1.824
2022-11-16 02:00 | 1.824
2022-11-16 03:00 | 1.8203
2022-11-16 04:00 | 1.813
2022-11-16 05:00 | 1.8158
2022-11-16 06:00 | 1.8313
2022-11-16 07:00 | 1.9758
2022-11-16 08:00 | 6.812
2022-11-16 09:00 | 6.8302
2022-11-16 10:00 | 6.7645
2022-11-16 11:00 | 6.706
2022-11-16 12:00 | 6.6829
2022-11-16 13:00 | 6.6731
2022-11-16 14:00 | 6.6766
2022-11-16 15:00 | 6.6502
2022-11-16 16:00 | 6.6608
2022-11-16 17:00 | 6.6526
2022-11-16 18:00 | 6.7293
2022-11-16 19:00 | 6.7208
2022-11-16 20:00 | 6.7185
2022-11-16 21:00 | 8.5315
2022-11-16 22:00 | 3.0792
2022-11-16 23:00 | 0.9436
2022-11-17 | 0.98117
2022-11-17 01:00 | 0.98117
2022-11-17 02:00 | 0.98312
2022-11-17 03:00 | 0.98117
2022-11-17 04:00 | 0.98601
2022-11-17 05:00 | 0.99172
2022-11-17 06:00 | 1.007
2022-11-17 07:00 | 3.8656
2022-11-17 08:00 | 6.8339
2022-11-17 09:00 | 6.8174
2022-11-17 10:00 | 6.7833
2022-11-17 11:00 | 6.722
2022-11-17 12:00 | 6.7106
2022-11-17 13:00 | 6.6928
2022-11-17 14:00 | 6.6835
2022-11-17 15:00 | 7.104
2022-11-17 16:00 | 7.911
2022-11-17 17:00 | 7.902
2022-11-17 18:00 | 7.9156
2022-11-17 19:00 | 7.907
2022-11-17 20:00 | 7.8898
2022-11-17 21:00 | 7.8973
2022-11-17 22:00 | 6.5452
2022-11-17 23:00 | 4.6662
2022-11-18 | 4.6861
2022-11-18 01:00 | 4.6971
2022-11-18 02:00 | 4.707
2022-11-18 03:00 | 4.708
2022-11-18 04:00 | 4.783
2022-11-18 05:00 | 4.7948
2022-11-18 06:00 | 4.8301
2022-11-18 07:00 | 4.8535
2022-11-18 08:00 | 4.8565
2022-11-18 09:00 | 5.1087
2022-11-18 10:00 | 7.9246
2022-11-18 11:00 | 7.8782
2022-11-18 12:00 | 7.8624
2022-11-18 13:00 | 7.8649
2022-11-18 14:00 | 7.8636
2022-11-18 15:00 | 7.8344
2022-11-18 16:00 | 7.8521
2022-11-18 17:00 | 7.8452
2022-11-18 18:00 | 7.87
2022-11-18 19:00 | 7.8604
2022-11-18 20:00 | 7.8447
2022-11-18 21:00 | 7.8486
2022-11-18 22:00 | 7.8595
2022-11-18 23:00 | 7.8998
2022-11-19 | 7.9103
2022-11-19 01:00 | 7.9103
2022-11-19 02:00 | 7.9249
2022-11-19 03:00 | 7.9171
2022-11-19 04:00 | 7.9384
2022-11-19 05:00 | 7.9333
2022-11-19 06:00 | 7.9453
2022-11-19 07:00 | 7.9435
2022-11-19 08:00 | 7.9221
2022-11-19 09:00 | 7.9471
2022-11-19 10:00 | 7.9427
2022-11-19 11:00 | 7.954
2022-11-19 12:00 | 7.9419
2022-11-19 13:00 | 7.945
2022-11-19 14:00 | 7.9246
2022-11-19 15:00 | 7.9138
2022-11-19 16:00 | 7.9173
2022-11-19 17:00 | 7.9257
2022-11-19 18:00 | 7.9244
2022-11-19 19:00 | 7.8755
2022-11-19 20:00 | 7.8839
2022-11-19 21:00 | 7.873
2022-11-19 22:00 | 7.8658
2022-11-19 23:00 | 7.9138
2022-11-20 | 7.8978
2022-11-20 01:00 | 7.8794
2022-11-20 02:00 | 7.8995
2022-11-20 03:00 | 7.8918
2022-11-20 04:00 | 7.9259
2022-11-20 05:00 | 7.9361
2022-11-20 06:00 | 7.9305
2022-11-20 07:00 | 7.9168
2022-11-20 08:00 | 7.9214
2022-11-20 09:00 | 7.9404
2022-11-20 10:00 | 7.9543
2022-11-20 11:00 | 7.9556
2022-11-20 12:00 | 7.9504
2022-11-20 13:00 | 7.9038
2022-11-20 14:00 | 7.9136
2022-11-20 15:00 | 7.9274
2022-11-20 16:00 | 7.9373
2022-11-20 17:00 | 7.9279
2022-11-20 18:00 | 7.944
2022-11-20 19:00 | 7.9496
2022-11-20 20:00 | 7.9532
2022-11-20 21:00 | 7.9646
2022-11-20 22:00 | 7.9486
2022-11-20 23:00 | 7.9717
2022-11-21 | 7.9764
2022-11-21 01:00 | 7.9659
2022-11-21 02:00 | 8.0126
2022-11-21 03:00 | 7.9877
2022-11-21 04:00 | 8.0011
2022-11-21 05:00 | 7.9954
2022-11-21 06:00 | 8.5002
2022-11-21 07:00 | 12.1367
2022-11-21 08:00 | 11.9254
2022-11-21 09:00 | 11.8114
2022-11-21 10:00 | 11.6449
2022-11-21 11:00 | 11.4519
2022-11-21 12:00 | 11.3499
2022-11-21 13:00 | 11.189
2022-11-21 14:00 | 10.948
2022-11-21 15:00 | 10.8479
2022-11-21 16:00 | 10.7823
2022-11-21 17:00 | 10.7047
2022-11-21 18:00 | 8.2591
2022-11-21 19:00 | 7.6862
2022-11-21 20:00 | 7.6958
2022-11-21 21:00 | 7.7102
2022-11-21 22:00 | 7.7259
2022-11-21 23:00 | 7.7403
2022-11-22 | 7.7534
2022-11-22 01:00 | 7.7495
2022-11-22 02:00 | 7.7606
2022-11-22 03:00 | 7.7701
2022-11-22 04:00 | 7.7682
2022-11-22 05:00 | 7.7633
2022-11-22 06:00 | 7.7601
2022-11-22 07:00 | 7.7829
2022-11-22 08:00 | 7.7768
2022-11-22 09:00 | 7.7547
2022-11-22 10:00 | 7.7069
2022-11-22 11:00 | 7.6803
2022-11-22 12:00 | 7.6856
2022-11-22 13:00 | 7.6795
2022-11-22 14:00 | 7.6459
2022-11-22 15:00 | 7.6522
2022-11-22 16:00 | 7.6425
2022-11-22 17:00 | 7.6351
2022-11-22 18:00 | 7.6772
2022-11-22 19:00 | 7.6793
2022-11-22 20:00 | 7.6785
2022-11-22 21:00 | 7.7331
2022-11-22 22:00 | 7.693
2022-11-22 23:00 | 7.6854
2022-11-23 | 7.7071
2022-11-23 01:00 | 7.7059
2022-11-23 02:00 | 7.7172
2022-11-23 03:00 | 7.7264
2022-11-23 04:00 | 7.7331
2022-11-23 05:00 | 7.7615
2022-11-23 06:00 | 7.7495
2022-11-23 07:00 | 7.7674
2022-11-23 08:00 | 7.7167
2022-11-23 09:00 | 0.94455
2022-11-23 10:00 | 0.90567
2022-11-23 11:00 | 0.89096
2022-11-23 12:00 | 0.9047
2022-11-23 13:00 | 0.87619
2022-11-23 14:00 | 0.88903
2022-11-23 15:00 | 0.88407
2022-11-23 16:00 | 0.92223
2022-11-23 17:00 | 1.219
2022-11-23 18:00 | 7.0825
2022-11-23 19:00 | 7.0051
2022-11-23 20:00 | 6.9809
2022-11-23 21:00 | 6.9741
2022-11-23 22:00 | 7.0201
2022-11-23 23:00 | 7.0405
2022-11-24 | 7.0551
2022-11-24 01:00 | 7.0432
2022-11-24 02:00 | 7.04
2022-11-24 03:00 | 7.0935
2022-11-24 04:00 | 7.1153
2022-11-24 05:00 | 7.1587
2022-11-24 06:00 | 7.1158
2022-11-24 07:00 | 8.3118
2022-11-24 08:00 | 12.0351
2022-11-24 09:00 | 12.0351
2022-11-24 10:00 | 12.0351
2022-11-24 11:00 | 12.0351
2022-11-24 12:00 | 12.0351
2022-11-24 13:00 | 12.0351
2022-11-24 14:00 | 7.1368
2022-11-24 15:00 | 7.1368
2022-11-24 16:00 | 7.0686
2022-11-24 17:00 | 7.0812
2022-11-24 18:00 | 7.0758
2022-11-24 19:00 | 7.0682
2022-11-24 20:00 | 7.0704
2022-11-24 21:00 | 7.0887
2022-11-24 22:00 | 7.0988
2022-11-24 23:00 | 7.078
2022-11-25 | 7.0713
2022-11-25 01:00 | 7.0682
2022-11-25 02:00 | 7.0838
2022-11-25 03:00 | 7.1515
2022-11-25 04:00 | 7.1566
2022-11-25 05:00 | 7.1457
2022-11-25 06:00 | 7.1666
2022-11-25 07:00 | 7.1666
2022-11-25 08:00 | 7.1703
2022-11-25 09:00 | 7.1486
2022-11-25 10:00 | 7.1227
2022-11-25 11:00 | 7.0641
2022-11-25 12:00 | 7.0496
2022-11-25 13:00 | 7.0651
2022-11-25 14:00 | 7.0614
2022-11-25 15:00 | 7.0519
2022-11-25 16:00 | 7.0405
2022-11-25 17:00 | 7.0225
2022-11-25 18:00 | 7.028
2022-11-25 19:00 | 7.0505
2022-11-25 20:00 | 7.0492
2022-11-25 21:00 | 7.0533
2022-11-25 22:00 | 7.0592
2022-11-25 23:00 | 7.0437
2022-11-26 | 7.0432
2022-11-26 01:00 | 7.0623
2022-11-26 02:00 | 7.1001
2022-11-26 03:00 | 7.1045
2022-11-26 04:00 | 7.1054
2022-11-26 05:00 | 7.1045
2022-11-26 06:00 | 7.1578
2022-11-26 07:00 | 7.1637
2022-11-26 08:00 | 7.1805
2022-11-26 09:00 | 7.169
2022-11-26 10:00 | 7.1193
2022-11-26 11:00 | 7.1274
2022-11-26 12:00 | 7.1149
2022-11-26 13:00 | 7.0359
2022-11-26 14:00 | 7.0483
2022-11-26 15:00 | 7.046
2022-11-26 16:00 | 7.0578
2022-11-26 17:00 | 7.0614
2022-11-26 18:00 | 7.0619
2022-11-26 19:00 | 7.078
2022-11-26 20:00 | 7.056
2022-11-26 21:00 | 7.0601
2022-11-26 22:00 | 7.0501
2022-11-26 23:00 | 7.0455
2022-11-27 | 7.0596
2022-11-27 01:00 | 7.0637
2022-11-27 02:00 | 7.0962
2022-11-27 03:00 | 7.1006
2022-11-27 04:00 | 7.1123
2022-11-27 05:00 | 7.1032
2022-11-27 06:00 | 7.1058
2022-11-27 07:00 | 7.1278
2022-11-27 08:00 | 7.1257
2022-11-27 09:00 | 7.0789
2022-11-27 10:00 | 7.0776
2022-11-27 11:00 | 7.0843
2022-11-27 12:00 | 7.0825
2022-11-27 13:00 | 7.0487
2022-11-27 14:00 | 7.0368
2022-11-27 15:00 | 7.0578
2022-11-27 16:00 | 7.0655
2022-11-27 17:00 | 7.0537
2022-11-27 18:00 | 7.0396
2022-11-27 19:00 | 7.028
2022-11-27 20:00 | 7.0089
2022-11-27 21:00 | 7.0084
2022-11-27 22:00 | 7.0042
2022-11-27 23:00 | 7.0084
2022-11-28 | 7.0173
2022-11-28 01:00 | 7.0451
2022-11-28 02:00 | 7.0528
2022-11-28 03:00 | 7.0605
2022-11-28 04:00 | 7.0578
2022-11-28 05:00 | 7.074
2022-11-28 06:00 | 7.1101
2022-11-28 07:00 | 7.9186
2022-11-28 08:00 | 7.8789
2022-11-28 09:00 | 7.8698
2022-11-28 10:00 | 7.8737
2022-11-28 11:00 | 7.8455
2022-11-28 12:00 | 7.858
2022-11-28 13:00 | 7.8366
2022-11-28 14:00 | 7.8474
2022-11-28 15:00 | 7.8496
2022-11-28 16:00 | 7.8364
2022-11-28 17:00 | 7.8545
2022-11-28 18:00 | 7.8607
2022-11-28 19:00 | 7.8864
2022-11-28 20:00 | 7.8548
2022-11-28 21:00 | 7.8881
2022-11-28 22:00 | 7.8809
2022-11-28 23:00 | 7.8769
2022-11-29 | 7.8851
2022-11-29 01:00 | 7.8908
2022-11-29 02:00 | 7.8948
2022-11-29 03:00 | 7.9259
2022-11-29 04:00 | 7.9356
2022-11-29 05:00 | 7.952
2022-11-29 06:00 | 7.9618
2022-11-29 07:00 | 8.2626
2022-11-29 08:00 | 8.5594
2022-11-29 09:00 | 8.5039
2022-11-29 10:00 | 8.4747
2022-11-29 11:00 | 8.4365
2022-11-29 12:00 | 8.3602
2022-11-29 13:00 | 8.3456
2022-11-29 14:00 | 8.3555
2022-11-29 15:00 | 8.3347
2022-11-29 16:00 | 8.3144
2022-11-29 17:00 | 8.3209
2022-11-29 18:00 | 8.3963
2022-11-29 19:00 | 8.398
2022-11-29 20:00 | 8.4408
2022-11-29 21:00 | 8.3992
2022-11-29 22:00 | 8.3836
2022-11-29 23:00 | 8.3811
2022-11-30 | 8.4067
2022-11-30 01:00 | 8.3674
2022-11-30 02:00 | 8.3779
2022-11-30 03:00 | 8.371
2022-11-30 04:00 | 8.403
2022-11-30 05:00 | 8.4172
2022-11-30 06:00 | 8.4274
2022-11-30 07:00 | 8.4707
2022-11-30 08:00 | 8.4636
2022-11-30 09:00 | 8.3955
2022-11-30 10:00 | 8.3722
2022-11-30 11:00 | 8.3046
2022-11-30 12:00 | 8.2545
2022-11-30 13:00 | 8.2043
2022-11-30 14:00 | 8.1771
2022-11-30 15:00 | 8.1931
2022-11-30 16:00 | 8.1891
2022-11-30 17:00 | 8.2017
2022-11-30 18:00 | 8.2464
2022-11-30 19:00 | 8.2253
2022-11-30 20:00 | 8.2623
2022-11-30 21:00 | 8.2401
2022-11-30 22:00 | 8.2796
2022-11-30 23:00 | 8.2898
2022-12-01 | 8.2756
2022-12-01 01:00 | 8.2817
2022-12-01 02:00 | 8.311
2022-12-01 03:00 | 8.3339
2022-12-01 04:00 | 8.361
2022-12-01 05:00 | 8.3959
2022-12-01 06:00 | 8.4013
2022-12-01 07:00 | 8.4649
2022-12-01 08:00 | 8.4236
2022-12-01 09:00 | 8.3984
2022-12-01 10:00 | 8.3767
2022-12-01 11:00 | 8.3328
2022-12-01 12:00 | 8.3293
2022-12-01 13:00 | 8.3394
2022-12-01 14:00 | 8.3378
2022-12-01 15:00 | 8.3374
2022-12-01 16:00 | 8.3646
2022-12-01 17:00 | 8.369
2022-12-01 18:00 | 8.4122
2022-12-01 19:00 | 8.3706
2022-12-01 20:00 | 8.416
2022-12-01 21:00 | 8.3618
2022-12-01 22:00 | 8.371
2022-12-01 23:00 | 8.3971
2022-12-02 | 8.4228
2022-12-02 01:00 | 8.4556
2022-12-02 02:00 | 8.4788
2022-12-02 03:00 | 8.4928
2022-12-02 04:00 | 8.515
2022-12-02 05:00 | 8.4892
2022-12-02 06:00 | 8.4951
2022-12-02 07:00 | 8.5155
2022-12-02 08:00 | 8.5141
2022-12-02 09:00 | 8.4215
2022-12-02 10:00 | 8.4063
2022-12-02 11:00 | 8.3783
2022-12-02 12:00 | 8.3702
2022-12-02 13:00 | 8.3706
2022-12-02 14:00 | 8.3942
2022-12-02 15:00 | 8.3787
2022-12-02 16:00 | 8.3722
2022-12-02 17:00 | 8.3626
2022-12-02 18:00 | 7.7425
2022-12-02 19:00 | 6.9683
2022-12-02 20:00 | 6.964
2022-12-02 21:00 | 6.9947
2022-12-02 22:00 | 7.0051
2022-12-02 23:00 | 6.999
2022-12-03 | 6.9683
2022-12-03 01:00 | 6.9315
2022-12-03 02:00 | 6.9404
2022-12-03 03:00 | 6.9434
2022-12-03 04:00 | 6.9419
2022-12-03 05:00 | 6.927
2022-12-03 06:00 | 6.9395
2022-12-03 07:00 | 6.9221
2022-12-03 08:00 | 6.9236
2022-12-03 09:00 | 6.9054
2022-12-03 10:00 | 6.9295
2022-12-03 11:00 | 6.9039
2022-12-03 12:00 | 6.8948
2022-12-03 13:00 | 6.8922
2022-12-03 14:00 | 6.8768
2022-12-03 15:00 | 6.8753
2022-12-03 16:00 | 6.8753
2022-12-03 17:00 | 6.8716
2022-12-03 18:00 | 6.8789
2022-12-03 19:00 | 6.8696
2022-12-03 20:00 | 6.8881
2022-12-03 21:00 | 6.8897
2022-12-03 22:00 | 6.9034
2022-12-03 23:00 | 6.8984
2022-12-04 | 6.927
2022-12-04 01:00 | 6.8984
2022-12-04 02:00 | 6.8753
2022-12-04 03:00 | 6.8907
2022-12-04 04:00 | 6.9325
2022-12-04 05:00 | 6.933
2022-12-04 06:00 | 6.933
2022-12-04 07:00 | 6.9615
2022-12-04 08:00 | 7.0023
2022-12-04 09:00 | 7.0243
2022-12-04 10:00 | 7.0056
2022-12-04 11:00 | 6.9885
2022-12-04 12:00 | 6.9823
2022-12-04 13:00 | 6.9698
2022-12-04 14:00 | 6.9571
2022-12-04 15:00 | 6.935
2022-12-04 16:00 | 6.9503
2022-12-04 17:00 | 6.9571
2022-12-04 18:00 | 6.9712
2022-12-04 19:00 | 6.9469
2022-12-04 20:00 | 6.9625
2022-12-04 21:00 | 6.9493
2022-12-04 22:00 | 6.9596
2022-12-04 23:00 | 6.9478
2022-12-05 | 6.9215
2022-12-05 01:00 | 6.9581
2022-12-05 02:00 | 6.964
2022-12-05 03:00 | 6.9942
2022-12-05 04:00 | 6.9923
2022-12-05 05:00 | 6.9813
2022-12-05 06:00 | 6.9837
2022-12-05 07:00 | 7.0131
2022-12-05 08:00 | 7.0009
2022-12-05 09:00 | 6.9717
2022-12-05 10:00 | 6.9761
2022-12-05 11:00 | 6.8998
2022-12-05 12:00 | 6.9054
2022-12-05 13:00 | 6.9085
2022-12-05 14:00 | 6.8742
2022-12-05 15:00 | 6.8737
2022-12-05 16:00 | 6.8784
2022-12-05 17:00 | 6.8633
2022-12-05 18:00 | 6.9215
2022-12-05 19:00 | 6.8892
2022-12-05 20:00 | 6.8763
2022-12-05 21:00 | 6.9674
2022-12-05 22:00 | 7.7966
2022-12-05 23:00 | 7.8083
2022-12-06 | 7.8183
2022-12-06 01:00 | 7.8222
2022-12-06 02:00 | 7.8499
2022-12-06 03:00 | 7.8513
2022-12-06 04:00 | 7.8649
2022-12-06 05:00 | 7.8881
2022-12-06 06:00 | 7.8797
2022-12-06 07:00 | 7.911
2022-12-06 08:00 | 6.7822
2022-12-06 09:00 | 5.1219
2022-12-06 10:00 | 5.0917
2022-12-06 11:00 | 5.0614
2022-12-06 12:00 | 5.0215
2022-12-06 13:00 | 5.0415
2022-12-06 14:00 | 4.9832
2022-12-06 15:00 | 5.0899
2022-12-06 16:00 | 5.0262
2022-12-06 17:00 | 5.0243
2022-12-06 18:00 | 5.087
2022-12-06 19:00 | 5.0586
2022-12-06 20:00 | 5.0176
2022-12-06 21:00 | 4.9553
2022-12-06 22:00 | 5.0424
2022-12-06 23:00 | 5.0936
2022-12-07 | 5.0176
2022-12-07 01:00 | 5.1116
2022-12-07 02:00 | 5.1678
2022-12-07 03:00 | 5.1743
2022-12-07 04:00 | 5.1939
2022-12-07 05:00 | 5.1715
2022-12-07 06:00 | 5.2032
2022-12-07 07:00 | 5.2632
2022-12-07 08:00 | 5.2494
2022-12-07 09:00 | 5.206
2022-12-07 10:00 | 5.1425
2022-12-07 11:00 | 5.1585
2022-12-07 12:00 | 5.087
2022-12-07 13:00 | 5.069
2022-12-07 14:00 | 5.0993
2022-12-07 15:00 | 5.0728
2022-12-07 16:00 | 5.1078
2022-12-07 17:00 | 5.1257
2022-12-07 18:00 | 5.1762
2022-12-07 19:00 | 5.1725
2022-12-07 20:00 | 5.1266
2022-12-07 21:00 | 5.1266
2022-12-07 22:00 | 5.151
2022-12-07 23:00 | 5.1407
2022-12-08 | 5.151
2022-12-08 01:00 | 5.206
2022-12-08 02:00 | 5.218
2022-12-08 03:00 | 5.3126
2022-12-08 04:00 | 5.328
2022-12-08 05:00 | 5.3642
2022-12-08 06:00 | 5.385
2022-12-08 07:00 | 5.3778
2022-12-08 08:00 | 5.2961
2022-12-08 09:00 | 5.2696
2022-12-08 10:00 | 5.2087
2022-12-08 11:00 | 5.1883
2022-12-08 12:00 | 5.1594
2022-12-08 13:00 | 5.1332
2022-12-08 14:00 | 5.1228
2022-12-08 15:00 | 5.1144
2022-12-08 16:00 | 4.3636
2022-12-08 17:00 | 2.3025
2022-12-08 18:00 | 4.6553
2022-12-08 19:00 | 4.6403
2022-12-08 20:00 | 4.6453
2022-12-08 21:00 | 4.5832
2022-12-08 22:00 | 4.5652
2022-12-08 23:00 | 4.6143
2022-12-09 | 4.6971
2022-12-09 01:00 | 4.703
2022-12-09 02:00 | 4.7229
2022-12-09 03:00 | 4.6901
2022-12-09 04:00 | 4.6792
2022-12-09 05:00 | 4.704
2022-12-09 06:00 | 4.704
2022-12-09 07:00 | 4.7633
2022-12-09 08:00 | 5.5415
2022-12-09 09:00 | 7.0596
2022-12-09 10:00 | 7.0659
2022-12-09 11:00 | 7.0243
2022-12-09 12:00 | 7.0061
2022-12-09 13:00 | 7.0018
2022-12-09 14:00 | 7.0004
2022-12-09 15:00 | 7.0014
2022-12-09 16:00 | 6.9833
2022-12-09 17:00 | 6.9823
2022-12-09 18:00 | 7.0099
2022-12-09 19:00 | 6.9375
2022-12-09 20:00 | 6.9717
2022-12-09 21:00 | 6.9625
2022-12-09 22:00 | 6.961
2022-12-09 23:00 | 6.9669
2022-12-10 | 7.0051
2022-12-10 01:00 | 7.0267
2022-12-10 02:00 | 7.0336
2022-12-10 03:00 | 7.0596
2022-12-10 04:00 | 7.0547
2022-12-10 05:00 | 7.041
2022-12-10 06:00 | 7.0641
2022-12-10 07:00 | 7.0587
2022-12-10 08:00 | 7.0816
2022-12-10 09:00 | 7.1058
2022-12-10 10:00 | 7.1019
2022-12-10 11:00 | 7.1014
2022-12-10 12:00 | 7.0962
2022-12-10 13:00 | 7.0927
2022-12-10 14:00 | 7.1014
2022-12-10 15:00 | 7.1045
2022-12-10 16:00 | 7.1158
2022-12-10 17:00 | 7.1106
2022-12-10 18:00 | 7.1253
2022-12-10 19:00 | 7.141
2022-12-10 20:00 | 7.0882
2022-12-10 21:00 | 7.0722
2022-12-10 22:00 | 7.0851
2022-12-10 23:00 | 7.0882
2022-12-11 | 7.1452
2022-12-11 01:00 | 7.1474
2022-12-11 02:00 | 7.1532
2022-12-11 03:00 | 7.1616
2022-12-11 04:00 | 7.1653
2022-12-11 05:00 | 7.1674
2022-12-11 06:00 | 7.1595
2022-12-11 07:00 | 7.1682
2022-12-11 08:00 | 7.2076
2022-12-11 09:00 | 7.2064
2022-12-11 10:00 | 7.1903
2022-12-11 11:00 | 7.1231
2022-12-11 12:00 | 7.1171
2022-12-11 13:00 | 7.1001
2022-12-11 14:00 | 7.0966
2022-12-11 15:00 | 7.0772
2022-12-11 16:00 | 7.0713
2022-12-11 17:00 | 7.1132
2022-12-11 18:00 | 7.1197
2022-12-11 19:00 | 7.1317
2022-12-11 20:00 | 7.1076
2022-12-11 21:00 | 7.0958
2022-12-11 22:00 | 7.0754
2022-12-11 23:00 | 7.0682
2022-12-12 | 7.0891
2022-12-12 01:00 | 7.1474
2022-12-12 02:00 | 7.1532
2022-12-12 03:00 | 7.1515
2022-12-12 04:00 | 7.1511
2022-12-12 05:00 | 7.1562
2022-12-12 06:00 | 7.5411
2022-12-12 07:00 | 8.5965
2022-12-12 08:00 | 8.5301
2022-12-12 09:00 | 8.4797
2022-12-12 10:00 | 8.3992
2022-12-12 11:00 | 8.3864
2022-12-12 12:00 | 8.3646
2022-12-12 13:00 | 8.3747
2022-12-12 14:00 | 8.3598
2022-12-12 15:00 | 8.3523
2022-12-12 16:00 | 8.3771
2022-12-12 17:00 | 8.3976
2022-12-12 18:00 | 8.3266
2022-12-12 19:00 | 8.3028
2022-12-12 20:00 | 8.2562
2022-12-12 21:00 | 8.3031
2022-12-12 22:00 | 8.4139
2022-12-12 23:00 | 8.3836
2022-12-13 | 8.4583
2022-12-13 01:00 | 8.4543
2022-12-13 02:00 | 8.4892
2022-12-13 03:00 | 8.4919
2022-12-13 04:00 | 8.4774
2022-12-13 05:00 | 8.4266
2022-12-13 06:00 | 8.4391
2022-12-13 07:00 | 8.4539
2022-12-13 08:00 | 8.4469
2022-12-13 09:00 | 8.3347
2022-12-13 10:00 | 8.327
2022-12-13 11:00 | 8.3076
2022-12-13 12:00 | 8.3058
2022-12-13 13:00 | 8.339
2022-12-13 14:00 | 8.2839
2022-12-13 15:00 | 8.288
2022-12-13 16:00 | 8.2673
2022-12-13 17:00 | 8.2648
2022-12-13 18:00 | 8.3122
2022-12-13 19:00 | 8.2304
2022-12-13 20:00 | 8.2687
2022-12-13 21:00 | 8.2965
2022-12-13 22:00 | 8.2759
2022-12-13 23:00 | 8.3262
2022-12-14 | 8.3359
2022-12-14 01:00 | 8.3682
2022-12-14 02:00 | 8.3803
2022-12-14 03:00 | 8.3771
2022-12-14 04:00 | 8.384
2022-12-14 05:00 | 8.3759
2022-12-14 06:00 | 8.3495
2022-12-14 07:00 | 8.3984
2022-12-14 08:00 | 8.4071
2022-12-14 09:00 | 8.3803
2022-12-14 10:00 | 8.3527
2022-12-14 11:00 | 8.3069
2022-12-14 12:00 | 8.239
2022-12-14 13:00 | 8.2464
2022-12-14 14:00 | 8.2415
2022-12-14 15:00 | 8.2394
2022-12-14 16:00 | 8.2249
2022-12-14 17:00 | 8.2185
2022-12-14 18:00 | 8.2785
2022-12-14 19:00 | 8.263
2022-12-14 20:00 | 8.2655
2022-12-14 21:00 | 8.285
2022-12-14 22:00 | 8.3698
2022-12-14 23:00 | 8.3606
2022-12-15 | 8.3186
2022-12-15 01:00 | 8.3799
2022-12-15 02:00 | 8.424
2022-12-15 03:00 | 8.4561
2022-12-15 04:00 | 8.4752
2022-12-15 05:00 | 8.4752
2022-12-15 06:00 | 8.4477
2022-12-15 07:00 | 8.4352
2022-12-15 08:00 | 8.3456
2022-12-15 09:00 | 8.357
2022-12-15 10:00 | 8.3175
2022-12-15 11:00 | 8.3031
2022-12-15 12:00 | 8.3065
2022-12-15 13:00 | 8.2767
2022-12-15 14:00 | 8.2619
2022-12-15 15:00 | 8.246
2022-12-15 16:00 | 8.237
2022-12-15 17:00 | 8.2408
2022-12-15 18:00 | 8.2531
2022-12-15 19:00 | 8.2467
2022-12-15 20:00 | 8.2872
2022-12-15 21:00 | 8.2716
2022-12-15 22:00 | 8.2408
2022-12-15 23:00 | 8.2691
2022-12-16 | 8.2591
2022-12-16 01:00 | 8.2669
2022-12-16 02:00 | 8.3122
2022-12-16 03:00 | 8.348
2022-12-16 04:00 | 8.3734
2022-12-16 05:00 | 8.3938
2022-12-16 06:00 | 8.3926
2022-12-16 07:00 | 8.3914
2022-12-16 08:00 | 8.2976
2022-12-16 09:00 | 8.263
2022-12-16 10:00 | 8.258
2022-12-16 11:00 | 8.206
2022-12-16 12:00 | 8.2239
2022-12-16 13:00 | 8.2294
2022-12-16 14:00 | 8.2232
2022-12-16 15:00 | 8.2174
2022-12-16 16:00 | 8.2124
2022-12-16 17:00 | 8.2308
2022-12-16 18:00 | 8.2283
2022-12-16 19:00 | 8.205
2022-12-16 20:00 | 8.2208
2022-12-16 21:00 | 8.2185
2022-12-16 22:00 | 8.2097
2022-12-16 23:00 | 8.199
2022-12-17 | 8.1927
2022-12-17 01:00 | 8.2222
2022-12-17 02:00 | 8.2366
2022-12-17 03:00 | 8.2222
2022-12-17 04:00 | 8.2598
2022-12-17 05:00 | 8.2608
2022-12-17 06:00 | 8.2404
2022-12-17 07:00 | 8.2777
2022-12-17 08:00 | 8.2506
2022-12-17 09:00 | 8.252
2022-12-17 10:00 | 8.2662
2022-12-17 11:00 | 8.2788
2022-12-17 12:00 | 8.2594
2022-12-17 13:00 | 8.2513
2022-12-17 14:00 | 8.2499
2022-12-17 15:00 | 8.2345
2022-12-17 16:00 | 8.2134
2022-12-17 17:00 | 8.2373
2022-12-17 18:00 | 8.2443
2022-12-17 19:00 | 8.3178
2022-12-17 20:00 | 8.2616
2022-12-17 21:00 | 8.2446
2022-12-17 22:00 | 8.2759
2022-12-17 23:00 | 8.2909
2022-12-18 | 8.3175
2022-12-18 01:00 | 8.2843
2022-12-18 02:00 | 8.2817
2022-12-18 03:00 | 8.2876
2022-12-18 04:00 | 8.332
2022-12-18 05:00 | 8.3658
2022-12-18 06:00 | 8.3515
2022-12-18 07:00 | 8.3658
2022-12-18 08:00 | 8.3602
2022-12-18 09:00 | 8.3832
2022-12-18 10:00 | 8.3905
2022-12-18 11:00 | 8.3951
2022-12-18 12:00 | 8.3706
2022-12-18 13:00 | 8.3578
2022-12-18 14:00 | 8.369
2022-12-18 15:00 | 8.3662
2022-12-18 16:00 | 8.3507
2022-12-18 17:00 | 8.339
2022-12-18 18:00 | 8.308
2022-12-18 19:00 | 8.3122
2022-12-18 20:00 | 8.332
2022-12-18 21:00 | 8.3374
2022-12-18 22:00 | 8.3091
2022-12-18 23:00 | 8.3332
2022-12-19 | 8.373
2022-12-19 01:00 | 8.3905
2022-12-19 02:00 | 8.4042
2022-12-19 03:00 | 8.4046
2022-12-19 04:00 | 8.4219
2022-12-19 05:00 | 8.4236
2022-12-19 06:00 | 8.4561
2022-12-19 07:00 | 8.4924
2022-12-19 08:00 | 8.453
2022-12-19 09:00 | 9.5145
2022-12-19 10:00 | 10.7688
2022-12-19 11:00 | 10.7374
2022-12-19 12:00 | 10.566
2022-12-19 13:00 | 10.4077
2022-12-19 14:00 | 10.3823
2022-12-19 15:00 | 10.4212
2022-12-19 16:00 | 10.373
2022-12-19 17:00 | 10.3944
2022-12-19 18:00 | 10.5916
2022-12-19 19:00 | 10.6593
2022-12-19 20:00 | 10.5323
2022-12-19 21:00 | 10.4893
2022-12-19 22:00 | 10.381
2022-12-19 23:00 | 10.4578
2022-12-20 | 10.6145
2022-12-20 01:00 | 10.4783
2022-12-20 02:00 | 10.5379
2022-12-20 03:00 | 10.7463
2022-12-20 04:00 | 10.8341
2022-12-20 05:00 | 10.7313
2022-12-20 06:00 | 10.7298
2022-12-20 07:00 | 10.9447
2022-12-20 08:00 | 11.0706
2022-12-20 09:00 | 10.9384
2022-12-20 10:00 | 10.6944
2022-12-20 11:00 | 10.401
2022-12-20 12:00 | 10.2946
2022-12-20 13:00 | 10.292
2022-12-20 14:00 | 10.4306
2022-12-20 15:00 | 10.405
2022-12-20 16:00 | 10.3493
2022-12-20 17:00 | 10.4455
2022-12-20 18:00 | 10.5816
2022-12-20 19:00 | 10.3075
2022-12-20 20:00 | 10.3611
2022-12-20 21:00 | 10.4225
2022-12-20 22:00 | 10.5859
2022-12-20 23:00 | 10.6274
2022-12-21 | 10.6607
2022-12-21 01:00 | 10.5156
2022-12-21 02:00 | 10.7582
2022-12-21 03:00 | 10.868
2022-12-21 04:00 | 10.8897
2022-12-21 05:00 | 10.7628
2022-12-21 06:00 | 10.8265
2022-12-21 07:00 | 10.8914
2022-12-21 08:00 | 10.9321
2022-12-21 09:00 | 10.8005
2022-12-21 10:00 | 10.6361
2022-12-21 11:00 | 10.5859
2022-12-21 12:00 | 10.5859
2022-12-21 13:00 | 10.5059
2022-12-21 14:00 | 10.4975
2022-12-21 15:00 | 10.301
2022-12-21 16:00 | 10.2997
2022-12-21 17:00 | 10.3322
2022-12-21 18:00 | 10.6505
2022-12-21 19:00 | 10.5281
2022-12-21 20:00 | 10.5197
2022-12-21 21:00 | 10.5281
2022-12-21 22:00 | 10.6087
2022-12-21 23:00 | 10.5688
2022-12-22 | 10.6317
2022-12-22 01:00 | 10.6375
2022-12-22 02:00 | 10.6768
2022-12-22 03:00 | 10.6491
2022-12-22 04:00 | 10.8051
2022-12-22 05:00 | 10.7553
2022-12-22 06:00 | 10.7537
2022-12-22 07:00 | 11.0266
2022-12-22 08:00 | 10.5816
2022-12-22 09:00 | 10.4428
2022-12-22 10:00 | 10.5031
2022-12-22 11:00 | 10.1734
2022-12-22 12:00 | 10.1784
2022-12-22 13:00 | 10.2971
2022-12-22 14:00 | 10.1821
2022-12-22 15:00 | 10.1366
2022-12-22 16:00 | 10.0979
2022-12-22 17:00 | 10.0729
2022-12-22 18:00 | 10.0895
2022-12-22 19:00 | 10.0304
2022-12-22 20:00 | 10.1771
2022-12-22 21:00 | 10.0351
2022-12-22 22:00 | 10.0884
2022-12-22 23:00 | 9.9487
2022-12-23 | 9.9555
2022-12-23 01:00 | 9.8762
2022-12-23 02:00 | 9.7553
2022-12-23 03:00 | 9.934
2022-12-23 04:00 | 9.8069
2022-12-23 05:00 | 9.8316
2022-12-23 06:00 | 9.8577
2022-12-23 07:00 | 9.8316
2022-12-23 08:00 | 9.7741
2022-12-23 09:00 | 9.7815
2022-12-23 10:00 | 9.7458
2022-12-23 11:00 | 9.6824
2022-12-23 12:00 | 9.6414
2022-12-23 13:00 | 9.5061
2022-12-23 14:00 | 9.606
2022-12-23 15:00 | 9.6593
2022-12-23 16:00 | 9.4932
2022-12-23 17:00 | 9.6703
2022-12-23 18:00 | 9.7129
2022-12-23 19:00 | 10.048
2022-12-23 20:00 | 10.0293
2022-12-23 21:00 | 9.9784
2022-12-23 22:00 | 9.9968
2022-12-23 23:00 | 10.0657
2022-12-24 | 10.1697
2022-12-24 01:00 | 10.0968
2022-12-24 02:00 | 10.2383
2022-12-24 03:00 | 10.5519
2022-12-24 04:00 | 10.5548
2022-12-24 05:00 | 10.603
2022-12-24 06:00 | 10.5646
2022-12-24 07:00 | 10.7135
2022-12-24 08:00 | 10.5916
2022-12-24 09:00 | 10.5632
2022-12-24 10:00 | 10.7642
2022-12-24 11:00 | 10.7748
2022-12-24 12:00 | 10.8005
2022-12-24 13:00 | 10.5703
2022-12-24 14:00 | 10.6245
2022-12-24 15:00 | 10.5958
2022-12-24 16:00 | 10.5253
2022-12-24 17:00 | 10.4646
2022-12-24 18:00 | 10.5746
2022-12-24 19:00 | 10.5887
2022-12-24 20:00 | 10.5816
2022-12-24 21:00 | 10.6812
2022-12-24 22:00 | 10.6274
2022-12-24 23:00 | 10.5337
2022-12-25 | 10.5212
2022-12-25 01:00 | 10.9227
2022-12-25 02:00 | 11.0461
2022-12-25 03:00 | 10.975
2022-12-25 04:00 | 11.2539
2022-12-25 05:00 | 11.2145
2022-12-25 06:00 | 11.1603
2022-12-25 07:00 | 11.1185
2022-12-25 08:00 | 10.6944
2022-12-25 09:00 | 10.9022
2022-12-25 10:00 | 10.8541
2022-12-25 11:00 | 10.8081
2022-12-25 12:00 | 10.7688
2022-12-25 13:00 | 10.7582
2022-12-25 14:00 | 10.851
2022-12-25 15:00 | 10.7975
2022-12-25 16:00 | 10.7388
2022-12-25 17:00 | 10.6563
2022-12-25 18:00 | 10.7165
2022-12-25 19:00 | 10.7854
2022-12-25 20:00 | 10.828
2022-12-25 21:00 | 10.8142
2022-12-25 22:00 | 10.7508
2022-12-25 23:00 | 10.8005
2022-12-26 | 10.6724
2022-12-26 01:00 | 11.0953
2022-12-26 02:00 | 11.1301
2022-12-26 03:00 | 11.1451
2022-12-26 04:00 | 11.1168
2022-12-26 05:00 | 11.1451
2022-12-26 06:00 | 11.1451
2022-12-26 07:00 | 11.2712
2022-12-26 08:00 | 11.2009
2022-12-26 09:00 | 11.1992
2022-12-26 10:00 | 11.3234
2022-12-26 11:00 | 11.299
2022-12-26 12:00 | 11.0152
2022-12-26 13:00 | 11.0607
2022-12-26 14:00 | 11.0217
2022-12-26 15:00 | 10.8341
2022-12-26 16:00 | 10.7733
2022-12-26 17:00 | 10.8142
2022-12-26 18:00 | 10.8619
2022-12-26 19:00 | 10.8572
2022-12-26 20:00 | 10.7194
2022-12-26 21:00 | 10.7076
2022-12-26 22:00 | 10.5101
2022-12-26 23:00 | 10.5212
2022-12-27 | 10.8541
2022-12-27 01:00 | 11.0055
2022-12-27 02:00 | 11.0623
2022-12-27 03:00 | 11.2868
2022-12-27 04:00 | 11.1771
2022-12-27 05:00 | 11.1218
2022-12-27 06:00 | 11.1957
2022-12-27 07:00 | 11.1906
2022-12-27 08:00 | 11.1052
2022-12-27 09:00 | 10.8265
2022-12-27 10:00 | 10.4346
2022-12-27 11:00 | 10.559
2022-12-27 12:00 | 10.5548
2022-12-27 13:00 | 10.7224
2022-12-27 14:00 | 10.8203
2022-12-27 15:00 | 10.6461
2022-12-27 16:00 | 10.6044
2022-12-27 17:00 | 10.5632
2022-12-27 18:00 | 10.626
2022-12-27 19:00 | 10.5003
2022-12-27 20:00 | 10.6738
2022-12-27 21:00 | 10.7839
2022-12-27 22:00 | 10.5674
2022-12-27 23:00 | 10.6331
2022-12-28 | 10.7343
2022-12-28 01:00 | 10.6988
2022-12-28 02:00 | 10.8929
2022-12-28 03:00 | 11.1771
2022-12-28 04:00 | 11.172
2022-12-28 05:00 | 10.9895
2022-12-28 06:00 | 10.9655
2022-12-28 07:00 | 11.2504
2022-12-28 08:00 | 11.0201
2022-12-28 09:00 | 10.8929
2022-12-28 10:00 | 10.7823
2022-12-28 11:00 | 10.6929
2022-12-28 12:00 | 10.6245
2022-12-28 13:00 | 10.6738
2022-12-28 14:00 | 10.6159
2022-12-28 15:00 | 10.5973
2022-12-28 16:00 | 10.6826
2022-12-28 17:00 | 10.7582
2022-12-28 18:00 | 10.7477
2022-12-28 19:00 | 10.5101
2022-12-28 20:00 | 10.6202
2022-12-28 21:00 | 10.6058
2022-12-28 22:00 | 10.5393
2022-12-28 23:00 | 10.6709
2022-12-29 | 10.6593
2022-12-29 01:00 | 10.8157
2022-12-29 02:00 | 10.967
2022-12-29 03:00 | 10.9416
2022-12-29 04:00 | 11.0837
2022-12-29 05:00 | 11.235
2022-12-29 06:00 | 11.189
2022-12-29 07:00 | 11.0493
2022-12-29 08:00 | 10.8835
2022-12-29 09:00 | 10.851
2022-12-29 10:00 | 10.8773
2022-12-29 11:00 | 10.8188
2022-12-29 12:00 | 10.7313
2022-12-29 13:00 | 10.6447
2022-12-29 14:00 | 10.718
2022-12-29 15:00 | 10.6361
2022-12-29 16:00 | 10.593
2022-12-29 17:00 | 10.5816
2022-12-29 18:00 | 10.7194
2022-12-29 19:00 | 10.5973
2022-12-29 20:00 | 10.4292
2022-12-29 21:00 | 10.3651
2022-12-29 22:00 | 10.4144
2022-12-29 23:00 | 10.4077
2022-12-30 | 10.6637
2022-12-30 01:00 | 10.593
2022-12-30 02:00 | 10.7239
2022-12-30 03:00 | 10.7343
2022-12-30 04:00 | 10.8311
2022-12-30 05:00 | 10.8867
2022-12-30 06:00 | 10.8479
2022-12-30 07:00 | 11.1636
2022-12-30 08:00 | 11.0837
2022-12-30 09:00 | 10.828
2022-12-30 10:00 | 10.7717
2022-12-30 11:00 | 10.5958
2022-12-30 12:00 | 10.5337
2022-12-30 13:00 | 10.4064
2022-12-30 14:00 | 10.405
2022-12-30 15:00 | 10.3088
2022-12-30 16:00 | 10.3309
2022-12-30 17:00 | 10.2971
2022-12-30 18:00 | 10.4171
2022-12-30 19:00 | 10.3519
2022-12-30 20:00 | 10.187
2022-12-30 21:00 | 10.0422
2022-12-30 22:00 | 10.0563
2022-12-30 23:00 | 10.0222
2022-12-31 | 10.0257
2022-12-31 01:00 | 10.4198
2022-12-31 02:00 | 10.5086
2022-12-31 03:00 | 10.4523
2022-12-31 04:00 | 10.4797
2022-12-31 05:00 | 10.4238
2022-12-31 06:00 | 10.4252
2022-12-31 07:00 | 10.2868
2022-12-31 08:00 | 10.3757
2022-12-31 09:00 | 10.3944
2022-12-31 10:00 | 10.3585
2022-12-31 11:00 | 10.3717
2022-12-31 12:00 | 10.3361
2022-12-31 13:00 | 10.2095
2022-12-31 14:00 | 10.11
2022-12-31 15:00 | 10.0824
2022-12-31 16:00 | 10.0586
2022-12-31 17:00 | 10.0083
2022-12-31 18:00 | 10.0049
2022-12-31 19:00 | 9.9692
2022-12-31 20:00 | 9.9522
2022-12-31 21:00 | 9.9408
2022-12-31 22:00 | 9.9105
2022-12-31 23:00 | 9.8544

## Step 1.2 Return Fan Power Data
Datetime | RMS Power (kW)
2022-03-11 09:00 | 4.0959
2022-03-11 10:00 | 4.0959
2022-03-11 11:00 | 4.0959
2022-03-11 12:00 | 4.0959
2022-03-11 13:00 | 4.0959
2022-03-11 14:00 | 4.0959
2022-03-11 15:00 | 4.0959
2022-03-11 16:00 | 4.0959
2022-03-11 17:00 | 4.0959
2022-03-11 18:00 | 4.0959
2022-03-11 19:00 | 4.0959
2022-03-11 20:00 | 2.9296
2022-03-11 21:00 | 2.9127
2022-03-11 22:00 | 2.9089
2022-03-11 23:00 | 2.9044
2022-03-12 | 2.8768
2022-03-12 01:00 | 2.9014
2022-03-12 02:00 | 2.9304
2022-03-12 03:00 | 2.9586
2022-03-12 04:00 | 2.9569
2022-03-12 05:00 | 2.9569
2022-03-12 06:00 | 2.9635
2022-03-12 07:00 | 2.9545
2022-03-12 08:00 | 2.9553
2022-03-12 09:00 | 2.9288
2022-03-12 10:00 | 2.9652
2022-03-12 11:00 | 2.9257
2022-03-12 12:00 | 2.8803
2022-03-12 13:00 | 2.8918
2022-03-12 14:00 | 2.9036
2022-03-12 15:00 | 2.9081
2022-03-12 16:00 | 2.9142
2022-03-12 17:00 | 2.9119
2022-03-12 18:00 | 2.9602
2022-03-12 19:00 | 2.9943
2022-03-12 20:00 | 2.9779
2022-03-12 21:00 | 2.961
2022-03-12 22:00 | 3.0014
2022-03-12 23:00 | 2.9848
2022-03-13 | 2.983
2022-03-13 01:00 | 3.0267
2022-03-13 02:00 | 3.0257
2022-03-13 03:00 | 3.0725
2022-03-13 04:00 | 3.0734
2022-03-13 05:00 | 3.0945
2022-03-13 06:00 | 3.0646
2022-03-13 07:00 | 3.1131
2022-03-13 08:00 | 3.1956
2022-03-13 09:00 | 3.1343
2022-03-13 10:00 | 3.1353
2022-03-13 11:00 | 3.144
2022-03-13 12:00 | 3.0754
2022-03-13 13:00 | 3.0211
2022-03-13 14:00 | 3.0139
2022-03-13 15:00 | 3.0094
2022-03-13 16:00 | 3.0103
2022-03-13 17:00 | 3.0175
2022-03-13 18:00 | 3.0257
2022-03-13 19:00 | 3.0407
2022-03-13 20:00 | 3.0646
2022-03-13 21:00 | 3.0588
2022-03-13 22:00 | 3.0257
2022-03-13 23:00 | 3.0955
2022-03-14 | 3.0794
2022-03-14 01:00 | 3.145
2022-03-14 02:00 | 3.1494
2022-03-14 03:00 | 3.1131
2022-03-14 04:00 | 3.1068
2022-03-14 05:00 | 4.0959
2022-03-14 06:00 | 4.0959
2022-03-14 07:00 | 4.0959
2022-03-14 08:00 | 4.0959
2022-03-14 09:00 | 4.0959
2022-03-14 10:00 | 4.0959
2022-03-14 11:00 | 4.0959
2022-03-14 12:00 | 4.0959
2022-03-14 13:00 | 4.0959
2022-03-14 14:00 | 4.0959
2022-03-14 15:00 | 4.0959
2022-03-14 16:00 | 4.0959
2022-03-14 17:00 | 4.0959
2022-03-14 18:00 | 4.0959
2022-03-14 19:00 | 2.9423
2022-03-14 20:00 | 2.9051
2022-03-14 21:00 | 2.9142
2022-03-14 22:00 | 2.9359
2022-03-14 23:00 | 3.0407
2022-03-15 | 3.0511
2022-03-15 01:00 | 3.0945
2022-03-15 02:00 | 3.1131
2022-03-15 03:00 | 3.1483
2022-03-15 04:00 | 3.1353
2022-03-15 05:00 | 3.1818
2022-03-15 06:00 | 4.0959
2022-03-15 07:00 | 4.0959
2022-03-15 08:00 | 4.0959
2022-03-15 09:00 | 4.0959
2022-03-15 10:00 | 4.0959
2022-03-15 11:00 | 4.0959
2022-03-15 12:00 | 4.0959
2022-03-15 13:00 | 4.0959
2022-03-15 14:00 | 4.0959
2022-03-15 15:00 | 4.0959
2022-03-15 16:00 | 4.0959
2022-03-15 17:00 | 4.0959
2022-03-15 18:00 | 0.80309
2022-03-15 19:00 | 0.84074
2022-03-15 20:00 | 0.83667
2022-03-15 21:00 | 0.82546
2022-03-15 22:00 | 0.81833
2022-03-15 23:00 | 0.81327
2022-03-16 | 0.8326
2022-03-16 01:00 | 0.85197
2022-03-16 02:00 | 0.8336
2022-03-16 03:00 | 0.82953
2022-03-16 04:00 | 0.85806
2022-03-16 05:00 | 0.86114
2022-03-16 06:00 | 4.0959
2022-03-16 07:00 | 4.0959
2022-03-16 08:00 | 4.0959
2022-03-16 09:00 | 4.0959
2022-03-16 10:00 | 4.0959
2022-03-16 11:00 | 4.0959
2022-03-16 12:00 | 4.0959
2022-03-16 13:00 | 4.0959
2022-03-16 14:00 | 4.0959
2022-03-16 15:00 | 4.0959
2022-03-16 16:00 | 4.0959
2022-03-16 17:00 | 4.0959
2022-03-16 18:00 | 2.8768
2022-03-16 19:00 | 2.9211
2022-03-16 20:00 | 2.9265
2022-03-16 21:00 | 2.9029
2022-03-16 22:00 | 2.9528
2022-03-16 23:00 | 2.9961
2022-03-17 | 2.9594
2022-03-17 01:00 | 3.004
2022-03-17 02:00 | 3.0388
2022-03-17 03:00 | 3.0378
2022-03-17 04:00 | 3.0666
2022-03-17 05:00 | 3.0454
2022-03-17 06:00 | 4.0959
2022-03-17 07:00 | 4.0959
2022-03-17 08:00 | 4.0959
2022-03-17 09:00 | 4.0959
2022-03-17 10:00 | 4.0959
2022-03-17 11:00 | 4.0959
2022-03-17 12:00 | 4.0959
2022-03-17 13:00 | 4.0959
2022-03-17 14:00 | 4.0959
2022-03-17 15:00 | 4.0959
2022-03-17 16:00 | 4.0959
2022-03-17 17:00 | 4.0959
2022-03-17 18:00 | 2.8712
2022-03-17 19:00 | 2.8761
2022-03-17 20:00 | 2.8691
2022-03-17 21:00 | 2.9553
2022-03-17 22:00 | 2.9677
2022-03-17 23:00 | 2.9969
2022-03-18 | 2.9677
2022-03-18 01:00 | 2.9686
2022-03-18 02:00 | 2.9455
2022-03-18 03:00 | 2.9594
2022-03-18 04:00 | 3.004
2022-03-18 05:00 | 3.0332
2022-03-18 06:00 | 4.0959
2022-03-18 07:00 | 4.0959
2022-03-18 08:00 | 4.0959
2022-03-18 09:00 | 4.0959
2022-03-18 10:00 | 4.0959
2022-03-18 11:00 | 4.0959
2022-03-18 12:00 | 4.0959
2022-03-18 13:00 | 4.0959
2022-03-18 14:00 | 4.0959
2022-03-18 15:00 | 4.0959
2022-03-18 16:00 | 4.0959
2022-03-18 17:00 | 4.0959
2022-03-18 18:00 | 4.0959
2022-03-18 19:00 | 2.9007
2022-03-18 20:00 | 2.9007
2022-03-18 21:00 | 2.8918
2022-03-18 22:00 | 2.9234
2022-03-18 23:00 | 2.9652
2022-03-19 | 3.0058
2022-03-19 01:00 | 2.9908
2022-03-19 02:00 | 2.9882
2022-03-19 03:00 | 2.9711
2022-03-19 04:00 | 2.9978
2022-03-19 05:00 | 2.9848
2022-03-19 06:00 | 2.9882
2022-03-19 07:00 | 2.9969
2022-03-19 08:00 | 2.9856
2022-03-19 09:00 | 2.9553
2022-03-19 10:00 | 2.9242
2022-03-19 11:00 | 2.9196
2022-03-19 12:00 | 2.9312
2022-03-19 13:00 | 2.9561
2022-03-19 14:00 | 2.9415
2022-03-19 15:00 | 2.9022
2022-03-19 16:00 | 2.8933
2022-03-19 17:00 | 2.9051
2022-03-19 18:00 | 2.8643
2022-03-19 19:00 | 2.8561
2022-03-19 20:00 | 2.8629
2022-03-19 21:00 | 2.8467
2022-03-19 22:00 | 2.8507
2022-03-19 23:00 | 2.8768
2022-03-20 | 2.8684
2022-03-20 01:00 | 2.8933
2022-03-20 02:00 | 2.9051
2022-03-20 03:00 | 2.8761
2022-03-20 04:00 | 2.8733
2022-03-20 05:00 | 2.894
2022-03-20 06:00 | 2.9007
2022-03-20 07:00 | 2.932
2022-03-20 08:00 | 2.9242
2022-03-20 09:00 | 2.8985
2022-03-20 10:00 | 2.9127
2022-03-20 11:00 | 2.8818
2022-03-20 12:00 | 2.8854
2022-03-20 13:00 | 2.8657
2022-03-20 14:00 | 2.8514
2022-03-20 15:00 | 2.8428
2022-03-20 16:00 | 2.8636
2022-03-20 17:00 | 2.8382
2022-03-20 18:00 | 2.8481
2022-03-20 19:00 | 2.8561
2022-03-20 20:00 | 2.8705
2022-03-20 21:00 | 2.8408
2022-03-20 22:00 | 2.8382
2022-03-20 23:00 | 2.8561
2022-03-21 | 2.8761
2022-03-21 01:00 | 2.894
2022-03-21 02:00 | 2.9226
2022-03-21 03:00 | 2.8977
2022-03-21 04:00 | 2.9336
2022-03-21 05:00 | 4.0959
2022-03-21 06:00 | 4.0959
2022-03-21 07:00 | 4.0959
2022-03-21 08:00 | 4.0959
2022-03-21 09:00 | 4.0959
2022-03-21 10:00 | 4.0959
2022-03-21 11:00 | 4.0959
2022-03-21 12:00 | 4.0959
2022-03-21 13:00 | 4.0959
2022-03-21 14:00 | 4.0959
2022-03-21 15:00 | 4.0959
2022-03-21 16:00 | 4.0959
2022-03-21 17:00 | 4.0959
2022-03-21 18:00 | 2.8292
2022-03-21 19:00 | 2.8754
2022-03-21 20:00 | 2.8198
2022-03-21 21:00 | 2.8016
2022-03-21 22:00 | 2.807
2022-03-21 23:00 | 2.8356
2022-03-22 | 2.833
2022-03-22 01:00 | 2.9112
2022-03-22 02:00 | 2.8726
2022-03-22 03:00 | 2.9165
2022-03-22 04:00 | 2.9312
2022-03-22 05:00 | 2.9702
2022-03-22 06:00 | 4.0959
2022-03-22 07:00 | 4.0959
2022-03-22 08:00 | 4.0959
2022-03-22 09:00 | 4.0959
2022-03-22 10:00 | 4.0959
2022-03-22 11:00 | 4.0959
2022-03-22 12:00 | 4.0959
2022-03-22 13:00 | 4.0959
2022-03-22 14:00 | 4.0959
2022-03-22 15:00 | 4.0959
2022-03-22 16:00 | 4.0959
2022-03-22 17:00 | 4.0959
2022-03-22 18:00 | 2.3338
2022-03-22 19:00 | 2.3491
2022-03-22 20:00 | 2.342
2022-03-22 21:00 | 2.3474
2022-03-22 22:00 | 2.3384
2022-03-22 23:00 | 2.3335
2022-03-23 | 2.3447
2022-03-23 01:00 | 2.3579
2022-03-23 02:00 | 2.3423
2022-03-23 03:00 | 2.3517
2022-03-23 04:00 | 2.3551
2022-03-23 05:00 | 2.3599
2022-03-23 06:00 | 4.0959
2022-03-23 07:00 | 4.0959
2022-03-23 08:00 | 4.0959
2022-03-23 09:00 | 4.0959
2022-03-23 10:00 | 4.0959
2022-03-23 11:00 | 4.0959
2022-03-23 12:00 | 4.0959
2022-03-23 13:00 | 4.0959
2022-03-23 14:00 | 4.0959
2022-03-23 15:00 | 4.0959
2022-03-23 16:00 | 4.0959
2022-03-23 17:00 | 4.0959
2022-03-23 18:00 | 2.828
2022-03-23 19:00 | 2.8382
2022-03-23 20:00 | 2.8082
2022-03-23 21:00 | 2.8173
2022-03-23 22:00 | 2.8507
2022-03-23 23:00 | 2.8421
2022-03-24 | 2.894
2022-03-24 01:00 | 2.9203
2022-03-24 02:00 | 2.9142
2022-03-24 03:00 | 2.9149
2022-03-24 04:00 | 2.9359
2022-03-24 05:00 | 2.9487
2022-03-24 06:00 | 4.0959
2022-03-24 07:00 | 4.0959
2022-03-24 08:00 | 4.0959
2022-03-24 09:00 | 4.0959
2022-03-24 10:00 | 4.0959
2022-03-24 11:00 | 4.0959
2022-03-24 12:00 | 4.0959
2022-03-24 13:00 | 4.0959
2022-03-24 14:00 | 4.0959
2022-03-24 15:00 | 4.0959
2022-03-24 16:00 | 4.0959
2022-03-24 17:00 | 4.0959
2022-03-24 18:00 | 2.8204
2022-03-24 19:00 | 2.8408
2022-03-24 20:00 | 2.8064
2022-03-24 21:00 | 2.8167
2022-03-24 22:00 | 2.8388
2022-03-24 23:00 | 2.8467
2022-03-25 | 2.8698
2022-03-25 01:00 | 2.8832
2022-03-25 02:00 | 2.8846
2022-03-25 03:00 | 2.9074
2022-03-25 04:00 | 2.8789
2022-03-25 05:00 | 2.8977
2022-03-25 06:00 | 2.9296
2022-03-25 07:00 | 2.8977
2022-03-25 08:00 | 4.0959
2022-03-25 09:00 | 4.0959
2022-03-25 10:00 | 4.0959
2022-03-25 11:00 | 4.0959
2022-03-25 12:00 | 4.0959
2022-03-25 13:00 | 4.0959
2022-03-25 14:00 | 4.0959
2022-03-25 15:00 | 4.0959
2022-03-25 16:00 | 4.0959
2022-03-25 17:00 | 4.0959
2022-03-25 18:00 | 2.8112
2022-03-25 19:00 | 2.813
2022-03-25 20:00 | 2.791
2022-03-25 21:00 | 2.7853
2022-03-25 22:00 | 2.7905
2022-03-25 23:00 | 2.8376
2022-03-26 | 2.8657
2022-03-26 01:00 | 2.8911
2022-03-26 02:00 | 2.9351
2022-03-26 03:00 | 2.9463
2022-03-26 04:00 | 2.9196
2022-03-26 05:00 | 2.9351
2022-03-26 06:00 | 2.9487
2022-03-26 07:00 | 2.9134
2022-03-26 08:00 | 2.9203
2022-03-26 09:00 | 2.9242
2022-03-26 10:00 | 2.9066
2022-03-26 11:00 | 2.8761
2022-03-26 12:00 | 2.833
2022-03-26 13:00 | 2.8235
2022-03-26 14:00 | 2.8204
2022-03-26 15:00 | 2.8118
2022-03-26 16:00 | 2.8155
2022-03-26 17:00 | 2.826
2022-03-26 18:00 | 2.8636
2022-03-26 19:00 | 2.8324
2022-03-26 20:00 | 2.8311
2022-03-26 21:00 | 2.8448
2022-03-26 22:00 | 2.8402
2022-03-26 23:00 | 2.8861
2022-03-27 | 2.8761
2022-03-27 01:00 | 2.9257
2022-03-27 02:00 | 2.9553
2022-03-27 03:00 | 2.9762
2022-03-27 04:00 | 2.9586
2022-03-27 05:00 | 2.9487
2022-03-27 06:00 | 2.9652
2022-03-27 07:00 | 2.961
2022-03-27 08:00 | 2.9796
2022-03-27 09:00 | 2.9447
2022-03-27 10:00 | 2.8933
2022-03-27 11:00 | 2.8733
2022-03-27 12:00 | 2.8712
2022-03-27 13:00 | 2.8698
2022-03-27 14:00 | 2.8622
2022-03-27 15:00 | 2.8747
2022-03-27 16:00 | 2.8507
2022-03-27 17:00 | 2.8677
2022-03-27 18:00 | 2.8882
2022-03-27 19:00 | 2.9044
2022-03-27 20:00 | 2.8992
2022-03-27 21:00 | 2.881
2022-03-27 22:00 | 2.8803
2022-03-27 23:00 | 2.8955
2022-03-28 | 2.9172
2022-03-28 01:00 | 2.9219
2022-03-28 02:00 | 2.9336
2022-03-28 03:00 | 2.961
2022-03-28 04:00 | 2.9471
2022-03-28 05:00 | 2.9694
2022-03-28 06:00 | 4.0959
2022-03-28 07:00 | 4.0959
2022-03-28 08:00 | 4.0959
2022-03-28 09:00 | 4.0959
2022-03-28 10:00 | 4.0959
2022-03-28 11:00 | 4.0959
2022-03-28 12:00 | 4.0959
2022-03-28 13:00 | 4.0959
2022-03-28 14:00 | 4.0959
2022-03-28 15:00 | 4.0959
2022-03-28 16:00 | 4.0959
2022-03-28 17:00 | 4.0959
2022-03-28 18:00 | 2.7648
2022-03-28 19:00 | 2.7632
2022-03-28 20:00 | 2.7713
2022-03-28 21:00 | 2.7697
2022-03-28 22:00 | 2.7882
2022-03-28 23:00 | 2.8058
2022-03-29 | 2.8311
2022-03-29 01:00 | 2.874
2022-03-29 02:00 | 2.9471
2022-03-29 03:00 | 2.9694
2022-03-29 04:00 | 3.0049
2022-03-29 05:00 | 2.9839
2022-03-29 06:00 | 4.0959
2022-03-29 07:00 | 4.0959
2022-03-29 08:00 | 4.0959
2022-03-29 09:00 | 4.0959
2022-03-29 10:00 | 4.0959
2022-03-29 11:00 | 4.0959
2022-03-29 12:00 | 4.0959
2022-03-29 13:00 | 4.0959
2022-03-29 14:00 | 4.0959
2022-03-29 15:00 | 4.0959
2022-03-29 16:00 | 4.0959
2022-03-29 17:00 | 4.0959
2022-03-29 18:00 | 4.0959
2022-03-29 19:00 | 2.8904
2022-03-29 20:00 | 2.8761
2022-03-29 21:00 | 2.9022
2022-03-29 22:00 | 2.9188
2022-03-29 23:00 | 2.9242
2022-03-30 | 2.9336
2022-03-30 01:00 | 2.9804
2022-03-30 02:00 | 2.9969
2022-03-30 03:00 | 2.9891
2022-03-30 04:00 | 2.9987
2022-03-30 05:00 | 2.9796
2022-03-30 06:00 | 4.0959
2022-03-30 07:00 | 4.0959
2022-03-30 08:00 | 4.0959
2022-03-30 09:00 | 4.0959
2022-03-30 10:00 | 4.0959
2022-03-30 11:00 | 4.0959
2022-03-30 12:00 | 4.0959
2022-03-30 13:00 | 4.0959
2022-03-30 14:00 | 4.0959
2022-03-30 15:00 | 4.0959
2022-03-30 16:00 | 4.0959
2022-03-30 17:00 | 4.0959
2022-03-30 18:00 | 4.0959
2022-03-30 19:00 | 4.0959
2022-03-30 20:00 | 4.0959
2022-03-30 21:00 | 2.6526
2022-03-30 22:00 | 2.8726
2022-03-30 23:00 | 2.881
2022-03-31 | 2.9296
2022-03-31 01:00 | 2.9383
2022-03-31 02:00 | 2.932
2022-03-31 03:00 | 2.9536
2022-03-31 04:00 | 2.9813
2022-03-31 05:00 | 2.9762
2022-03-31 06:00 | 4.0959
2022-03-31 07:00 | 4.0959
2022-03-31 08:00 | 4.0959
2022-03-31 09:00 | 4.0959
2022-03-31 10:00 | 4.0959
2022-03-31 11:00 | 4.0959
2022-03-31 12:00 | 4.0959
2022-03-31 13:00 | 4.0959
2022-03-31 14:00 | 4.0959
2022-03-31 15:00 | 4.0959
2022-03-31 16:00 | 4.0959
2022-03-31 17:00 | 4.0959
2022-03-31 18:00 | 2.7928
2022-03-31 19:00 | 2.8118
2022-03-31 20:00 | 2.7963
2022-03-31 21:00 | 2.8034
2022-03-31 22:00 | 2.8064
2022-03-31 23:00 | 2.874
2022-04-01 | 2.8948
2022-04-01 01:00 | 2.9344
2022-04-01 02:00 | 2.9059
2022-04-01 03:00 | 2.9074
2022-04-01 04:00 | 2.9257
2022-04-01 05:00 | 2.9431
2022-04-01 06:00 | 2.9848
2022-04-01 07:00 | 2.9219
2022-04-01 08:00 | 2.8911
2022-04-01 09:00 | 2.8926
2022-04-01 10:00 | 2.8356
2022-04-01 11:00 | 2.7945
2022-04-01 12:00 | 2.7928
2022-04-01 13:00 | 2.8292
2022-04-01 14:00 | 2.828
2022-04-01 15:00 | 2.7864
2022-04-01 16:00 | 2.8028
2022-04-01 17:00 | 2.8534
2022-04-01 18:00 | 2.5429
2022-04-01 19:00 | 0.81227
2022-04-01 20:00 | 0.82753
2022-04-01 21:00 | 0.82646
2022-04-01 22:00 | 0.79299
2022-04-01 23:00 | 0.79804
2022-04-02 | 0.81634
2022-04-02 01:00 | 0.81634
2022-04-02 02:00 | 0.81733
2022-04-02 03:00 | 0.82546
2022-04-02 04:00 | 0.83867
2022-04-02 05:00 | 0.83667
2022-04-02 06:00 | 0.81833
2022-04-02 07:00 | 0.8509
2022-04-02 08:00 | 0.82953
2022-04-02 09:00 | 0.82753
2022-04-02 10:00 | 0.82953
2022-04-02 11:00 | 0.8346
2022-04-02 12:00 | 0.83767
2022-04-02 13:00 | 0.83867
2022-04-02 14:00 | 0.82953
2022-04-02 15:00 | 0.82646
2022-04-02 16:00 | 0.82753
2022-04-02 17:00 | 0.82546
2022-04-02 18:00 | 0.82753
2022-04-02 19:00 | 0.81527
2022-04-02 20:00 | 0.80515
2022-04-02 21:00 | 0.79704
2022-04-02 22:00 | 0.8204
2022-04-02 23:00 | 0.80715
2022-04-03 | 0.81527
2022-04-03 01:00 | 0.80416
2022-04-03 02:00 | 0.80615
2022-04-03 03:00 | 0.81634
2022-04-03 04:00 | 0.81327
2022-04-03 05:00 | 0.81227
2022-04-03 06:00 | 0.8214
2022-04-03 07:00 | 0.8214
2022-04-03 08:00 | 0.82953
2022-04-03 09:00 | 0.80515
2022-04-03 10:00 | 0.80309
2022-04-03 11:00 | 0.78589
2022-04-03 12:00 | 0.79093
2022-04-03 13:00 | 0.80921
2022-04-03 14:00 | 0.81634
2022-04-03 15:00 | 0.82853
2022-04-03 16:00 | 0.81933
2022-04-03 17:00 | 0.81227
2022-04-03 18:00 | 0.82953
2022-04-03 19:00 | 0.83667
2022-04-03 20:00 | 0.82953
2022-04-03 21:00 | 0.84175
2022-04-03 22:00 | 0.8224
2022-04-03 23:00 | 0.80309
2022-04-04 | 0.8234
2022-04-04 01:00 | 0.80715
2022-04-04 02:00 | 0.8316
2022-04-04 03:00 | 0.81933
2022-04-04 04:00 | 0.82753
2022-04-04 05:00 | 0.84275
2022-04-04 06:00 | 4.0959
2022-04-04 07:00 | 4.0959
2022-04-04 08:00 | 4.0959
2022-04-04 09:00 | 4.0959
2022-04-04 10:00 | 4.0959
2022-04-04 11:00 | 4.0959
2022-04-04 12:00 | 4.0959
2022-04-04 13:00 | 4.0959
2022-04-04 14:00 | 4.0959
2022-04-04 15:00 | 4.0959
2022-04-04 16:00 | 4.0959
2022-04-04 17:00 | 0.81021
2022-04-04 18:00 | 0.81227
2022-04-04 19:00 | 0.79598
2022-04-04 20:00 | 0.80715
2022-04-04 21:00 | 0.81733
2022-04-04 22:00 | 0.8214
2022-04-04 23:00 | 0.8001
2022-04-05 | 0.81021
2022-04-05 01:00 | 0.80515
2022-04-05 02:00 | 0.81327
2022-04-05 03:00 | 0.84789
2022-04-05 04:00 | 0.83974
2022-04-05 05:00 | 0.85605
2022-04-05 06:00 | 4.0959
2022-04-05 07:00 | 4.0959
2022-04-05 08:00 | 4.0959
2022-04-05 09:00 | 4.0959
2022-04-05 10:00 | 4.0959
2022-04-05 11:00 | 4.0959
2022-04-05 12:00 | 4.0959
2022-04-05 13:00 | 4.0959
2022-04-05 14:00 | 4.0959
2022-04-05 15:00 | 4.0959
2022-04-05 16:00 | 4.0959
2022-04-05 17:00 | 0.8214
2022-04-05 18:00 | 0.8326
2022-04-05 19:00 | 0.83867
2022-04-05 20:00 | 0.8336
2022-04-05 21:00 | 0.83567
2022-04-05 22:00 | 0.83974
2022-04-05 23:00 | 0.83667
2022-04-06 | 0.84175
2022-04-06 01:00 | 0.85398
2022-04-06 02:00 | 0.85297
2022-04-06 03:00 | 0.8499
2022-04-06 04:00 | 0.88674
2022-04-06 05:00 | 0.87239
2022-04-06 06:00 | 4.0959
2022-04-06 07:00 | 4.0959
2022-04-06 08:00 | 4.0959
2022-04-06 09:00 | 4.0959
2022-04-06 10:00 | 4.0959
2022-04-06 11:00 | 4.0959
2022-04-06 12:00 | 4.0959
2022-04-06 13:00 | 4.0959
2022-04-06 14:00 | 4.0959
2022-04-06 15:00 | 4.0959
2022-04-06 16:00 | 4.0959
2022-04-06 17:00 | 2.9226
2022-04-06 18:00 | 2.9066
2022-04-06 19:00 | 2.9415
2022-04-06 20:00 | 2.9188
2022-04-06 21:00 | 2.8948
2022-04-06 22:00 | 2.9257
2022-04-06 23:00 | 2.9273
2022-04-07 | 2.9383
2022-04-07 01:00 | 3.0067
2022-04-07 02:00 | 2.9882
2022-04-07 03:00 | 2.9813
2022-04-07 04:00 | 2.9961
2022-04-07 05:00 | 3.0248
2022-04-07 06:00 | 4.0959
2022-04-07 07:00 | 4.0959
2022-04-07 08:00 | 4.0959
2022-04-07 09:00 | 4.0959
2022-04-07 10:00 | 4.0959
2022-04-07 11:00 | 4.0959
2022-04-07 12:00 | 4.0959
2022-04-07 13:00 | 2.0525
2022-04-07 14:00 | 2.0632
2022-04-07 15:00 | 4.0959
2022-04-07 16:00 | 4.0959
2022-04-07 17:00 | 3.3899
2022-04-07 18:00 | 2.8474
2022-04-07 19:00 | 2.8861
2022-04-07 20:00 | 2.8846
2022-04-07 21:00 | 2.8733
2022-04-07 22:00 | 2.9044
2022-04-07 23:00 | 2.8663
2022-04-08 | 2.9273
2022-04-08 01:00 | 2.828
2022-04-08 02:00 | 2.8768
2022-04-08 03:00 | 2.8832
2022-04-08 04:00 | 2.9112
2022-04-08 05:00 | 2.925
2022-04-08 06:00 | 4.0959
2022-04-08 07:00 | 4.0959
2022-04-08 08:00 | 4.0959
2022-04-08 09:00 | 4.0959
2022-04-08 10:00 | 4.0959
2022-04-08 11:00 | 4.0959
2022-04-08 12:00 | 4.0959
2022-04-08 13:00 | 4.0959
2022-04-08 14:00 | 4.0959
2022-04-08 15:00 | 4.0959
2022-04-08 16:00 | 4.0959
2022-04-08 17:00 | 4.0959
2022-04-08 18:00 | 2.8726
2022-04-08 19:00 | 2.8691
2022-04-08 20:00 | 2.8588
2022-04-08 21:00 | 2.8768
2022-04-08 22:00 | 2.8534
2022-04-08 23:00 | 2.8705
2022-04-09 | 2.8705
2022-04-09 01:00 | 2.8992
2022-04-09 02:00 | 2.9312
2022-04-09 03:00 | 2.9586
2022-04-09 04:00 | 2.9577
2022-04-09 05:00 | 2.9528
2022-04-09 06:00 | 2.9652
2022-04-09 07:00 | 2.9496
2022-04-09 08:00 | 2.9007
2022-04-09 09:00 | 2.8796
2022-04-09 10:00 | 2.8663
2022-04-09 11:00 | 2.8691
2022-04-09 12:00 | 2.8615
2022-04-09 13:00 | 2.8789
2022-04-09 14:00 | 2.8719
2022-04-09 15:00 | 2.867
2022-04-09 16:00 | 2.8534
2022-04-09 17:00 | 2.8267
2022-04-09 18:00 | 2.8292
2022-04-09 19:00 | 2.8317
2022-04-09 20:00 | 2.828
2022-04-09 21:00 | 2.8051
2022-04-09 22:00 | 2.8046
2022-04-09 23:00 | 2.854
2022-04-10 | 2.9545
2022-04-10 01:00 | 2.9496
2022-04-10 02:00 | 2.9431
2022-04-10 03:00 | 2.9504
2022-04-10 04:00 | 2.9463
2022-04-10 05:00 | 2.9602
2022-04-10 06:00 | 2.9669
2022-04-10 07:00 | 3.013
2022-04-10 08:00 | 3.0157
2022-04-10 09:00 | 2.9987
2022-04-10 10:00 | 2.9635
2022-04-10 11:00 | 2.9089
2022-04-10 12:00 | 2.874
2022-04-10 13:00 | 2.8719
2022-04-10 14:00 | 2.867
2022-04-10 15:00 | 2.8581
2022-04-10 16:00 | 2.8636
2022-04-10 17:00 | 2.867
2022-04-10 18:00 | 2.8754
2022-04-10 19:00 | 2.897
2022-04-10 20:00 | 2.8882
2022-04-10 21:00 | 2.8747
2022-04-10 22:00 | 2.9096
2022-04-10 23:00 | 2.9059
2022-04-11 | 2.9296
2022-04-11 01:00 | 2.9455
2022-04-11 02:00 | 2.9577
2022-04-11 03:00 | 2.9762
2022-04-11 04:00 | 3.0193
2022-04-11 05:00 | 3.022
2022-04-11 06:00 | 4.0959
2022-04-11 07:00 | 4.0959
2022-04-11 08:00 | 4.0959
2022-04-11 09:00 | 4.0959
2022-04-11 10:00 | 4.0959
2022-04-11 11:00 | 4.0959
2022-04-11 12:00 | 4.0959
2022-04-11 13:00 | 4.0959
2022-04-11 14:00 | 4.0959
2022-04-11 15:00 | 4.0959
2022-04-11 16:00 | 4.0959
2022-04-11 17:00 | 4.0959
2022-04-11 18:00 | 2.759
2022-04-11 19:00 | 2.9652
2022-04-11 20:00 | 2.9804
2022-04-11 21:00 | 2.9943
2022-04-11 22:00 | 2.9677
2022-04-11 23:00 | 2.9586
2022-04-12 | 2.9627
2022-04-12 01:00 | 2.9265
2022-04-12 02:00 | 2.925
2022-04-12 03:00 | 2.9431
2022-04-12 04:00 | 2.9367
2022-04-12 05:00 | 2.9839
2022-04-12 06:00 | 2.9865
2022-04-12 07:00 | 2.7819
2022-04-12 08:00 | 2.7859
2022-04-12 09:00 | 2.7808
2022-04-12 10:00 | 2.7681
2022-04-12 11:00 | 2.7611
2022-04-12 12:00 | 2.7611
2022-04-12 13:00 | 2.7405
2022-04-12 14:00 | 2.745
2022-04-12 15:00 | 2.7425
2022-04-12 16:00 | 2.745
2022-04-12 17:00 | 2.7847
2022-04-12 18:00 | 2.7465
2022-04-12 19:00 | 2.9134
2022-04-12 20:00 | 2.9359
2022-04-12 21:00 | 2.9022
2022-04-12 22:00 | 2.9367
2022-04-12 23:00 | 2.897
2022-04-13 | 2.9288
2022-04-13 01:00 | 2.9652
2022-04-13 02:00 | 2.9504
2022-04-13 03:00 | 2.9908
2022-04-13 04:00 | 2.9569
2022-04-13 05:00 | 2.9694
2022-04-13 06:00 | 2.9891
2022-04-13 07:00 | 2.8142
2022-04-13 08:00 | 2.7859
2022-04-13 09:00 | 2.7719
2022-04-13 10:00 | 2.736
2022-04-13 11:00 | 2.7146
2022-04-13 12:00 | 2.7119
2022-04-13 13:00 | 2.6934
2022-04-13 14:00 | 2.7119
2022-04-13 15:00 | 2.7123
2022-04-13 16:00 | 2.4421
2022-04-13 17:00 | 0.79093
2022-04-13 18:00 | 0.75456
2022-04-13 19:00 | 0.73139
2022-04-13 20:00 | 0.72434
2022-04-13 21:00 | 0.73442
2022-04-13 22:00 | 0.7364
2022-04-13 23:00 | 0.72638
2022-04-14 | 0.72737
2022-04-14 01:00 | 0.73238
2022-04-14 02:00 | 0.74445
2022-04-14 03:00 | 0.74954
2022-04-14 04:00 | 0.75357
2022-04-14 05:00 | 0.76462
2022-04-14 06:00 | 0.7717
2022-04-14 07:00 | 0.75859
2022-04-14 08:00 | 0.76058
2022-04-14 09:00 | 0.76058
2022-04-14 10:00 | 0.75456
2022-04-14 11:00 | 0.76058
2022-04-14 12:00 | 0.76058
2022-04-14 13:00 | 0.74445
2022-04-14 14:00 | 0.76462
2022-04-14 15:00 | 0.76667
2022-04-14 16:00 | 0.76667
2022-04-14 17:00 | 0.77879
2022-04-14 18:00 | 1.3029
2022-04-14 19:00 | 1.2968
2022-04-14 20:00 | 1.3039
2022-04-14 21:00 | 1.2887
2022-04-14 22:00 | 1.2672
2022-04-14 23:00 | 1.2804
2022-04-15 | 1.2753
2022-04-15 01:00 | 1.3029
2022-04-15 02:00 | 1.2887
2022-04-15 03:00 | 1.2937
2022-04-15 04:00 | 1.3009
2022-04-15 05:00 | 1.3212
2022-04-15 06:00 | 1.3171
2022-04-15 07:00 | 1.2988
2022-04-15 08:00 | 1.3029
2022-04-15 09:00 | 1.311
2022-04-15 10:00 | 1.2815
2022-04-15 11:00 | 1.2467
2022-04-15 12:00 | 1.2446
2022-04-15 13:00 | 1.22
2022-04-15 14:00 | 1.221
2022-04-15 15:00 | 1.2159
2022-04-15 16:00 | 1.2334
2022-04-15 17:00 | 1.2457
2022-04-15 18:00 | 1.2159
2022-04-15 19:00 | 1.2138
2022-04-15 20:00 | 1.2159
2022-04-15 21:00 | 1.2221
2022-04-15 22:00 | 1.2128
2022-04-15 23:00 | 1.2272
2022-04-16 | 1.2713
2022-04-16 01:00 | 1.2804
2022-04-16 02:00 | 1.2815
2022-04-16 03:00 | 1.2856
2022-04-16 04:00 | 1.2733
2022-04-16 05:00 | 1.2713
2022-04-16 06:00 | 1.2518
2022-04-16 07:00 | 1.2978
2022-04-16 08:00 | 1.2682
2022-04-16 09:00 | 1.2641
2022-04-16 10:00 | 1.2539
2022-04-16 11:00 | 1.2672
2022-04-16 12:00 | 1.2539
2022-04-16 13:00 | 1.2313
2022-04-16 14:00 | 1.2405
2022-04-16 15:00 | 1.2426
2022-04-16 16:00 | 1.2159
2022-04-16 17:00 | 1.2621
2022-04-16 18:00 | 1.2631
2022-04-16 19:00 | 1.2662
2022-04-16 20:00 | 1.2334
2022-04-16 21:00 | 1.26
2022-04-16 22:00 | 1.26
2022-04-16 23:00 | 1.2825
2022-04-17 | 1.2692
2022-04-17 01:00 | 1.2682
2022-04-17 02:00 | 1.2641
2022-04-17 03:00 | 1.2743
2022-04-17 04:00 | 1.2876
2022-04-17 05:00 | 1.2917
2022-04-17 06:00 | 1.3212
2022-04-17 07:00 | 1.3232
2022-04-17 08:00 | 1.3252
2022-04-17 09:00 | 1.3293
2022-04-17 10:00 | 1.3131
2022-04-17 11:00 | 1.311
2022-04-17 12:00 | 1.3364
2022-04-17 13:00 | 1.2917
2022-04-17 14:00 | 1.2897
2022-04-17 15:00 | 1.3059
2022-04-17 16:00 | 1.2743
2022-04-17 17:00 | 1.31
2022-04-17 18:00 | 1.2876
2022-04-17 19:00 | 1.2947
2022-04-17 20:00 | 1.2988
2022-04-17 21:00 | 1.3059
2022-04-17 22:00 | 1.2887
2022-04-17 23:00 | 1.2804
2022-04-18 | 1.3059
2022-04-18 01:00 | 1.2631
2022-04-18 02:00 | 1.2763
2022-04-18 03:00 | 1.2641
2022-04-18 04:00 | 1.2763
2022-04-18 05:00 | 1.2835
2022-04-18 06:00 | 4.0959
2022-04-18 07:00 | 4.0959
2022-04-18 08:00 | 4.0959
2022-04-18 09:00 | 4.0959
2022-04-18 10:00 | 4.0959
2022-04-18 11:00 | 4.0959
2022-04-18 12:00 | 4.0959
2022-04-18 13:00 | 4.0959
2022-04-18 14:00 | 4.0959
2022-04-18 15:00 | 4.0959
2022-04-18 16:00 | 4.0959
2022-04-18 17:00 | 4.0959
2022-04-18 18:00 | 2.4771
2022-04-18 19:00 | 2.4776
2022-04-18 20:00 | 2.4786
2022-04-18 21:00 | 2.4817
2022-04-18 22:00 | 2.4795
2022-04-18 23:00 | 2.4815
2022-04-19 | 2.4806
2022-04-19 01:00 | 2.4862
2022-04-19 02:00 | 2.4854
2022-04-19 03:00 | 2.4786
2022-04-19 04:00 | 2.4825
2022-04-19 05:00 | 2.484
2022-04-19 06:00 | 4.0959
2022-04-19 07:00 | 4.0959
2022-04-19 08:00 | 4.0959
2022-04-19 09:00 | 4.0959
2022-04-19 10:00 | 4.0959
2022-04-19 11:00 | 4.0959
2022-04-19 12:00 | 4.0959
2022-04-19 13:00 | 4.0959
2022-04-19 14:00 | 4.0959
2022-04-19 15:00 | 4.0959
2022-04-19 16:00 | 4.0959
2022-04-19 17:00 | 4.0959
2022-04-19 18:00 | 4.0959
2022-04-19 19:00 | 2.9899
2022-04-19 20:00 | 2.9736
2022-04-19 21:00 | 2.9669
2022-04-19 22:00 | 2.9504
2022-04-19 23:00 | 3.0022
2022-04-20 | 3.0435
2022-04-20 01:00 | 3.0666
2022-04-20 02:00 | 3.2215
2022-04-20 03:00 | 3.2014
2022-04-20 04:00 | 3.2556
2022-04-20 05:00 | 3.2518
2022-04-20 06:00 | 4.0959
2022-04-20 07:00 | 4.0959
2022-04-20 08:00 | 4.0959
2022-04-20 09:00 | 4.0959
2022-04-20 10:00 | 4.0959
2022-04-20 11:00 | 4.0959
2022-04-20 12:00 | 4.0959
2022-04-20 13:00 | 4.0959
2022-04-20 14:00 | 4.0959
2022-04-20 15:00 | 4.0959
2022-04-20 16:00 | 4.0959
2022-04-20 17:00 | 4.0959
2022-04-20 18:00 | 4.0959
2022-04-20 19:00 | 2.9744
2022-04-20 20:00 | 2.977
2022-04-20 21:00 | 2.9917
2022-04-20 22:00 | 2.9753
2022-04-20 23:00 | 3.0202
2022-04-21 | 3.0378
2022-04-21 01:00 | 3.1549
2022-04-21 02:00 | 3.1853
2022-04-21 03:00 | 3.1853
2022-04-21 04:00 | 3.2481
2022-04-21 05:00 | 3.2643
2022-04-21 06:00 | 4.0959
2022-04-21 07:00 | 4.0959
2022-04-21 08:00 | 4.0959
2022-04-21 09:00 | 4.0959
2022-04-21 10:00 | 4.0959
2022-04-21 11:00 | 4.0959
2022-04-21 12:00 | 4.0959
2022-04-21 13:00 | 4.0959
2022-04-21 14:00 | 4.0959
2022-04-21 15:00 | 4.0959
2022-04-21 16:00 | 4.0959
2022-04-21 17:00 | 4.0959
2022-04-21 18:00 | 4.0959
2022-04-21 19:00 | 2.9952
2022-04-21 20:00 | 2.9779
2022-04-21 21:00 | 2.9987
2022-04-21 22:00 | 2.9545
2022-04-21 23:00 | 2.9288
2022-04-22 | 2.9149
2022-04-22 01:00 | 2.9423
2022-04-22 02:00 | 2.9719
2022-04-22 03:00 | 2.9934
2022-04-22 04:00 | 3.0248
2022-04-22 05:00 | 3.0804
2022-04-22 06:00 | 4.0959
2022-04-22 07:00 | 4.0959
2022-04-22 08:00 | 4.0959
2022-04-22 09:00 | 4.0959
2022-04-22 10:00 | 4.0959
2022-04-22 11:00 | 4.0959
2022-04-22 12:00 | 4.0959
2022-04-22 13:00 | 4.0959
2022-04-22 14:00 | 4.0959
2022-04-22 15:00 | 4.0959
2022-04-22 16:00 | 4.0959
2022-04-22 17:00 | 4.0959
2022-04-22 18:00 | 4.0959
2022-04-22 19:00 | 2.9569
2022-04-22 20:00 | 2.9257
2022-04-22 21:00 | 2.9644
2022-04-22 22:00 | 2.9891
2022-04-22 23:00 | 2.9787
2022-04-23 | 2.9865
2022-04-23 01:00 | 3.1079
2022-04-23 02:00 | 3.0855
2022-04-23 03:00 | 3.0935
2022-04-23 04:00 | 3.0986
2022-04-23 05:00 | 3.144
2022-04-23 06:00 | 3.1429
2022-04-23 07:00 | 3.1549
2022-04-23 08:00 | 3.1152
2022-04-23 09:00 | 3.0895
2022-04-23 10:00 | 3.0627
2022-04-23 11:00 | 3.0588
2022-04-23 12:00 | 3.0598
2022-04-23 13:00 | 3.0085
2022-04-23 14:00 | 3.0276
2022-04-23 15:00 | 3.0332
2022-04-23 16:00 | 3.0193
2022-04-23 17:00 | 3.0112
2022-04-23 18:00 | 3.0332
2022-04-23 19:00 | 3.0121
2022-04-23 20:00 | 3.0202
2022-04-23 21:00 | 3.0598
2022-04-23 22:00 | 3.0511
2022-04-23 23:00 | 3.0511
2022-04-24 | 3.0598
2022-04-24 01:00 | 3.0666
2022-04-24 02:00 | 3.054
2022-04-24 03:00 | 3.0705
2022-04-24 04:00 | 3.0764
2022-04-24 05:00 | 3.0676
2022-04-24 06:00 | 3.0764
2022-04-24 07:00 | 3.0814
2022-04-24 08:00 | 3.0935
2022-04-24 09:00 | 3.0925
2022-04-24 10:00 | 3.0844
2022-04-24 11:00 | 3.0656
2022-04-24 12:00 | 2.9969
2022-04-24 13:00 | 3.0463
2022-04-24 14:00 | 3.0193
2022-04-24 15:00 | 2.9926
2022-04-24 16:00 | 3.0049
2022-04-24 17:00 | 3.0435
2022-04-24 18:00 | 3.0521
2022-04-24 19:00 | 3.054
2022-04-24 20:00 | 3.0397
2022-04-24 21:00 | 2.9987
2022-04-24 22:00 | 3.0257
2022-04-24 23:00 | 3.0085
2022-04-25 | 3.0407
2022-04-25 01:00 | 3.0935
2022-04-25 02:00 | 3.1225
2022-04-25 03:00 | 3.156
2022-04-25 04:00 | 3.1582
2022-04-25 05:00 | 3.1762
2022-04-25 06:00 | 4.0959
2022-04-25 07:00 | 4.0959
2022-04-25 08:00 | 4.0959
2022-04-25 09:00 | 4.0959
2022-04-25 10:00 | 4.0959
2022-04-25 11:00 | 4.0959
2022-04-25 12:00 | 4.0959
2022-04-25 13:00 | 4.0959
2022-04-25 14:00 | 4.0959
2022-04-25 15:00 | 4.0959
2022-04-25 16:00 | 4.0959
2022-04-25 17:00 | 4.0959
2022-04-25 18:00 | 2.8575
2022-04-25 19:00 | 2.9934
2022-04-25 20:00 | 2.9744
2022-04-25 21:00 | 2.9702
2022-04-25 22:00 | 3.0369
2022-04-25 23:00 | 3.0121
2022-04-26 | 3.004
2022-04-26 01:00 | 3.0784
2022-04-26 02:00 | 3.0715
2022-04-26 03:00 | 3.0715
2022-04-26 04:00 | 3.1068
2022-04-26 05:00 | 3.1343
2022-04-26 06:00 | 3.0915
2022-04-26 07:00 | 2.9081
2022-04-26 08:00 | 2.8575
2022-04-26 09:00 | 2.8629
2022-04-26 10:00 | 2.8581
2022-04-26 11:00 | 2.8337
2022-04-26 12:00 | 2.8155
2022-04-26 13:00 | 2.7893
2022-04-26 14:00 | 2.8004
2022-04-26 15:00 | 2.7887
2022-04-26 16:00 | 2.9504
2022-04-26 17:00 | 3.0157
2022-04-26 18:00 | 2.4004
2022-04-26 19:00 | 0.84582
2022-04-26 20:00 | 0.8683
2022-04-26 21:00 | 0.8499
2022-04-26 22:00 | 0.85605
2022-04-26 23:00 | 0.83667
2022-04-27 | 0.84682
2022-04-27 01:00 | 0.85806
2022-04-27 02:00 | 0.87339
2022-04-27 03:00 | 0.88466
2022-04-27 04:00 | 0.87648
2022-04-27 05:00 | 0.89285
2022-04-27 06:00 | 0.88775
2022-04-27 07:00 | 0.8673
2022-04-27 08:00 | 0.86623
2022-04-27 09:00 | 0.82646
2022-04-27 10:00 | 0.8234
2022-04-27 11:00 | 0.83667
2022-04-27 12:00 | 0.8234
2022-04-27 13:00 | 0.81733
2022-04-27 14:00 | 0.8234
2022-04-27 15:00 | 0.80821
2022-04-27 16:00 | 0.82753
2022-04-27 17:00 | 0.84682
2022-04-27 18:00 | 0.84175
2022-04-27 19:00 | 2.2325
2022-04-27 20:00 | 2.3764
2022-04-27 21:00 | 2.362
2022-04-27 22:00 | 2.3669
2022-04-27 23:00 | 2.3754
2022-04-28 | 2.3746
2022-04-28 01:00 | 2.3861
2022-04-28 02:00 | 2.3833
2022-04-28 03:00 | 2.3962
2022-04-28 04:00 | 2.398
2022-04-28 05:00 | 2.4071
2022-04-28 06:00 | 4.0959
2022-04-28 07:00 | 4.0959
2022-04-28 08:00 | 4.0959
2022-04-28 09:00 | 4.0959
2022-04-28 10:00 | 4.0959
2022-04-28 11:00 | 4.0959
2022-04-28 12:00 | 4.0959
2022-04-28 13:00 | 4.0959
2022-04-28 14:00 | 4.0959
2022-04-28 15:00 | 4.0959
2022-04-28 16:00 | 4.0959
2022-04-28 17:00 | 4.0959
2022-04-28 18:00 | 4.0959
2022-04-28 19:00 | 4.0959
2022-04-28 20:00 | 2.9561
2022-04-28 21:00 | 2.9627
2022-04-28 22:00 | 2.9399
2022-04-28 23:00 | 2.9627
2022-04-29 | 2.9908
2022-04-29 01:00 | 3.0148
2022-04-29 02:00 | 3.0157
2022-04-29 03:00 | 3.0425
2022-04-29 04:00 | 3.0607
2022-04-29 05:00 | 3.112
2022-04-29 06:00 | 4.0959
2022-04-29 07:00 | 4.0959
2022-04-29 08:00 | 4.0959
2022-04-29 09:00 | 4.0959
2022-04-29 10:00 | 4.0959
2022-04-29 11:00 | 4.0959
2022-04-29 12:00 | 4.0959
2022-04-29 13:00 | 4.0959
2022-04-29 14:00 | 4.0959
2022-04-29 15:00 | 4.0959
2022-04-29 16:00 | 4.0959
2022-04-29 17:00 | 4.0959
2022-04-29 18:00 | 2.7622
2022-04-29 19:00 | 2.9545
2022-04-29 20:00 | 2.9383
2022-04-29 21:00 | 2.9744
2022-04-29 22:00 | 2.961
2022-04-29 23:00 | 2.9917
2022-04-30 | 3.0239
2022-04-30 01:00 | 3.0804
2022-04-30 02:00 | 3.0814
2022-04-30 03:00 | 3.0965
2022-04-30 04:00 | 3.0725
2022-04-30 05:00 | 3.0935
2022-04-30 06:00 | 3.1321
2022-04-30 07:00 | 3.1204
2022-04-30 08:00 | 3.0685
2022-04-30 09:00 | 3.0834
2022-04-30 10:00 | 3.055
2022-04-30 11:00 | 2.9943
2022-04-30 12:00 | 3.0014
2022-04-30 13:00 | 2.983
2022-04-30 14:00 | 2.9926
2022-04-30 15:00 | 2.9891
2022-04-30 16:00 | 3.0022
2022-04-30 17:00 | 2.9882
2022-04-30 18:00 | 2.952
2022-04-30 19:00 | 3.0166
2022-04-30 20:00 | 3.0184
2022-04-30 21:00 | 3.0454
2022-04-30 22:00 | 3.0322
2022-04-30 23:00 | 3.0578
2022-05-01 | 3.0695
2022-05-01 01:00 | 3.0874
2022-05-01 02:00 | 3.0666
2022-05-01 03:00 | 3.0646
2022-05-01 04:00 | 3.1538
2022-05-01 05:00 | 3.144
2022-05-01 06:00 | 3.1353
2022-05-01 07:00 | 3.1527
2022-05-01 08:00 | 2.9891
2022-05-01 09:00 | 2.9839
2022-05-01 10:00 | 2.9882
2022-05-01 11:00 | 2.9952
2022-05-01 12:00 | 3.0157
2022-05-01 13:00 | 2.9753
2022-05-01 14:00 | 2.9602
2022-05-01 15:00 | 2.9677
2022-05-01 16:00 | 2.9736
2022-05-01 17:00 | 2.9762
2022-05-01 18:00 | 2.9787
2022-05-01 19:00 | 2.9736
2022-05-01 20:00 | 3.0058
2022-05-01 21:00 | 3.0049
2022-05-01 22:00 | 3.0285
2022-05-01 23:00 | 2.9987
2022-05-02 | 3.0844
2022-05-02 01:00 | 3.0794
2022-05-02 02:00 | 3.0656
2022-05-02 03:00 | 3.0715
2022-05-02 04:00 | 3.0482
2022-05-02 05:00 | 3.0745
2022-05-02 06:00 | 3.1538
2022-05-02 07:00 | 2.8977
2022-05-02 08:00 | 2.8963
2022-05-02 09:00 | 2.8527
2022-05-02 10:00 | 2.8317
2022-05-02 11:00 | 2.8235
2022-05-02 12:00 | 2.8501
2022-05-02 13:00 | 3.0112
2022-05-02 14:00 | 3.0076
2022-05-02 15:00 | 2.9969
2022-05-02 16:00 | 2.9926
2022-05-02 17:00 | 3.0511
2022-05-02 18:00 | 3.0617
2022-05-02 19:00 | 3.0685
2022-05-02 20:00 | 3.0996
2022-05-02 21:00 | 3.0965
2022-05-02 22:00 | 3.0725
2022-05-02 23:00 | 3.0454
2022-05-03 | 3.0935
2022-05-03 01:00 | 3.1483
2022-05-03 02:00 | 3.1225
2022-05-03 03:00 | 3.1571
2022-05-03 04:00 | 3.1853
2022-05-03 05:00 | 3.1649
2022-05-03 06:00 | 3.1818
2022-05-03 07:00 | 2.9536
2022-05-03 08:00 | 2.9022
2022-05-03 09:00 | 2.8588
2022-05-03 10:00 | 2.8376
2022-05-03 11:00 | 2.8402
2022-05-03 12:00 | 2.8414
2022-05-03 13:00 | 2.8106
2022-05-03 14:00 | 2.8292
2022-05-03 15:00 | 2.8088
2022-05-03 16:00 | 2.8051
2022-05-03 17:00 | 2.8636
2022-05-03 18:00 | 2.8421
2022-05-03 19:00 | 3.0874
2022-05-03 20:00 | 3.0578
2022-05-03 21:00 | 3.0148
2022-05-03 22:00 | 2.9856
2022-05-03 23:00 | 3.0085
2022-05-04 | 3.0814
2022-05-04 01:00 | 3.0745
2022-05-04 02:00 | 3.1215
2022-05-04 03:00 | 3.1343
2022-05-04 04:00 | 3.1875
2022-05-04 05:00 | 3.1739
2022-05-04 06:00 | 3.1956
2022-05-04 07:00 | 2.9423
2022-05-04 08:00 | 2.9134
2022-05-04 09:00 | 2.8481
2022-05-04 10:00 | 2.8305
2022-05-04 11:00 | 2.8501
2022-05-04 12:00 | 2.8395
2022-05-04 13:00 | 2.854
2022-05-04 14:00 | 2.8382
2022-05-04 15:00 | 2.8248
2022-05-04 16:00 | 2.8337
2022-05-04 17:00 | 2.8507
2022-05-04 18:00 | 2.8299
2022-05-04 19:00 | 3.0094
2022-05-04 20:00 | 3.0094
2022-05-04 21:00 | 3.0184
2022-05-04 22:00 | 2.9987
2022-05-04 23:00 | 3.0313
2022-05-05 | 3.0666
2022-05-05 01:00 | 3.0112
2022-05-05 02:00 | 3.053
2022-05-05 03:00 | 3.0378
2022-05-05 04:00 | 3.0407
2022-05-05 05:00 | 3.0715
2022-05-05 06:00 | 3.1017
2022-05-05 07:00 | 3.0976
2022-05-05 08:00 | 3.0705
2022-05-05 09:00 | 3.0014
2022-05-05 10:00 | 2.9383
2022-05-05 11:00 | 2.9312
2022-05-05 12:00 | 2.9383
2022-05-05 13:00 | 2.918
2022-05-05 14:00 | 2.9226
2022-05-05 15:00 | 2.9196
2022-05-05 16:00 | 2.8933
2022-05-05 17:00 | 2.9336
2022-05-05 18:00 | 2.9089
2022-05-05 19:00 | 2.9719
2022-05-05 20:00 | 2.9496
2022-05-05 21:00 | 2.9899
2022-05-05 22:00 | 3.023
2022-05-05 23:00 | 2.9644
2022-05-06 | 2.952
2022-05-06 01:00 | 3.0014
2022-05-06 02:00 | 2.9728
2022-05-06 03:00 | 3.0139
2022-05-06 04:00 | 3.0454
2022-05-06 05:00 | 3.0313
2022-05-06 06:00 | 3.0569
2022-05-06 07:00 | 3.0388
2022-05-06 08:00 | 3.0076
2022-05-06 09:00 | 3.0322
2022-05-06 10:00 | 2.9969
2022-05-06 11:00 | 2.9677
2022-05-06 12:00 | 2.9577
2022-05-06 13:00 | 3.0022
2022-05-06 14:00 | 3.004
2022-05-06 15:00 | 2.9577
2022-05-06 16:00 | 2.9943
2022-05-06 17:00 | 3.0193
2022-05-06 18:00 | 2.9969
2022-05-06 19:00 | 2.977
2022-05-06 20:00 | 2.9711
2022-05-06 21:00 | 3.0285
2022-05-06 22:00 | 2.9961
2022-05-06 23:00 | 2.9728
2022-05-07 | 3.0435
2022-05-07 01:00 | 3.0617
2022-05-07 02:00 | 3.0804
2022-05-07 03:00 | 3.0705
2022-05-07 04:00 | 3.0578
2022-05-07 05:00 | 3.0627
2022-05-07 06:00 | 3.0627
2022-05-07 07:00 | 3.1027
2022-05-07 08:00 | 3.1321
2022-05-07 09:00 | 3.1225
2022-05-07 10:00 | 3.0444
2022-05-07 11:00 | 3.0598
2022-05-07 12:00 | 3.0598
2022-05-07 13:00 | 3.0794
2022-05-07 14:00 | 3.0617
2022-05-07 15:00 | 3.0304
2022-05-07 16:00 | 3.0425
2022-05-07 17:00 | 3.0569
2022-05-07 18:00 | 3.0492
2022-05-07 19:00 | 3.0397
2022-05-07 20:00 | 3.054
2022-05-07 21:00 | 3.0569
2022-05-07 22:00 | 3.0637
2022-05-07 23:00 | 3.0588
2022-05-08 | 3.0804
2022-05-08 01:00 | 3.1582
2022-05-08 02:00 | 3.1278
2022-05-08 03:00 | 3.0148
2022-05-08 04:00 | 3.1162
2022-05-08 05:00 | 3.145
2022-05-08 06:00 | 3.1717
2022-05-08 07:00 | 3.1979
2022-05-08 08:00 | 3.2061
2022-05-08 09:00 | 3.2061
2022-05-08 10:00 | 3.0905
2022-05-08 11:00 | 3.0193
2022-05-08 12:00 | 3.0239
2022-05-08 13:00 | 3.013
2022-05-08 14:00 | 2.9952
2022-05-08 15:00 | 3.013
2022-05-08 16:00 | 3.0014
2022-05-08 17:00 | 2.9987
2022-05-08 18:00 | 3.0076
2022-05-08 19:00 | 3.053
2022-05-08 20:00 | 3.0637
2022-05-08 21:00 | 3.0267
2022-05-08 22:00 | 3.0248
2022-05-08 23:00 | 3.0676
2022-05-09 | 3.0905
2022-05-09 01:00 | 3.0407
2022-05-09 02:00 | 3.0285
2022-05-09 03:00 | 3.1762
2022-05-09 04:00 | 3.1407
2022-05-09 05:00 | 3.2143
2022-05-09 06:00 | 3.2335
2022-05-09 07:00 | 4.0959
2022-05-09 08:00 | 4.0959
2022-05-09 09:00 | 4.0959
2022-05-09 10:00 | 4.0959
2022-05-09 11:00 | 4.0959
2022-05-09 12:00 | 4.0959
2022-05-09 13:00 | 4.0959
2022-05-09 14:00 | 4.0959
2022-05-09 15:00 | 4.0959
2022-05-09 16:00 | 4.0959
2022-05-09 17:00 | 4.0959
2022-05-09 18:00 | 4.0959
2022-05-09 19:00 | 3.0157
2022-05-09 20:00 | 3.0482
2022-05-09 21:00 | 3.0617
2022-05-09 22:00 | 3.0211
2022-05-09 23:00 | 3.0774
2022-05-10 | 3.0715
2022-05-10 01:00 | 3.0976
2022-05-10 02:00 | 3.1047
2022-05-10 03:00 | 3.1225
2022-05-10 04:00 | 3.1183
2022-05-10 05:00 | 3.1494
2022-05-10 06:00 | 3.1853
2022-05-10 07:00 | 2.9536
2022-05-10 08:00 | 2.9569
2022-05-10 09:00 | 2.8719
2022-05-10 10:00 | 2.828
2022-05-10 11:00 | 2.8082
2022-05-10 12:00 | 2.7998
2022-05-10 13:00 | 2.7974
2022-05-10 14:00 | 2.8046
2022-05-10 15:00 | 2.798
2022-05-10 16:00 | 2.81
2022-05-10 17:00 | 2.81
2022-05-10 18:00 | 2.81
2022-05-10 19:00 | 3.1047
2022-05-10 20:00 | 3.0844
2022-05-10 21:00 | 3.0685
2022-05-10 22:00 | 3.1089
2022-05-10 23:00 | 3.0864
2022-05-11 | 3.1932
2022-05-11 01:00 | 3.1864
2022-05-11 02:00 | 3.1762
2022-05-11 03:00 | 3.1494
2022-05-11 04:00 | 3.2263
2022-05-11 05:00 | 3.2359
2022-05-11 06:00 | 3.2794
2022-05-11 07:00 | 2.9051
2022-05-11 08:00 | 2.8963
2022-05-11 09:00 | 2.8719
2022-05-11 10:00 | 2.8388
2022-05-11 11:00 | 2.8467
2022-05-11 12:00 | 2.835
2022-05-11 13:00 | 2.8636
2022-05-11 14:00 | 2.8441
2022-05-11 15:00 | 2.8402
2022-05-11 16:00 | 2.8363
2022-05-11 17:00 | 2.8554
2022-05-11 18:00 | 2.8051
2022-05-11 19:00 | 3.0884
2022-05-11 20:00 | 3.0734
2022-05-11 21:00 | 3.0945
2022-05-11 22:00 | 3.131
2022-05-11 23:00 | 3.1638
2022-05-12 | 3.1626
2022-05-12 01:00 | 3.1516
2022-05-12 02:00 | 3.0884
2022-05-12 03:00 | 3.1289
2022-05-12 04:00 | 3.1717
2022-05-12 05:00 | 3.1527
2022-05-12 06:00 | 4.0959
2022-05-12 07:00 | 4.0959
2022-05-12 08:00 | 4.0959
2022-05-12 09:00 | 4.0959
2022-05-12 10:00 | 4.0959
2022-05-12 11:00 | 4.0959
2022-05-12 12:00 | 4.0959
2022-05-12 13:00 | 4.0959
2022-05-12 14:00 | 4.0959
2022-05-12 15:00 | 4.0959
2022-05-12 16:00 | 4.0959
2022-05-12 17:00 | 4.0959
2022-05-12 18:00 | 4.0959
2022-05-12 19:00 | 0.89083
2022-05-12 20:00 | 0.89903
2022-05-12 21:00 | 0.91853
2022-05-12 22:00 | 0.90615
2022-05-12 23:00 | 0.91443
2022-05-13 | 0.90925
2022-05-13 01:00 | 0.91443
2022-05-13 02:00 | 0.91745
2022-05-13 03:00 | 0.90205
2022-05-13 04:00 | 0.90313
2022-05-13 05:00 | 0.93908
2022-05-13 06:00 | 0.92675
2022-05-13 07:00 | 0.89083
2022-05-13 08:00 | 0.89386
2022-05-13 09:00 | 0.87031
2022-05-13 10:00 | 0.83667
2022-05-13 11:00 | 0.85505
2022-05-13 12:00 | 0.84789
2022-05-13 13:00 | 0.84482
2022-05-13 14:00 | 0.84682
2022-05-13 15:00 | 0.8316
2022-05-13 16:00 | 0.83767
2022-05-13 17:00 | 0.99677
2022-05-13 18:00 | 1.6083
2022-05-13 19:00 | 1.6359
2022-05-13 20:00 | 1.6185
2022-05-13 21:00 | 1.6295
2022-05-13 22:00 | 1.6514
2022-05-13 23:00 | 1.6496
2022-05-14 | 1.6405
2022-05-14 01:00 | 1.6387
2022-05-14 02:00 | 1.6587
2022-05-14 03:00 | 1.6523
2022-05-14 04:00 | 1.6313
2022-05-14 05:00 | 1.6341
2022-05-14 06:00 | 1.6396
2022-05-14 07:00 | 1.6414
2022-05-14 08:00 | 1.6332
2022-05-14 09:00 | 1.6441
2022-05-14 10:00 | 1.6641
2022-05-14 11:00 | 1.6785
2022-05-14 12:00 | 1.645
2022-05-14 13:00 | 1.6559
2022-05-14 14:00 | 1.6487
2022-05-14 15:00 | 1.6478
2022-05-14 16:00 | 1.6614
2022-05-14 17:00 | 1.6441
2022-05-14 18:00 | 1.6424
2022-05-14 19:00 | 1.6323
2022-05-14 20:00 | 1.6596
2022-05-14 21:00 | 1.6668
2022-05-14 22:00 | 1.6713
2022-05-14 23:00 | 1.6542
2022-05-15 | 1.6387
2022-05-15 01:00 | 1.6148
2022-05-15 02:00 | 1.6176
2022-05-15 03:00 | 1.6194
2022-05-15 04:00 | 1.6359
2022-05-15 05:00 | 1.6212
2022-05-15 06:00 | 1.6148
2022-05-15 07:00 | 1.645
2022-05-15 08:00 | 1.6396
2022-05-15 09:00 | 1.6258
2022-05-15 10:00 | 1.6332
2022-05-15 11:00 | 1.6414
2022-05-15 12:00 | 1.6523
2022-05-15 13:00 | 1.6267
2022-05-15 14:00 | 1.6523
2022-05-15 15:00 | 1.6731
2022-05-15 16:00 | 1.6668
2022-05-15 17:00 | 1.6587
2022-05-15 18:00 | 1.6605
2022-05-15 19:00 | 1.6749
2022-05-15 20:00 | 1.635
2022-05-15 21:00 | 1.6231
2022-05-15 22:00 | 1.6659
2022-05-15 23:00 | 1.6313
2022-05-16 | 1.6332
2022-05-16 01:00 | 1.6157
2022-05-16 02:00 | 1.6258
2022-05-16 03:00 | 1.6027
2022-05-16 04:00 | 1.6377
2022-05-16 05:00 | 1.6496
2022-05-16 06:00 | 2.739
2022-05-16 07:00 | 4.0959
2022-05-16 08:00 | 4.0959
2022-05-16 09:00 | 4.0959
2022-05-16 10:00 | 4.0959
2022-05-16 11:00 | 4.0959
2022-05-16 12:00 | 4.0959
2022-05-16 13:00 | 4.0959
2022-05-16 14:00 | 4.0959
2022-05-16 15:00 | 4.0959
2022-05-16 16:00 | 4.0959
2022-05-16 17:00 | 4.0959
2022-05-16 18:00 | 2.961
2022-05-16 19:00 | 2.9577
2022-05-16 20:00 | 3.0184
2022-05-16 21:00 | 2.9661
2022-05-16 22:00 | 2.9987
2022-05-16 23:00 | 2.983
2022-05-17 | 3.0454
2022-05-17 01:00 | 2.9536
2022-05-17 02:00 | 3.022
2022-05-17 03:00 | 3.0734
2022-05-17 04:00 | 3.0844
2022-05-17 05:00 | 3.0666
2022-05-17 06:00 | 4.0959
2022-05-17 07:00 | 4.0959
2022-05-17 08:00 | 4.0959
2022-05-17 09:00 | 4.0959
2022-05-17 10:00 | 4.0959
2022-05-17 11:00 | 4.0959
2022-05-17 12:00 | 4.0959
2022-05-17 13:00 | 4.0959
2022-05-17 14:00 | 4.0959
2022-05-17 15:00 | 4.0959
2022-05-17 16:00 | 4.0959
2022-05-17 17:00 | 4.0959
2022-05-17 18:00 | 4.0959
2022-05-17 19:00 | 2.9051
2022-05-17 20:00 | 2.9439
2022-05-17 21:00 | 2.9431
2022-05-17 22:00 | 2.9172
2022-05-17 23:00 | 2.9296
2022-05-18 | 2.9908
2022-05-18 01:00 | 2.9865
2022-05-18 02:00 | 2.9652
2022-05-18 03:00 | 2.9753
2022-05-18 04:00 | 3.004
2022-05-18 05:00 | 2.9943
2022-05-18 06:00 | 4.0959
2022-05-18 07:00 | 4.0959
2022-05-18 08:00 | 4.0959
2022-05-18 09:00 | 4.0959
2022-05-18 10:00 | 4.0959
2022-05-18 11:00 | 4.0959
2022-05-18 12:00 | 4.0959
2022-05-18 13:00 | 4.0959
2022-05-18 14:00 | 2.3953
2022-05-18 15:00 | 4.0959
2022-05-18 16:00 | 4.0959
2022-05-18 17:00 | 0.82853
2022-05-18 18:00 | 0.8224
2022-05-18 19:00 | 0.86321
2022-05-18 20:00 | 0.84382
2022-05-18 21:00 | 0.86114
2022-05-18 22:00 | 0.84382
2022-05-18 23:00 | 0.81427
2022-05-19 | 0.84175
2022-05-19 01:00 | 0.8509
2022-05-19 02:00 | 0.83053
2022-05-19 03:00 | 0.8234
2022-05-19 04:00 | 0.83974
2022-05-19 05:00 | 0.86422
2022-05-19 06:00 | 4.0959
2022-05-19 07:00 | 4.0959
2022-05-19 08:00 | 4.0959
2022-05-19 09:00 | 4.0959
2022-05-19 10:00 | 4.0959
2022-05-19 11:00 | 4.0959
2022-05-19 12:00 | 4.0959
2022-05-19 13:00 | 4.0959
2022-05-19 14:00 | 4.0959
2022-05-19 15:00 | 4.0959
2022-05-19 16:00 | 4.0959
2022-05-19 17:00 | 4.0959
2022-05-19 18:00 | 2.3408
2022-05-19 19:00 | 2.3835
2022-05-19 20:00 | 2.3762
2022-05-19 21:00 | 2.3818
2022-05-19 22:00 | 2.3746
2022-05-19 23:00 | 2.3723
2022-05-20 | 2.3746
2022-05-20 01:00 | 2.384
2022-05-20 02:00 | 2.3847
2022-05-20 03:00 | 2.3908
2022-05-20 04:00 | 2.396
2022-05-20 05:00 | 2.3926
2022-05-20 06:00 | 4.0959
2022-05-20 07:00 | 4.0959
2022-05-20 08:00 | 4.0959
2022-05-20 09:00 | 4.0959
2022-05-20 10:00 | 4.0959
2022-05-20 11:00 | 4.0959
2022-05-20 12:00 | 4.0959
2022-05-20 13:00 | 4.0959
2022-05-20 14:00 | 4.0959
2022-05-20 15:00 | 4.0959
2022-05-20 16:00 | 4.0959
2022-05-20 17:00 | 4.0959
2022-05-20 18:00 | 4.0959
2022-05-20 19:00 | 2.3896
2022-05-20 20:00 | 2.3828
2022-05-20 21:00 | 2.3759
2022-05-20 22:00 | 2.3779
2022-05-20 23:00 | 2.3685
2022-05-21 | 2.3682
2022-05-21 01:00 | 2.3762
2022-05-21 02:00 | 2.3685
2022-05-21 03:00 | 2.3729
2022-05-21 04:00 | 2.3776
2022-05-21 05:00 | 2.3746
2022-05-21 06:00 | 2.3766
2022-05-21 07:00 | 2.3809
2022-05-21 08:00 | 2.3915
2022-05-21 09:00 | 2.3861
2022-05-21 10:00 | 2.3826
2022-05-21 11:00 | 2.3774
2022-05-21 12:00 | 2.3813
2022-05-21 13:00 | 2.3759
2022-05-21 14:00 | 2.3794
2022-05-21 15:00 | 2.3821
2022-05-21 16:00 | 2.3804
2022-05-21 17:00 | 2.3801
2022-05-21 18:00 | 2.3786
2022-05-21 19:00 | 2.3764
2022-05-21 20:00 | 2.3764
2022-05-21 21:00 | 2.3713
2022-05-21 22:00 | 2.3721
2022-05-21 23:00 | 2.3786
2022-05-22 | 2.3741
2022-05-22 01:00 | 2.3629
2022-05-22 02:00 | 2.3653
2022-05-22 03:00 | 2.3468
2022-05-22 04:00 | 2.3532
2022-05-22 05:00 | 2.3462
2022-05-22 06:00 | 2.3517
2022-05-22 07:00 | 2.3626
2022-05-22 08:00 | 2.3634
2022-05-22 09:00 | 2.3456
2022-05-22 10:00 | 2.3506
2022-05-22 11:00 | 2.3488
2022-05-22 12:00 | 2.3565
2022-05-22 13:00 | 2.3593
2022-05-22 14:00 | 2.3618
2022-05-22 15:00 | 2.3599
2022-05-22 16:00 | 2.3631
2022-05-22 17:00 | 2.3615
2022-05-22 18:00 | 2.3517
2022-05-22 19:00 | 2.361
2022-05-22 20:00 | 2.3514
2022-05-22 21:00 | 2.3503
2022-05-22 22:00 | 2.35
2022-05-22 23:00 | 2.3512
2022-05-23 | 2.3534
2022-05-23 01:00 | 2.3447
2022-05-23 02:00 | 2.3477
2022-05-23 03:00 | 2.3529
2022-05-23 04:00 | 2.3512
2022-05-23 05:00 | 2.361
2022-05-23 06:00 | 4.0959
2022-05-23 07:00 | 4.0959
2022-05-23 08:00 | 4.0959
2022-05-23 09:00 | 4.0959
2022-05-23 10:00 | 4.0959
2022-05-23 11:00 | 4.0959
2022-05-23 12:00 | 4.0959
2022-05-23 13:00 | 4.0959
2022-05-23 14:00 | 4.0959
2022-05-23 15:00 | 4.0959
2022-05-23 16:00 | 4.0959
2022-05-23 17:00 | 4.0959
2022-05-23 18:00 | 2.345
2022-05-23 19:00 | 2.3477
2022-05-23 20:00 | 2.3453
2022-05-23 21:00 | 2.3429
2022-05-23 22:00 | 2.3663
2022-05-23 23:00 | 2.3661
2022-05-24 | 2.3671
2022-05-24 01:00 | 2.3623
2022-05-24 02:00 | 2.3585
2022-05-24 03:00 | 2.3718
2022-05-24 04:00 | 2.3744
2022-05-24 05:00 | 2.3816
2022-05-24 06:00 | 4.0959
2022-05-24 07:00 | 4.0959
2022-05-24 08:00 | 4.0959
2022-05-24 09:00 | 4.0959
2022-05-24 10:00 | 4.0959
2022-05-24 11:00 | 4.0959
2022-05-24 12:00 | 4.0959
2022-05-24 13:00 | 4.0959
2022-05-24 14:00 | 4.0959
2022-05-24 15:00 | 4.0959
2022-05-24 16:00 | 4.0959
2022-05-24 17:00 | 3.2445
2022-05-24 18:00 | 0.82446
2022-05-24 19:00 | 0.8224
2022-05-24 20:00 | 0.82753
2022-05-24 21:00 | 0.83867
2022-05-24 22:00 | 0.84482
2022-05-24 23:00 | 0.8509
2022-05-25 | 0.8316
2022-05-25 01:00 | 0.85398
2022-05-25 02:00 | 0.86321
2022-05-25 03:00 | 0.87849
2022-05-25 04:00 | 0.91234
2022-05-25 05:00 | 0.92264
2022-05-25 06:00 | 4.0959
2022-05-25 07:00 | 4.0959
2022-05-25 08:00 | 4.0959
2022-05-25 09:00 | 4.0959
2022-05-25 10:00 | 4.0959
2022-05-25 11:00 | 4.0959
2022-05-25 12:00 | 4.0959
2022-05-25 13:00 | 4.0959
2022-05-25 14:00 | 4.0959
2022-05-25 15:00 | 4.0959
2022-05-25 16:00 | 4.0959
2022-05-25 17:00 | 4.0959
2022-05-25 18:00 | 4.0959
2022-05-25 19:00 | 2.3999
2022-05-25 20:00 | 2.4008
2022-05-25 21:00 | 2.4163
2022-05-25 22:00 | 2.4112
2022-05-25 23:00 | 2.4095
2022-05-26 | 2.4089
2022-05-26 01:00 | 2.3999
2022-05-26 02:00 | 2.4114
2022-05-26 03:00 | 2.4135
2022-05-26 04:00 | 2.4149
2022-05-26 05:00 | 2.4191
2022-05-26 06:00 | 4.0959
2022-05-26 07:00 | 4.0959
2022-05-26 08:00 | 4.0959
2022-05-26 09:00 | 4.0959
2022-05-26 10:00 | 4.0959
2022-05-26 11:00 | 4.0959
2022-05-26 12:00 | 4.0959
2022-05-26 13:00 | 4.0959
2022-05-26 14:00 | 4.0959
2022-05-26 15:00 | 4.0959
2022-05-26 16:00 | 4.0959
2022-05-26 17:00 | 4.0959
2022-05-26 18:00 | 2.3774
2022-05-26 19:00 | 2.4025
2022-05-26 20:00 | 2.4056
2022-05-26 21:00 | 2.3988
2022-05-26 22:00 | 2.4006
2022-05-26 23:00 | 2.398
2022-05-27 | 2.3946
2022-05-27 01:00 | 2.396
2022-05-27 02:00 | 2.3852
2022-05-27 03:00 | 2.3899
2022-05-27 04:00 | 2.3899
2022-05-27 05:00 | 2.3917
2022-05-27 06:00 | 4.0959
2022-05-27 07:00 | 4.0959
2022-05-27 08:00 | 4.0959
2022-05-27 09:00 | 4.0959
2022-05-27 10:00 | 4.0959
2022-05-27 11:00 | 4.0959
2022-05-27 12:00 | 4.0959
2022-05-27 13:00 | 4.0959
2022-05-27 14:00 | 4.0959
2022-05-27 15:00 | 4.0959
2022-05-27 16:00 | 4.0959
2022-05-27 17:00 | 2.5489
2022-05-27 18:00 | 1.3222
2022-05-27 19:00 | 1.2559
2022-05-27 20:00 | 1.2457
2022-05-27 21:00 | 1.2508
2022-05-27 22:00 | 1.258
2022-05-27 23:00 | 1.2426
2022-05-28 | 1.2498
2022-05-28 01:00 | 1.2436
2022-05-28 02:00 | 1.2138
2022-05-28 03:00 | 1.2293
2022-05-28 04:00 | 1.2149
2022-05-28 05:00 | 1.2097
2022-05-28 06:00 | 1.2457
2022-05-28 07:00 | 1.2149
2022-05-28 08:00 | 1.2446
2022-05-28 09:00 | 1.259
2022-05-28 10:00 | 1.2508
2022-05-28 11:00 | 1.2528
2022-05-28 12:00 | 1.258
2022-05-28 13:00 | 1.2313
2022-05-28 14:00 | 1.2118
2022-05-28 15:00 | 1.2457
2022-05-28 16:00 | 1.2056
2022-05-28 17:00 | 1.2303
2022-05-28 18:00 | 1.2086
2022-05-28 19:00 | 1.2395
2022-05-28 20:00 | 1.2518
2022-05-28 21:00 | 1.2457
2022-05-28 22:00 | 1.22
2022-05-28 23:00 | 1.2385
2022-05-29 | 1.2252
2022-05-29 01:00 | 1.1953
2022-05-29 02:00 | 1.2097
2022-05-29 03:00 | 1.2035
2022-05-29 04:00 | 1.2035
2022-05-29 05:00 | 1.2107
2022-05-29 06:00 | 1.2159
2022-05-29 07:00 | 1.218
2022-05-29 08:00 | 1.2272
2022-05-29 09:00 | 1.2045
2022-05-29 10:00 | 1.2107
2022-05-29 11:00 | 1.1798
2022-05-29 12:00 | 1.1881
2022-05-29 13:00 | 1.1891
2022-05-29 14:00 | 1.221
2022-05-29 15:00 | 1.2076
2022-05-29 16:00 | 1.2097
2022-05-29 17:00 | 1.2231
2022-05-29 18:00 | 1.2159
2022-05-29 19:00 | 1.2015
2022-05-29 20:00 | 1.221
2022-05-29 21:00 | 1.2293
2022-05-29 22:00 | 1.187
2022-05-29 23:00 | 1.1808
2022-05-30 | 1.1932
2022-05-30 01:00 | 1.1623
2022-05-30 02:00 | 1.1891
2022-05-30 03:00 | 1.1716
2022-05-30 04:00 | 1.1499
2022-05-30 05:00 | 1.1705
2022-05-30 06:00 | 1.1819
2022-05-30 07:00 | 4.0959
2022-05-30 08:00 | 4.0959
2022-05-30 09:00 | 4.0959
2022-05-30 10:00 | 4.0959
2022-05-30 11:00 | 4.0959
2022-05-30 12:00 | 4.0959
2022-05-30 13:00 | 4.0959
2022-05-30 14:00 | 4.0959
2022-05-30 15:00 | 2.3363
2022-05-30 16:00 | 2.3503
2022-05-30 17:00 | 2.3465
2022-05-30 18:00 | 2.3599
2022-05-30 19:00 | 2.3529
2022-05-30 20:00 | 2.3462
2022-05-30 21:00 | 2.3568
2022-05-30 22:00 | 2.3543
2022-05-30 23:00 | 2.3631
2022-05-31 | 2.3639
2022-05-31 01:00 | 2.3477
2022-05-31 02:00 | 2.3585
2022-05-31 03:00 | 2.3503
2022-05-31 04:00 | 2.3534
2022-05-31 05:00 | 2.3607
2022-05-31 06:00 | 4.0959
2022-05-31 07:00 | 4.0959
2022-05-31 08:00 | 4.0959
2022-05-31 09:00 | 4.0959
2022-05-31 10:00 | 4.0959
2022-05-31 11:00 | 4.0959
2022-05-31 12:00 | 4.0959
2022-05-31 13:00 | 4.0959
2022-05-31 14:00 | 4.0959
2022-05-31 15:00 | 4.0959
2022-05-31 16:00 | 4.0959
2022-05-31 17:00 | 4.0959
2022-05-31 18:00 | 4.0959
2022-05-31 19:00 | 4.0959
2022-05-31 20:00 | 4.0959
2022-05-31 21:00 | 2.3847
2022-05-31 22:00 | 2.3885
2022-05-31 23:00 | 2.3723
2022-06-01 | 2.3669
2022-06-01 01:00 | 2.3626
2022-06-01 02:00 | 2.3669
2022-06-01 03:00 | 2.3781
2022-06-01 04:00 | 2.3671
2022-06-01 05:00 | 2.3642
2022-06-01 06:00 | 2.7137
2022-06-01 07:00 | 4.0959
2022-06-01 08:00 | 4.0959
2022-06-01 09:00 | 4.0959
2022-06-01 10:00 | 4.0959
2022-06-01 11:00 | 4.0959
2022-06-01 12:00 | 4.0959
2022-06-01 13:00 | 4.0959
2022-06-01 14:00 | 4.0959
2022-06-01 15:00 | 4.0959
2022-06-01 16:00 | 4.0959
2022-06-01 17:00 | 4.0959
2022-06-01 18:00 | 4.0959
2022-06-01 19:00 | 2.3917
2022-06-01 20:00 | 2.3682
2022-06-01 21:00 | 2.3721
2022-06-01 22:00 | 2.3669
2022-06-01 23:00 | 2.3543
2022-06-02 | 2.359
2022-06-02 01:00 | 2.3512
2022-06-02 02:00 | 2.3557
2022-06-02 03:00 | 2.3551
2022-06-02 04:00 | 2.3599
2022-06-02 05:00 | 2.365
2022-06-02 06:00 | 4.0959
2022-06-02 07:00 | 4.0959
2022-06-02 08:00 | 4.0959
2022-06-02 09:00 | 4.0959
2022-06-02 10:00 | 4.0959
2022-06-02 11:00 | 4.0959
2022-06-02 12:00 | 4.0959
2022-06-02 13:00 | 4.0959
2022-06-02 14:00 | 4.0959
2022-06-02 15:00 | 4.0959
2022-06-02 16:00 | 4.0959
2022-06-02 17:00 | 4.0959
2022-06-02 18:00 | 4.0959
2022-06-02 19:00 | 2.3596
2022-06-02 20:00 | 2.3599
2022-06-02 21:00 | 2.3577
2022-06-02 22:00 | 2.3585
2022-06-02 23:00 | 2.3637
2022-06-03 | 2.3588
2022-06-03 01:00 | 2.3543
2022-06-03 02:00 | 2.354
2022-06-03 03:00 | 2.3453
2022-06-03 04:00 | 2.348
2022-06-03 05:00 | 2.3607
2022-06-03 06:00 | 4.0959
2022-06-03 07:00 | 4.0959
2022-06-03 08:00 | 4.0959
2022-06-03 09:00 | 4.0959
2022-06-03 10:00 | 4.0959
2022-06-03 11:00 | 4.0959
2022-06-03 12:00 | 4.0959
2022-06-03 13:00 | 4.0959
2022-06-03 14:00 | 4.0959
2022-06-03 15:00 | 4.0959
2022-06-03 16:00 | 4.0959
2022-06-03 17:00 | 4.0959
2022-06-03 18:00 | 4.0959
2022-06-03 19:00 | 4.0959
2022-06-03 20:00 | 4.0959
2022-06-03 21:00 | 2.3716
2022-06-03 22:00 | 2.3746
2022-06-03 23:00 | 2.3703
2022-06-04 | 2.3618
2022-06-04 01:00 | 2.3444
2022-06-04 02:00 | 2.3562
2022-06-04 03:00 | 2.3653
2022-06-04 04:00 | 2.3596
2022-06-04 05:00 | 2.3596
2022-06-04 06:00 | 2.3551
2022-06-04 07:00 | 2.3642
2022-06-04 08:00 | 2.3529
2022-06-04 09:00 | 2.3543
2022-06-04 10:00 | 2.3599
2022-06-04 11:00 | 2.3517
2022-06-04 12:00 | 2.3506
2022-06-04 13:00 | 2.3574
2022-06-04 14:00 | 2.352
2022-06-04 15:00 | 2.3485
2022-06-04 16:00 | 2.3509
2022-06-04 17:00 | 2.3414
2022-06-04 18:00 | 2.3399
2022-06-04 19:00 | 2.3393
2022-06-04 20:00 | 2.3462
2022-06-04 21:00 | 2.3384
2022-06-04 22:00 | 2.3387
2022-06-04 23:00 | 2.3405
2022-06-05 | 2.354
2022-06-05 01:00 | 2.3483
2022-06-05 02:00 | 2.3546
2022-06-05 03:00 | 2.348
2022-06-05 04:00 | 2.3503
2022-06-05 05:00 | 2.3588
2022-06-05 06:00 | 2.3585
2022-06-05 07:00 | 2.3623
2022-06-05 08:00 | 2.362
2022-06-05 09:00 | 2.3666
2022-06-05 10:00 | 2.3663
2022-06-05 11:00 | 2.3512
2022-06-05 12:00 | 2.3601
2022-06-05 13:00 | 2.3658
2022-06-05 14:00 | 2.3604
2022-06-05 15:00 | 2.3604
2022-06-05 16:00 | 2.354
2022-06-05 17:00 | 2.3459
2022-06-05 18:00 | 2.3474
2022-06-05 19:00 | 2.3441
2022-06-05 20:00 | 2.3491
2022-06-05 21:00 | 2.3488
2022-06-05 22:00 | 2.3465
2022-06-05 23:00 | 2.3369
2022-06-06 | 2.3565
2022-06-06 01:00 | 2.3517
2022-06-06 02:00 | 2.356
2022-06-06 03:00 | 2.3579
2022-06-06 04:00 | 2.3647
2022-06-06 05:00 | 2.3615
2022-06-06 06:00 | 4.0959
2022-06-06 07:00 | 4.0959
2022-06-06 08:00 | 4.0959
2022-06-06 09:00 | 4.0959
2022-06-06 10:00 | 4.0959
2022-06-06 11:00 | 4.0959
2022-06-06 12:00 | 4.0959
2022-06-06 13:00 | 4.0959
2022-06-06 14:00 | 4.0959
2022-06-06 15:00 | 4.0959
2022-06-06 16:00 | 4.0959
2022-06-06 17:00 | 4.0959
2022-06-06 18:00 | 2.342
2022-06-06 19:00 | 2.3514
2022-06-06 20:00 | 2.3574
2022-06-06 21:00 | 2.359
2022-06-06 22:00 | 2.3729
2022-06-06 23:00 | 2.3526
2022-06-07 | 2.3647
2022-06-07 01:00 | 2.3626
2022-06-07 02:00 | 2.3596
2022-06-07 03:00 | 2.3661
2022-06-07 04:00 | 2.3647
2022-06-07 05:00 | 2.3762
2022-06-07 06:00 | 4.0959
2022-06-07 07:00 | 4.0959
2022-06-07 08:00 | 4.0959
2022-06-07 09:00 | 4.0959
2022-06-07 10:00 | 4.0959
2022-06-07 11:00 | 4.0959
2022-06-07 12:00 | 4.0959
2022-06-07 13:00 | 4.0959
2022-06-07 14:00 | 4.0959
2022-06-07 15:00 | 4.0959
2022-06-07 16:00 | 4.0959
2022-06-07 17:00 | 4.0959
2022-06-07 18:00 | 2.3705
2022-06-07 19:00 | 2.3604
2022-06-07 20:00 | 2.3497
2022-06-07 21:00 | 2.3477
2022-06-07 22:00 | 2.3615
2022-06-07 23:00 | 2.3623
2022-06-08 | 2.352
2022-06-08 01:00 | 2.3441
2022-06-08 02:00 | 2.3411
2022-06-08 03:00 | 2.3378
2022-06-08 04:00 | 2.3494
2022-06-08 05:00 | 2.3596
2022-06-08 06:00 | 4.0959
2022-06-08 07:00 | 4.0959
2022-06-08 08:00 | 4.0959
2022-06-08 09:00 | 4.0959
2022-06-08 10:00 | 4.0959
2022-06-08 11:00 | 4.0959
2022-06-08 12:00 | 4.0959
2022-06-08 13:00 | 4.0959
2022-06-08 14:00 | 4.0959
2022-06-08 15:00 | 4.0959
2022-06-08 16:00 | 4.0959
2022-06-08 17:00 | 4.0959
2022-06-08 18:00 | 2.6942
2022-06-08 19:00 | 2.3577
2022-06-08 20:00 | 2.3529
2022-06-08 21:00 | 2.3588
2022-06-08 22:00 | 2.3474
2022-06-08 23:00 | 2.3417
2022-06-09 | 2.3543
2022-06-09 01:00 | 2.3468
2022-06-09 02:00 | 2.3384
2022-06-09 03:00 | 2.3441
2022-06-09 04:00 | 2.3411
2022-06-09 05:00 | 2.3477
2022-06-09 06:00 | 4.0959
2022-06-09 07:00 | 4.0959
2022-06-09 08:00 | 4.0959
2022-06-09 09:00 | 4.0959
2022-06-09 10:00 | 4.0959
2022-06-09 11:00 | 4.0959
2022-06-09 12:00 | 4.0959
2022-06-09 13:00 | 4.0959
2022-06-09 14:00 | 4.0959
2022-06-09 15:00 | 4.0959
2022-06-09 16:00 | 4.0959
2022-06-09 17:00 | 4.0959
2022-06-09 18:00 | 4.0959
2022-06-09 19:00 | 4.0959
2022-06-09 20:00 | 4.0959
2022-06-09 21:00 | 4.0959
2022-06-09 22:00 | 3.4743
2022-06-09 23:00 | 2.3698
2022-06-10 | 2.352
2022-06-10 01:00 | 2.3532
2022-06-10 02:00 | 2.3669
2022-06-10 03:00 | 2.3571
2022-06-10 04:00 | 2.3512
2022-06-10 05:00 | 2.3639
2022-06-10 06:00 | 4.0959
2022-06-10 07:00 | 4.0959
2022-06-10 08:00 | 4.0959
2022-06-10 09:00 | 4.0959
2022-06-10 10:00 | 4.0959
2022-06-10 11:00 | 4.0959
2022-06-10 12:00 | 4.0959
2022-06-10 13:00 | 4.0959
2022-06-10 14:00 | 4.0959
2022-06-10 15:00 | 4.0959
2022-06-10 16:00 | 4.0959
2022-06-10 17:00 | 4.0959
2022-06-10 18:00 | 2.383
2022-06-10 19:00 | 2.3816
2022-06-10 20:00 | 2.365
2022-06-10 21:00 | 2.3721
2022-06-10 22:00 | 2.3637
2022-06-10 23:00 | 2.3562
2022-06-11 | 2.3532
2022-06-11 01:00 | 2.3494
2022-06-11 02:00 | 2.3506
2022-06-11 03:00 | 2.3534
2022-06-11 04:00 | 2.3465
2022-06-11 05:00 | 2.3512
2022-06-11 06:00 | 2.3417
2022-06-11 07:00 | 2.3537
2022-06-11 08:00 | 2.3663
2022-06-11 09:00 | 2.3634
2022-06-11 10:00 | 2.3579
2022-06-11 11:00 | 2.3612
2022-06-11 12:00 | 2.3623
2022-06-11 13:00 | 2.3546
2022-06-11 14:00 | 2.3687
2022-06-11 15:00 | 2.3618
2022-06-11 16:00 | 2.3571
2022-06-11 17:00 | 2.3642
2022-06-11 18:00 | 2.3537
2022-06-11 19:00 | 2.3658
2022-06-11 20:00 | 2.3695
2022-06-11 21:00 | 2.3601
2022-06-11 22:00 | 2.3655
2022-06-11 23:00 | 2.3557
2022-06-12 | 2.3488
2022-06-12 01:00 | 2.3579
2022-06-12 02:00 | 2.3579
2022-06-12 03:00 | 2.3629
2022-06-12 04:00 | 2.3713
2022-06-12 05:00 | 2.3749
2022-06-12 06:00 | 2.3713
2022-06-12 07:00 | 2.3705
2022-06-12 08:00 | 2.3756
2022-06-12 09:00 | 2.3821
2022-06-12 10:00 | 2.3789
2022-06-12 11:00 | 2.3645
2022-06-12 12:00 | 2.3741
2022-06-12 13:00 | 2.3705
2022-06-12 14:00 | 2.3708
2022-06-12 15:00 | 2.3685
2022-06-12 16:00 | 2.3741
2022-06-12 17:00 | 2.3769
2022-06-12 18:00 | 2.3634
2022-06-12 19:00 | 2.3739
2022-06-12 20:00 | 2.3607
2022-06-12 21:00 | 2.361
2022-06-12 22:00 | 2.3623
2022-06-12 23:00 | 2.356
2022-06-13 | 2.3612
2022-06-13 01:00 | 2.3623
2022-06-13 02:00 | 2.3494
2022-06-13 03:00 | 2.3599
2022-06-13 04:00 | 2.3669
2022-06-13 05:00 | 2.3744
2022-06-13 06:00 | 4.0959
2022-06-13 07:00 | 4.0959
2022-06-13 08:00 | 4.0959
2022-06-13 09:00 | 4.0959
2022-06-13 10:00 | 4.0959
2022-06-13 11:00 | 4.0959
2022-06-13 12:00 | 4.0959
2022-06-13 13:00 | 4.0959
2022-06-13 14:00 | 4.0959
2022-06-13 15:00 | 4.0959
2022-06-13 16:00 | 4.0959
2022-06-13 17:00 | 4.0959
2022-06-13 18:00 | 4.0959
2022-06-13 19:00 | 4.0959
2022-06-13 20:00 | 2.4999
2022-06-13 21:00 | 2.4967
2022-06-13 22:00 | 2.4945
2022-06-13 23:00 | 2.4894
2022-06-14 | 2.4911
2022-06-14 01:00 | 2.49
2022-06-14 02:00 | 2.4884
2022-06-14 03:00 | 2.4887
2022-06-14 04:00 | 2.4875
2022-06-14 05:00 | 2.4928
2022-06-14 06:00 | 4.0959
2022-06-14 07:00 | 4.0959
2022-06-14 08:00 | 4.0959
2022-06-14 09:00 | 4.0959
2022-06-14 10:00 | 4.0959
2022-06-14 11:00 | 4.0959
2022-06-14 12:00 | 4.0959
2022-06-14 13:00 | 4.0959
2022-06-14 14:00 | 4.0959
2022-06-14 15:00 | 4.0959
2022-06-14 16:00 | 4.0959
2022-06-14 17:00 | 4.0959
2022-06-14 18:00 | 2.3804
2022-06-14 19:00 | 2.3849
2022-06-14 20:00 | 2.3736
2022-06-14 21:00 | 2.3729
2022-06-14 22:00 | 2.3658
2022-06-14 23:00 | 2.3642
2022-06-15 | 2.3734
2022-06-15 01:00 | 2.3607
2022-06-15 02:00 | 2.3645
2022-06-15 03:00 | 2.3582
2022-06-15 04:00 | 2.3653
2022-06-15 05:00 | 2.3741
2022-06-15 06:00 | 4.0959
2022-06-15 07:00 | 4.0959
2022-06-15 08:00 | 4.0959
2022-06-15 09:00 | 4.0959
2022-06-15 10:00 | 4.0959
2022-06-15 11:00 | 4.0959
2022-06-15 12:00 | 4.0959
2022-06-15 13:00 | 4.0959
2022-06-15 14:00 | 4.0959
2022-06-15 15:00 | 4.0959
2022-06-15 16:00 | 4.0959
2022-06-15 17:00 | 4.2434
2022-06-15 18:00 | 2.3736
2022-06-15 19:00 | 2.3847
2022-06-15 20:00 | 2.3721
2022-06-15 21:00 | 2.3801
2022-06-15 22:00 | 2.3786
2022-06-15 23:00 | 2.3749
2022-06-16 | 2.3774
2022-06-16 01:00 | 2.3766
2022-06-16 02:00 | 2.365
2022-06-16 03:00 | 2.3705
2022-06-16 04:00 | 2.3674
2022-06-16 05:00 | 2.3729
2022-06-16 06:00 | 4.0959
2022-06-16 07:00 | 4.0959
2022-06-16 08:00 | 4.0959
2022-06-16 09:00 | 4.0959
2022-06-16 10:00 | 4.0959
2022-06-16 11:00 | 4.0959
2022-06-16 12:00 | 4.0959
2022-06-16 13:00 | 4.0959
2022-06-16 14:00 | 4.0959
2022-06-16 15:00 | 4.0959
2022-06-16 16:00 | 4.0959
2022-06-16 17:00 | 3.1268
2022-06-16 18:00 | 2.3634
2022-06-16 19:00 | 2.3749
2022-06-16 20:00 | 2.37
2022-06-16 21:00 | 2.362
2022-06-16 22:00 | 2.3749
2022-06-16 23:00 | 2.3669
2022-06-17 | 2.3703
2022-06-17 01:00 | 2.359
2022-06-17 02:00 | 2.3554
2022-06-17 03:00 | 2.3588
2022-06-17 04:00 | 2.3585
2022-06-17 05:00 | 2.3729
2022-06-17 06:00 | 4.0959
2022-06-17 07:00 | 4.0959
2022-06-17 08:00 | 4.0959
2022-06-17 09:00 | 4.0959
2022-06-17 10:00 | 4.0959
2022-06-17 11:00 | 4.0959
2022-06-17 12:00 | 4.0959
2022-06-17 13:00 | 4.0959
2022-06-17 14:00 | 4.0959
2022-06-17 15:00 | 4.0959
2022-06-17 16:00 | 4.0959
2022-06-17 17:00 | 4.0959
2022-06-17 18:00 | 0.88365
2022-06-17 19:00 | 0.85705
2022-06-17 20:00 | 0.8214
2022-06-17 21:00 | 0.80921
2022-06-17 22:00 | 0.81634
2022-06-17 23:00 | 0.8001
2022-06-18 | 0.79804
2022-06-18 01:00 | 0.77979
2022-06-18 02:00 | 0.75859
2022-06-18 03:00 | 0.75859
2022-06-18 04:00 | 0.76971
2022-06-18 05:00 | 0.76462
2022-06-18 06:00 | 0.74954
2022-06-18 07:00 | 0.74445
2022-06-18 08:00 | 0.78994
2022-06-18 09:00 | 0.76766
2022-06-18 10:00 | 0.76362
2022-06-18 11:00 | 0.75959
2022-06-18 12:00 | 0.78085
2022-06-18 13:00 | 0.77071
2022-06-18 14:00 | 0.78085
2022-06-18 15:00 | 0.78085
2022-06-18 16:00 | 0.78085
2022-06-18 17:00 | 0.75654
2022-06-18 18:00 | 0.77071
2022-06-18 19:00 | 0.77375
2022-06-18 20:00 | 0.77879
2022-06-18 21:00 | 0.78184
2022-06-18 22:00 | 0.75959
2022-06-18 23:00 | 0.75456
2022-06-19 | 0.7576
2022-06-19 01:00 | 0.76971
2022-06-19 02:00 | 0.79904
2022-06-19 03:00 | 0.81327
2022-06-19 04:00 | 0.80416
2022-06-19 05:00 | 0.80821
2022-06-19 06:00 | 0.80515
2022-06-19 07:00 | 0.80921
2022-06-19 08:00 | 0.81327
2022-06-19 09:00 | 0.81833
2022-06-19 10:00 | 0.78994
2022-06-19 11:00 | 0.78589
2022-06-19 12:00 | 0.79498
2022-06-19 13:00 | 0.77979
2022-06-19 14:00 | 0.76164
2022-06-19 15:00 | 0.77276
2022-06-19 16:00 | 0.78894
2022-06-19 17:00 | 0.78788
2022-06-19 18:00 | 0.8021
2022-06-19 19:00 | 0.79193
2022-06-19 20:00 | 0.79093
2022-06-19 21:00 | 0.79299
2022-06-19 22:00 | 0.7778
2022-06-19 23:00 | 0.78489
2022-06-20 | 0.79299
2022-06-20 01:00 | 0.79904
2022-06-20 02:00 | 0.78688
2022-06-20 03:00 | 0.80309
2022-06-20 04:00 | 0.81227
2022-06-20 05:00 | 0.8234
2022-06-20 06:00 | 0.86013
2022-06-20 07:00 | 0.81634
2022-06-20 08:00 | 0.80515
2022-06-20 09:00 | 0.80515
2022-06-20 10:00 | 0.78788
2022-06-20 11:00 | 0.79904
2022-06-20 12:00 | 0.7778
2022-06-20 13:00 | 0.76567
2022-06-20 14:00 | 0.79093
2022-06-20 15:00 | 0.78085
2022-06-20 16:00 | 0.79193
2022-06-20 17:00 | 0.80821
2022-06-20 18:00 | 0.79193
2022-06-20 19:00 | 0.8021
2022-06-20 20:00 | 0.81933
2022-06-20 21:00 | 0.80715
2022-06-20 22:00 | 0.80921
2022-06-20 23:00 | 0.79598
2022-06-21 | 0.80715
2022-06-21 01:00 | 0.80615
2022-06-21 02:00 | 0.80921
2022-06-21 03:00 | 0.80821
2022-06-21 04:00 | 0.82953
2022-06-21 05:00 | 1.1932
2022-06-21 06:00 | 4.0959
2022-06-21 07:00 | 4.0959
2022-06-21 08:00 | 4.0959
2022-06-21 09:00 | 4.0959
2022-06-21 10:00 | 4.0959
2022-06-21 11:00 | 4.0959
2022-06-21 12:00 | 4.0959
2022-06-21 13:00 | 4.0959
2022-06-21 14:00 | 4.0959
2022-06-21 15:00 | 4.0959
2022-06-21 16:00 | 4.0959
2022-06-21 17:00 | 0.82546
2022-06-21 18:00 | 0.79093
2022-06-21 19:00 | 0.83053
2022-06-21 20:00 | 0.81527
2022-06-21 21:00 | 0.8509
2022-06-21 22:00 | 0.8489
2022-06-21 23:00 | 0.8489
2022-06-22 | 0.84275
2022-06-22 01:00 | 0.8214
2022-06-22 02:00 | 0.83053
2022-06-22 03:00 | 0.82646
2022-06-22 04:00 | 0.84482
2022-06-22 05:00 | 0.85705
2022-06-22 06:00 | 4.0959
2022-06-22 07:00 | 4.0959
2022-06-22 08:00 | 4.0959
2022-06-22 09:00 | 4.0959
2022-06-22 10:00 | 4.0959
2022-06-22 11:00 | 4.0959
2022-06-22 12:00 | 4.0959
2022-06-22 13:00 | 4.0959
2022-06-22 14:00 | 4.0959
2022-06-22 15:00 | 4.0959
2022-06-22 16:00 | 4.0959
2022-06-22 17:00 | 2.8629
2022-06-22 18:00 | 2.3838
2022-06-22 19:00 | 2.3852
2022-06-22 20:00 | 2.3838
2022-06-22 21:00 | 2.3875
2022-06-22 22:00 | 2.3828
2022-06-22 23:00 | 2.3799
2022-06-23 | 2.3809
2022-06-23 01:00 | 2.3857
2022-06-23 02:00 | 2.3838
2022-06-23 03:00 | 2.3772
2022-06-23 04:00 | 2.3779
2022-06-23 05:00 | 2.3875
2022-06-23 06:00 | 4.0959
2022-06-23 07:00 | 4.0959
2022-06-23 08:00 | 4.0959
2022-06-23 09:00 | 4.0959
2022-06-23 10:00 | 4.0959
2022-06-23 11:00 | 4.0959
2022-06-23 12:00 | 4.0959
2022-06-23 13:00 | 4.0959
2022-06-23 14:00 | 4.0959
2022-06-23 15:00 | 4.0959
2022-06-23 16:00 | 4.0959
2022-06-23 17:00 | 2.6201
2022-06-23 18:00 | 0.85705
2022-06-23 19:00 | 0.90205
2022-06-23 20:00 | 0.86321
2022-06-23 21:00 | 0.88674
2022-06-23 22:00 | 0.87138
2022-06-23 23:00 | 0.86013
2022-06-24 | 0.85297
2022-06-24 01:00 | 0.84582
2022-06-24 02:00 | 0.83567
2022-06-24 03:00 | 0.83767
2022-06-24 04:00 | 0.85297
2022-06-24 05:00 | 0.86623
2022-06-24 06:00 | 4.0959
2022-06-24 07:00 | 4.0959
2022-06-24 08:00 | 4.0959
2022-06-24 09:00 | 4.0959
2022-06-24 10:00 | 4.0959
2022-06-24 11:00 | 4.0959
2022-06-24 12:00 | 4.0959
2022-06-24 13:00 | 4.0959
2022-06-24 14:00 | 4.0959
2022-06-24 15:00 | 4.0959
2022-06-24 16:00 | 4.0959
2022-06-24 17:00 | 3.2744
2022-06-24 18:00 | 1.9998
2022-06-24 19:00 | 1.9895
2022-06-24 20:00 | 1.9742
2022-06-24 21:00 | 1.9798
2022-06-24 22:00 | 2.0059
2022-06-24 23:00 | 1.9812
2022-06-25 | 1.9621
2022-06-25 01:00 | 1.931
2022-06-25 02:00 | 1.9521
2022-06-25 03:00 | 1.9543
2022-06-25 04:00 | 1.9463
2022-06-25 05:00 | 1.9657
2022-06-25 06:00 | 1.9621
2022-06-25 07:00 | 1.9564
2022-06-25 08:00 | 1.9607
2022-06-25 09:00 | 1.9528
2022-06-25 10:00 | 1.9636
2022-06-25 11:00 | 1.972
2022-06-25 12:00 | 1.97
2022-06-25 13:00 | 1.9763
2022-06-25 14:00 | 1.972
2022-06-25 15:00 | 1.9784
2022-06-25 16:00 | 1.9944
2022-06-25 17:00 | 1.9798
2022-06-25 18:00 | 1.9763
2022-06-25 19:00 | 1.9685
2022-06-25 20:00 | 1.9749
2022-06-25 21:00 | 1.9902
2022-06-25 22:00 | 1.9643
2022-06-25 23:00 | 1.9514
2022-06-26 | 1.9664
2022-06-26 01:00 | 1.9685
2022-06-26 02:00 | 1.9543
2022-06-26 03:00 | 1.9514
2022-06-26 04:00 | 1.9678
2022-06-26 05:00 | 1.9735
2022-06-26 06:00 | 1.955
2022-06-26 07:00 | 1.9853
2022-06-26 08:00 | 1.96
2022-06-26 09:00 | 1.9636
2022-06-26 10:00 | 1.9405
2022-06-26 11:00 | 1.9657
2022-06-26 12:00 | 1.9571
2022-06-26 13:00 | 1.9628
2022-06-26 14:00 | 1.9628
2022-06-26 15:00 | 1.9621
2022-06-26 16:00 | 1.97
2022-06-26 17:00 | 1.9847
2022-06-26 18:00 | 1.9791
2022-06-26 19:00 | 1.9881
2022-06-26 20:00 | 1.9735
2022-06-26 21:00 | 1.9777
2022-06-26 22:00 | 1.9664
2022-06-26 23:00 | 1.9346
2022-06-27 | 1.9685
2022-06-27 01:00 | 1.9614
2022-06-27 02:00 | 1.9536
2022-06-27 03:00 | 1.955
2022-06-27 04:00 | 1.9507
2022-06-27 05:00 | 1.9685
2022-06-27 06:00 | 4.0959
2022-06-27 07:00 | 4.0959
2022-06-27 08:00 | 4.0959
2022-06-27 09:00 | 4.0959
2022-06-27 10:00 | 4.0959
2022-06-27 11:00 | 4.0959
2022-06-27 12:00 | 4.0959
2022-06-27 13:00 | 4.0959
2022-06-27 14:00 | 4.0959
2022-06-27 15:00 | 4.0959
2022-06-27 16:00 | 4.0959
2022-06-27 17:00 | 4.0959
2022-06-27 18:00 | 1.9826
2022-06-27 19:00 | 2.0039
2022-06-27 20:00 | 2.0025
2022-06-27 21:00 | 1.9861
2022-06-27 22:00 | 1.9888
2022-06-27 23:00 | 1.9354
2022-06-28 | 1.9847
2022-06-28 01:00 | 1.9784
2022-06-28 02:00 | 1.9463
2022-06-28 03:00 | 1.9664
2022-06-28 04:00 | 1.9735
2022-06-28 05:00 | 2.4605
2022-06-28 06:00 | 4.0959
2022-06-28 07:00 | 4.0959
2022-06-28 08:00 | 4.0959
2022-06-28 09:00 | 4.0959
2022-06-28 10:00 | 4.0959
2022-06-28 11:00 | 4.0959
2022-06-28 12:00 | 4.0959
2022-06-28 13:00 | 4.0959
2022-06-28 14:00 | 4.0959
2022-06-28 15:00 | 4.0959
2022-06-28 16:00 | 4.0959
2022-06-28 17:00 | 4.0959
2022-06-28 18:00 | 1.972
2022-06-28 19:00 | 2.0093
2022-06-28 20:00 | 1.9678
2022-06-28 21:00 | 1.9777
2022-06-28 22:00 | 1.9621
2022-06-28 23:00 | 1.9657
2022-06-29 | 1.97
2022-06-29 01:00 | 1.9456
2022-06-29 02:00 | 1.939
2022-06-29 03:00 | 1.9449
2022-06-29 04:00 | 1.9492
2022-06-29 05:00 | 1.9735
2022-06-29 06:00 | 4.0959
2022-06-29 07:00 | 4.0959
2022-06-29 08:00 | 4.0959
2022-06-29 09:00 | 4.0959
2022-06-29 10:00 | 4.0959
2022-06-29 11:00 | 4.0959
2022-06-29 12:00 | 4.0959
2022-06-29 13:00 | 4.0959
2022-06-29 14:00 | 4.0959
2022-06-29 15:00 | 4.0959
2022-06-29 16:00 | 4.0959
2022-06-29 17:00 | 4.0959
2022-06-29 18:00 | 1.1168
2022-06-29 19:00 | 1.1416
2022-06-29 20:00 | 1.1168
2022-06-29 21:00 | 1.1044
2022-06-29 22:00 | 1.0785
2022-06-29 23:00 | 1.093
2022-06-30 | 1.0858
2022-06-30 01:00 | 1.0774
2022-06-30 02:00 | 1.062
2022-06-30 03:00 | 1.1002
2022-06-30 04:00 | 1.1065
2022-06-30 05:00 | 1.125
2022-06-30 06:00 | 4.0959
2022-06-30 07:00 | 4.0959
2022-06-30 08:00 | 4.0959
2022-06-30 09:00 | 4.0959
2022-06-30 10:00 | 4.0959
2022-06-30 11:00 | 4.0959
2022-06-30 12:00 | 4.0959
2022-06-30 13:00 | 4.0959
2022-06-30 14:00 | 4.0959
2022-06-30 15:00 | 4.0959
2022-06-30 16:00 | 4.0959
2022-06-30 17:00 | 1.9992
2022-06-30 18:00 | 1.993
2022-06-30 19:00 | 2.0005
2022-06-30 20:00 | 2.0039
2022-06-30 21:00 | 1.993
2022-06-30 22:00 | 1.9944
2022-06-30 23:00 | 1.9671
2022-07-01 | 1.9628
2022-07-01 01:00 | 1.9671
2022-07-01 02:00 | 1.9692
2022-07-01 03:00 | 1.9685
2022-07-01 04:00 | 1.9742
2022-07-01 05:00 | 2.4688
2022-07-01 06:00 | 4.0959
2022-07-01 07:00 | 4.0959
2022-07-01 08:00 | 4.0959
2022-07-01 09:00 | 4.0959
2022-07-01 10:00 | 4.0959
2022-07-01 11:00 | 4.0959
2022-07-01 12:00 | 4.0959
2022-07-01 13:00 | 4.0959
2022-07-01 14:00 | 4.0959
2022-07-01 15:00 | 4.0959
2022-07-01 16:00 | 4.0959
2022-07-01 17:00 | 3.6319
2022-07-01 18:00 | 2.0012
2022-07-01 19:00 | 1.9902
2022-07-01 20:00 | 1.9735
2022-07-01 21:00 | 1.9853
2022-07-01 22:00 | 1.9777
2022-07-01 23:00 | 1.9628
2022-07-02 | 1.965
2022-07-02 01:00 | 1.9614
2022-07-02 02:00 | 1.9557
2022-07-02 03:00 | 1.9427
2022-07-02 04:00 | 1.9742
2022-07-02 05:00 | 1.9692
2022-07-02 06:00 | 1.9514
2022-07-02 07:00 | 1.9463
2022-07-02 08:00 | 1.9777
2022-07-02 09:00 | 1.9874
2022-07-02 10:00 | 1.9874
2022-07-02 11:00 | 1.9749
2022-07-02 12:00 | 1.9714
2022-07-02 13:00 | 1.984
2022-07-02 14:00 | 1.9847
2022-07-02 15:00 | 1.9692
2022-07-02 16:00 | 1.9636
2022-07-02 17:00 | 1.9543
2022-07-02 18:00 | 1.965
2022-07-02 19:00 | 1.9853
2022-07-02 20:00 | 1.993
2022-07-02 21:00 | 1.9791
2022-07-02 22:00 | 1.9692
2022-07-02 23:00 | 1.955
2022-07-03 | 1.9339
2022-07-03 01:00 | 1.9324
2022-07-03 02:00 | 1.9405
2022-07-03 03:00 | 1.9456
2022-07-03 04:00 | 1.9412
2022-07-03 05:00 | 1.9398
2022-07-03 06:00 | 1.9302
2022-07-03 07:00 | 1.9536
2022-07-03 08:00 | 1.9434
2022-07-03 09:00 | 1.9492
2022-07-03 10:00 | 1.9346
2022-07-03 11:00 | 1.9434
2022-07-03 12:00 | 1.955
2022-07-03 13:00 | 1.9557
2022-07-03 14:00 | 1.9383
2022-07-03 15:00 | 1.9339
2022-07-03 16:00 | 1.9514
2022-07-03 17:00 | 1.9543
2022-07-03 18:00 | 1.9521
2022-07-03 19:00 | 1.965
2022-07-03 20:00 | 1.947
2022-07-03 21:00 | 1.9593
2022-07-03 22:00 | 1.9427
2022-07-03 23:00 | 1.942
2022-07-04 | 1.9463
2022-07-04 01:00 | 1.942
2022-07-04 02:00 | 1.9272
2022-07-04 03:00 | 1.9456
2022-07-04 04:00 | 1.9536
2022-07-04 05:00 | 1.9485
2022-07-04 06:00 | 1.9564
2022-07-04 07:00 | 1.9728
2022-07-04 08:00 | 1.9557
2022-07-04 09:00 | 1.9657
2022-07-04 10:00 | 1.9578
2022-07-04 11:00 | 1.9636
2022-07-04 12:00 | 1.96
2022-07-04 13:00 | 1.9657
2022-07-04 14:00 | 1.96
2022-07-04 15:00 | 1.9564
2022-07-04 16:00 | 1.9692
2022-07-04 17:00 | 1.9671
2022-07-04 18:00 | 1.9607
2022-07-04 19:00 | 1.97
2022-07-04 20:00 | 1.9607
2022-07-04 21:00 | 1.96
2022-07-04 22:00 | 1.9492
2022-07-04 23:00 | 1.9763
2022-07-05 | 1.9819
2022-07-05 01:00 | 1.9742
2022-07-05 02:00 | 1.9564
2022-07-05 03:00 | 1.9478
2022-07-05 04:00 | 1.9528
2022-07-05 05:00 | 1.977
2022-07-05 06:00 | 4.0959
2022-07-05 07:00 | 4.0959
2022-07-05 08:00 | 4.0959
2022-07-05 09:00 | 4.0959
2022-07-05 10:00 | 4.0959
2022-07-05 11:00 | 4.0959
2022-07-05 12:00 | 4.0959
2022-07-05 13:00 | 4.0959
2022-07-05 14:00 | 4.0959
2022-07-05 15:00 | 4.0959
2022-07-05 16:00 | 4.0959
2022-07-05 17:00 | 4.0959
2022-07-05 18:00 | 4.0959
2022-07-05 19:00 | 2.0025
2022-07-05 20:00 | 1.9868
2022-07-05 21:00 | 1.9756
2022-07-05 22:00 | 1.9763
2022-07-05 23:00 | 1.9586
2022-07-06 | 1.9499
2022-07-06 01:00 | 1.965
2022-07-06 02:00 | 1.9685
2022-07-06 03:00 | 1.9735
2022-07-06 04:00 | 1.9593
2022-07-06 05:00 | 1.9714
2022-07-06 06:00 | 4.0959
2022-07-06 07:00 | 4.0959
2022-07-06 08:00 | 4.0959
2022-07-06 09:00 | 4.0959
2022-07-06 10:00 | 4.0959
2022-07-06 11:00 | 4.0959
2022-07-06 12:00 | 4.0959
2022-07-06 13:00 | 4.0959
2022-07-06 14:00 | 4.0959
2022-07-06 15:00 | 4.0959
2022-07-06 16:00 | 4.0959
2022-07-06 17:00 | 4.0959
2022-07-06 18:00 | 1.6286
2022-07-06 19:00 | 1.6821
2022-07-06 20:00 | 1.6359
2022-07-06 21:00 | 1.6587
2022-07-06 22:00 | 1.6222
2022-07-06 23:00 | 1.6111
2022-07-07 | 1.6295
2022-07-07 01:00 | 1.6359
2022-07-07 02:00 | 1.6276
2022-07-07 03:00 | 1.6222
2022-07-07 04:00 | 1.6231
2022-07-07 05:00 | 2.3607
2022-07-07 06:00 | 4.0959
2022-07-07 07:00 | 4.0959
2022-07-07 08:00 | 4.0959
2022-07-07 09:00 | 4.0959
2022-07-07 10:00 | 4.0959
2022-07-07 11:00 | 4.0959
2022-07-07 12:00 | 4.0959
2022-07-07 13:00 | 4.0959
2022-07-07 14:00 | 4.0959
2022-07-07 15:00 | 4.0959
2022-07-07 16:00 | 4.0959
2022-07-07 17:00 | 4.0959
2022-07-07 18:00 | 1.9265
2022-07-07 19:00 | 1.965
2022-07-07 20:00 | 1.9614
2022-07-07 21:00 | 1.9564
2022-07-07 22:00 | 1.9607
2022-07-07 23:00 | 1.9564
2022-07-08 | 1.9578
2022-07-08 01:00 | 1.9514
2022-07-08 02:00 | 1.9628
2022-07-08 03:00 | 1.9735
2022-07-08 04:00 | 1.9791
2022-07-08 05:00 | 1.9749
2022-07-08 06:00 | 4.0959
2022-07-08 07:00 | 4.0959
2022-07-08 08:00 | 4.0959
2022-07-08 09:00 | 4.0959
2022-07-08 10:00 | 4.0959
2022-07-08 11:00 | 4.0959
2022-07-08 12:00 | 4.0959
2022-07-08 13:00 | 4.0959
2022-07-08 14:00 | 4.0959
2022-07-08 15:00 | 4.0959
2022-07-08 16:00 | 4.0959
2022-07-08 17:00 | 4.0959
2022-07-08 18:00 | 1.995
2022-07-08 19:00 | 1.9763
2022-07-08 20:00 | 1.931
2022-07-08 21:00 | 1.9557
2022-07-08 22:00 | 1.9557
2022-07-08 23:00 | 1.9607
2022-07-09 | 1.9543
2022-07-09 01:00 | 1.9528
2022-07-09 02:00 | 1.96
2022-07-09 03:00 | 1.9376
2022-07-09 04:00 | 1.9492
2022-07-09 05:00 | 1.9456
2022-07-09 06:00 | 1.9485
2022-07-09 07:00 | 1.9514
2022-07-09 08:00 | 1.9657
2022-07-09 09:00 | 1.9478
2022-07-09 10:00 | 1.9514
2022-07-09 11:00 | 1.96
2022-07-09 12:00 | 1.9564
2022-07-09 13:00 | 1.965
2022-07-09 14:00 | 1.9593
2022-07-09 15:00 | 1.9643
2022-07-09 16:00 | 1.955
2022-07-09 17:00 | 1.9543
2022-07-09 18:00 | 1.9258
2022-07-09 19:00 | 1.9131
2022-07-09 20:00 | 1.9161
2022-07-09 21:00 | 1.8987
2022-07-09 22:00 | 1.9116
2022-07-09 23:00 | 1.9213
2022-07-10 | 1.9093
2022-07-10 01:00 | 1.9146
2022-07-10 02:00 | 1.9272
2022-07-10 03:00 | 1.9441
2022-07-10 04:00 | 1.9528
2022-07-10 05:00 | 1.9463
2022-07-10 06:00 | 1.9514
2022-07-10 07:00 | 1.9499
2022-07-10 08:00 | 1.9332
2022-07-10 09:00 | 1.9571
2022-07-10 10:00 | 1.9354
2022-07-10 11:00 | 1.9449
2022-07-10 12:00 | 1.965
2022-07-10 13:00 | 1.9671
2022-07-10 14:00 | 1.9492
2022-07-10 15:00 | 1.947
2022-07-10 16:00 | 1.9607
2022-07-10 17:00 | 1.9578
2022-07-10 18:00 | 1.9536
2022-07-10 19:00 | 1.9324
2022-07-10 20:00 | 1.9478
2022-07-10 21:00 | 1.9543
2022-07-10 22:00 | 1.9449
2022-07-10 23:00 | 1.9427
2022-07-11 | 1.9528
2022-07-11 01:00 | 1.9427
2022-07-11 02:00 | 1.9507
2022-07-11 03:00 | 1.9714
2022-07-11 04:00 | 1.9478
2022-07-11 05:00 | 4.0959
2022-07-11 06:00 | 4.0959
2022-07-11 07:00 | 4.0959
2022-07-11 08:00 | 4.0959
2022-07-11 09:00 | 4.0959
2022-07-11 10:00 | 4.0959
2022-07-11 11:00 | 4.0959
2022-07-11 12:00 | 4.0959
2022-07-11 13:00 | 4.0959
2022-07-11 14:00 | 4.0959
2022-07-11 15:00 | 4.0959
2022-07-11 16:00 | 4.0959
2022-07-11 17:00 | 4.0959
2022-07-11 18:00 | 4.0959
2022-07-11 19:00 | 2.9328
2022-07-11 20:00 | 2.8761
2022-07-11 21:00 | 2.8414
2022-07-11 22:00 | 2.8434
2022-07-11 23:00 | 2.8229
2022-07-12 | 2.8382
2022-07-12 01:00 | 2.8918
2022-07-12 02:00 | 2.8761
2022-07-12 03:00 | 2.8911
2022-07-12 04:00 | 2.897
2022-07-12 05:00 | 2.8889
2022-07-12 06:00 | 4.0959
2022-07-12 07:00 | 4.0959
2022-07-12 08:00 | 4.0959
2022-07-12 09:00 | 4.0959
2022-07-12 10:00 | 4.0959
2022-07-12 11:00 | 4.0959
2022-07-12 12:00 | 4.0959
2022-07-12 13:00 | 4.0959
2022-07-12 14:00 | 4.0959
2022-07-12 15:00 | 4.0959
2022-07-12 16:00 | 4.0959
2022-07-12 17:00 | 4.0959
2022-07-12 18:00 | 2.4888
2022-07-12 19:00 | 2.0326
2022-07-12 20:00 | 2.0233
2022-07-12 21:00 | 2.0455
2022-07-12 22:00 | 2.039
2022-07-12 23:00 | 2.0306
2022-07-13 | 2.0306
2022-07-13 01:00 | 2.0306
2022-07-13 02:00 | 2.0233
2022-07-13 03:00 | 2.0207
2022-07-13 04:00 | 2.0326
2022-07-13 05:00 | 2.8305
2022-07-13 06:00 | 4.0959
2022-07-13 07:00 | 4.0959
2022-07-13 08:00 | 4.0959
2022-07-13 09:00 | 4.0959
2022-07-13 10:00 | 4.0959
2022-07-13 11:00 | 4.0959
2022-07-13 12:00 | 4.0959
2022-07-13 13:00 | 4.0959
2022-07-13 14:00 | 4.0959
2022-07-13 15:00 | 4.0959
2022-07-13 16:00 | 4.0959
2022-07-13 17:00 | 4.0959
2022-07-13 18:00 | 4.0959
2022-07-13 19:00 | 4.0959
2022-07-13 20:00 | 4.0959
2022-07-13 21:00 | 4.0959
2022-07-13 22:00 | 4.0959
2022-07-13 23:00 | 4.0959
2022-07-14 | 4.0959
2022-07-14 01:00 | 4.0959
2022-07-14 02:00 | 4.0959
2022-07-14 03:00 | 4.0959
2022-07-14 04:00 | 4.0959
2022-07-14 05:00 | 4.0959
2022-07-14 06:00 | 4.0959
2022-07-14 07:00 | 4.0959
2022-07-14 08:00 | 4.0959
2022-07-14 09:00 | 4.0959
2022-07-14 10:00 | 4.0959
2022-07-14 11:00 | 4.0959
2022-07-14 12:00 | 4.0959
2022-07-14 13:00 | 4.0959
2022-07-14 14:00 | 4.0959
2022-07-14 15:00 | 4.0959
2022-07-14 16:00 | 4.0959
2022-07-14 17:00 | 4.0959
2022-07-14 18:00 | 4.0959
2022-07-14 19:00 | 4.0959
2022-07-14 20:00 | 4.0959
2022-07-14 21:00 | 4.0959
2022-07-14 22:00 | 4.0959
2022-07-14 23:00 | 4.0959
2022-07-15 | 4.0959
2022-07-15 01:00 | 4.0959
2022-07-15 02:00 | 4.0959
2022-07-15 03:00 | 4.0959
2022-07-15 04:00 | 4.0959
2022-07-15 05:00 | 4.0959
2022-07-15 06:00 | 4.0959
2022-07-15 07:00 | 4.0959
2022-07-15 08:00 | 4.0959
2022-07-15 09:00 | 4.0959
2022-07-15 10:00 | 4.0959
2022-07-15 11:00 | 4.0959
2022-07-15 12:00 | 4.0959
2022-07-15 13:00 | 4.0959
2022-07-15 14:00 | 4.0959
2022-07-15 15:00 | 4.0959
2022-07-15 16:00 | 4.0959
2022-07-15 17:00 | 4.0959
2022-07-15 18:00 | 4.0959
2022-07-15 19:00 | 4.0959
2022-07-15 20:00 | 4.0959
2022-07-15 21:00 | 4.0959
2022-07-15 22:00 | 4.0959
2022-07-15 23:00 | 4.0959
2022-07-16 | 4.0959
2022-07-16 01:00 | 4.0959
2022-07-16 02:00 | 4.0959
2022-07-16 03:00 | 4.0959
2022-07-16 04:00 | 4.0959
2022-07-16 05:00 | 4.0959
2022-07-16 06:00 | 4.0959
2022-07-16 07:00 | 4.0959
2022-07-16 08:00 | 4.0959
2022-07-16 09:00 | 4.0959
2022-07-16 10:00 | 4.0959
2022-07-16 11:00 | 4.0959
2022-07-16 12:00 | 4.0959
2022-07-16 13:00 | 4.0959
2022-07-16 14:00 | 4.0959
2022-07-16 15:00 | 4.0959
2022-07-16 16:00 | 4.0959
2022-07-16 17:00 | 4.0959
2022-07-16 18:00 | 4.0959
2022-07-16 19:00 | 4.0959
2022-07-16 20:00 | 4.0959
2022-07-16 21:00 | 4.0959
2022-07-16 22:00 | 4.0959
2022-07-16 23:00 | 4.0959
2022-07-17 | 4.0959
2022-07-17 01:00 | 4.0959
2022-07-17 02:00 | 4.0959
2022-07-17 03:00 | 4.0959
2022-07-17 04:00 | 4.0959
2022-07-17 05:00 | 4.0959
2022-07-17 06:00 | 4.0959
2022-07-17 07:00 | 4.0959
2022-07-17 08:00 | 4.0959
2022-07-17 09:00 | 4.0959
2022-07-17 10:00 | 4.0959
2022-07-17 11:00 | 4.0959
2022-07-17 12:00 | 4.0959
2022-07-17 13:00 | 4.0959
2022-07-17 14:00 | 4.0959
2022-07-17 15:00 | 4.0959
2022-07-17 16:00 | 4.0959
2022-07-17 17:00 | 4.0959
2022-07-17 18:00 | 4.0959
2022-07-17 19:00 | 4.0959
2022-07-17 20:00 | 4.0959
2022-07-17 21:00 | 4.0959
2022-07-17 22:00 | 4.0959
2022-07-17 23:00 | 4.0959
2022-07-18 | 4.0959
2022-07-18 01:00 | 4.0959
2022-07-18 02:00 | 4.0959
2022-07-18 03:00 | 4.0959
2022-07-18 04:00 | 4.0959
2022-07-18 05:00 | 4.0959
2022-07-18 06:00 | 4.0959
2022-07-18 07:00 | 4.0959
2022-07-18 08:00 | 4.0959
2022-07-18 09:00 | 4.0959
2022-07-18 10:00 | 4.0959
2022-07-18 11:00 | 4.0959
2022-07-18 12:00 | 4.0959
2022-07-18 13:00 | 4.0959
2022-07-18 14:00 | 4.0959
2022-07-18 15:00 | 4.0959
2022-07-18 16:00 | 1.665
2022-07-18 17:00 | 1.6865
2022-07-18 18:00 | 1.6972
2022-07-18 19:00 | 1.6848
2022-07-18 20:00 | 1.7131
2022-07-18 21:00 | 1.7192
2022-07-18 22:00 | 1.7166
2022-07-18 23:00 | 1.7025
2022-07-19 | 1.7069
2022-07-19 01:00 | 1.7052
2022-07-19 02:00 | 1.6981
2022-07-19 03:00 | 1.7131
2022-07-19 04:00 | 1.6936
2022-07-19 05:00 | 4.0959
2022-07-19 06:00 | 4.0959
2022-07-19 07:00 | 4.0959
2022-07-19 08:00 | 4.0959
2022-07-19 09:00 | 4.0959
2022-07-19 10:00 | 4.0959
2022-07-19 11:00 | 4.0959
2022-07-19 12:00 | 4.0959
2022-07-19 13:00 | 4.0959
2022-07-19 14:00 | 4.0959
2022-07-19 15:00 | 4.0959
2022-07-19 16:00 | 4.0959
2022-07-19 17:00 | 4.0959
2022-07-19 18:00 | 4.0959
2022-07-19 19:00 | 4.0959
2022-07-19 20:00 | 4.0959
2022-07-19 21:00 | 4.0959
2022-07-19 22:00 | 4.0959
2022-07-19 23:00 | 4.0959
2022-07-20 | 4.0959
2022-07-20 01:00 | 4.0959
2022-07-20 02:00 | 4.0959
2022-07-20 03:00 | 4.0959
2022-07-20 04:00 | 4.0959
2022-07-20 05:00 | 4.0959
2022-07-20 06:00 | 4.0959
2022-07-20 07:00 | 4.0959
2022-07-20 08:00 | 4.0959
2022-07-20 09:00 | 4.0959
2022-07-20 10:00 | 4.0959
2022-07-20 11:00 | 4.0959
2022-07-20 12:00 | 4.0959
2022-07-20 13:00 | 4.0959
2022-07-20 14:00 | 2.3682
2022-07-20 15:00 | 1.9833
2022-07-20 16:00 | 1.9749
2022-07-20 17:00 | 2.0107
2022-07-20 18:00 | 2.6588
2022-07-20 19:00 | 4.0959
2022-07-20 20:00 | 4.0959
2022-07-20 21:00 | 4.0959
2022-07-20 22:00 | 4.0959
2022-07-20 23:00 | 4.0959
2022-07-21 | 4.0959
2022-07-21 01:00 | 4.0959
2022-07-21 02:00 | 4.0959
2022-07-21 03:00 | 4.0959
2022-07-21 04:00 | 4.0959
2022-07-21 05:00 | 4.0959
2022-07-21 06:00 | 4.0959
2022-07-21 07:00 | 4.0959
2022-07-21 08:00 | 4.0959
2022-07-21 09:00 | 4.0959
2022-07-21 10:00 | 4.0959
2022-07-21 11:00 | 4.0959
2022-07-21 12:00 | 4.0959
2022-07-21 13:00 | 4.0959
2022-07-21 14:00 | 1.5934
2022-07-21 15:00 | 1.5821
2022-07-21 16:00 | 1.1561
2022-07-21 17:00 | 0.11314
2022-07-21 18:00 | 0.11314
2022-07-21 19:00 | 3.6494
2022-07-21 20:00 | 4.0959
2022-07-21 21:00 | 4.0959
2022-07-21 22:00 | 4.0959
2022-07-21 23:00 | 4.0959
2022-07-22 | 4.0959
2022-07-22 01:00 | 4.0959
2022-07-22 02:00 | 4.0959
2022-07-22 03:00 | 4.0959
2022-07-22 04:00 | 4.0959
2022-07-22 05:00 | 4.0959
2022-07-22 06:00 | 4.0959
2022-07-22 07:00 | 4.0959
2022-07-22 08:00 | 4.0959
2022-07-22 09:00 | 4.0959
2022-07-22 10:00 | 4.0959
2022-07-22 11:00 | 4.0959
2022-07-22 12:00 | 4.0959
2022-07-22 13:00 | 4.0959
2022-07-22 14:00 | 4.0959
2022-07-22 15:00 | 4.0959
2022-07-22 16:00 | 4.0959
2022-07-22 17:00 | 4.0959
2022-07-22 18:00 | 4.0959
2022-07-22 19:00 | 4.0959
2022-07-22 20:00 | 4.0959
2022-07-22 21:00 | 4.0959
2022-07-22 22:00 | 4.0959
2022-07-22 23:00 | 4.0959
2022-07-23 | 4.0959
2022-07-23 01:00 | 4.0959
2022-07-23 02:00 | 4.0959
2022-07-23 03:00 | 4.0959
2022-07-23 04:00 | 4.0959
2022-07-23 05:00 | 4.0959
2022-07-23 06:00 | 4.0959
2022-07-23 07:00 | 4.0959
2022-07-23 08:00 | 4.0959
2022-07-23 09:00 | 4.0959
2022-07-23 10:00 | 4.0959
2022-07-23 11:00 | 4.0959
2022-07-23 12:00 | 4.0959
2022-07-23 13:00 | 4.0959
2022-07-23 14:00 | 4.0959
2022-07-23 15:00 | 4.0959
2022-07-23 16:00 | 4.0959
2022-07-23 17:00 | 4.0959
2022-07-23 18:00 | 4.0959
2022-07-23 19:00 | 4.0959
2022-07-23 20:00 | 4.0959
2022-07-23 21:00 | 4.0959
2022-07-23 22:00 | 4.0959
2022-07-23 23:00 | 4.0959
2022-07-24 | 4.0959
2022-07-24 01:00 | 4.0959
2022-07-24 02:00 | 4.0959
2022-07-24 03:00 | 4.0959
2022-07-24 04:00 | 4.0959
2022-07-24 05:00 | 4.0959
2022-07-24 06:00 | 4.0959
2022-07-24 07:00 | 4.0959
2022-07-24 08:00 | 4.0959
2022-07-24 09:00 | 4.0959
2022-07-24 10:00 | 4.0959
2022-07-24 11:00 | 4.0959
2022-07-24 12:00 | 4.0959
2022-07-24 13:00 | 4.0959
2022-07-24 14:00 | 4.0959
2022-07-24 15:00 | 4.0959
2022-07-24 16:00 | 4.0959
2022-07-24 17:00 | 4.0959
2022-07-24 18:00 | 4.0959
2022-07-24 19:00 | 4.0959
2022-07-24 20:00 | 4.0959
2022-07-24 21:00 | 4.0959
2022-07-24 22:00 | 4.0959
2022-07-24 23:00 | 4.0959
2022-07-25 | 4.0959
2022-07-25 01:00 | 4.0959
2022-07-25 02:00 | 4.0959
2022-07-25 03:00 | 4.0959
2022-07-25 04:00 | 4.0959
2022-07-25 05:00 | 4.0959
2022-07-25 06:00 | 4.0959
2022-07-25 07:00 | 4.0959
2022-07-25 08:00 | 4.0959
2022-07-25 09:00 | 4.0959
2022-07-25 10:00 | 4.0959
2022-07-25 11:00 | 4.0959
2022-07-25 12:00 | 4.0959
2022-07-25 13:00 | 4.0959
2022-07-25 14:00 | 4.0959
2022-07-25 15:00 | 4.0959
2022-07-25 16:00 | 4.0959
2022-07-25 17:00 | 4.0959
2022-07-25 18:00 | 4.0959
2022-07-25 19:00 | 4.0959
2022-07-25 20:00 | 4.0959
2022-07-25 21:00 | 4.0959
2022-07-25 22:00 | 4.0959
2022-07-25 23:00 | 4.0959
2022-07-26 | 4.0959
2022-07-26 01:00 | 4.0959
2022-07-26 02:00 | 4.0959
2022-07-26 03:00 | 4.0959
2022-07-26 04:00 | 4.0959
2022-07-26 05:00 | 4.0959
2022-07-26 06:00 | 4.0959
2022-07-26 07:00 | 4.0959
2022-07-26 08:00 | 4.0959
2022-07-26 09:00 | 4.0959
2022-07-26 10:00 | 4.0959
2022-07-26 11:00 | 4.0959
2022-07-26 12:00 | 4.0959
2022-07-26 13:00 | 4.0959
2022-07-26 14:00 | 4.0959
2022-07-26 15:00 | 4.0959
2022-07-26 16:00 | 4.0959
2022-07-26 17:00 | 4.0959
2022-07-26 18:00 | 4.0959
2022-07-26 19:00 | 4.0959
2022-07-26 20:00 | 4.0959
2022-07-26 21:00 | 4.0959
2022-07-26 22:00 | 4.0959
2022-07-26 23:00 | 4.0959
2022-07-27 | 4.0959
2022-07-27 01:00 | 4.0959
2022-07-27 02:00 | 4.0959
2022-07-27 03:00 | 4.0959
2022-07-27 04:00 | 4.0959
2022-07-27 05:00 | 4.0959
2022-07-27 06:00 | 4.0959
2022-07-27 07:00 | 4.0959
2022-07-27 08:00 | 4.0959
2022-07-27 09:00 | 4.0959
2022-07-27 10:00 | 4.0959
2022-07-27 11:00 | 4.0959
2022-07-27 12:00 | 4.0959
2022-07-27 13:00 | 4.0959
2022-07-27 14:00 | 4.0959
2022-07-27 15:00 | 4.0959
2022-07-27 16:00 | 4.0959
2022-07-27 17:00 | 4.0959
2022-07-27 18:00 | 4.0959
2022-07-27 19:00 | 4.0959
2022-07-27 20:00 | 4.0959
2022-07-27 21:00 | 4.0959
2022-07-27 22:00 | 4.0959
2022-07-27 23:00 | 4.0959
2022-07-28 | 4.0959
2022-07-28 01:00 | 4.0959
2022-07-28 02:00 | 4.0959
2022-07-28 03:00 | 4.0959
2022-07-28 04:00 | 4.0959
2022-07-28 05:00 | 4.0959
2022-07-28 06:00 | 4.0959
2022-07-28 07:00 | 4.0959
2022-07-28 08:00 | 4.0959
2022-07-28 09:00 | 4.0959
2022-07-28 10:00 | 4.0959
2022-07-28 11:00 | 4.0959
2022-07-28 12:00 | 4.0959
2022-07-28 13:00 | 4.0959
2022-07-28 14:00 | 4.0959
2022-07-28 15:00 | 4.0959
2022-07-28 16:00 | 4.0959
2022-07-28 17:00 | 4.0959
2022-07-28 18:00 | 4.0959
2022-07-28 19:00 | 4.0959
2022-07-28 20:00 | 4.0959
2022-07-28 21:00 | 4.0959
2022-07-28 22:00 | 4.0959
2022-07-28 23:00 | 4.0959
2022-07-29 | 4.0959
2022-07-29 01:00 | 4.0959
2022-07-29 02:00 | 4.0959
2022-07-29 03:00 | 4.0959
2022-07-29 04:00 | 4.0959
2022-07-29 05:00 | 4.0959
2022-07-29 06:00 | 4.0959
2022-07-29 07:00 | 4.0959
2022-07-29 08:00 | 4.0959
2022-07-29 09:00 | 4.0959
2022-07-29 10:00 | 4.0959
2022-07-29 11:00 | 4.0959
2022-07-29 12:00 | 4.0959
2022-07-29 13:00 | 4.0959
2022-07-29 14:00 | 4.0959
2022-07-29 15:00 | 4.0959
2022-07-29 16:00 | 4.0959
2022-07-29 17:00 | 4.0959
2022-07-29 18:00 | 4.0959
2022-07-29 19:00 | 4.0959
2022-07-29 20:00 | 4.0959
2022-07-29 21:00 | 4.0959
2022-07-29 22:00 | 4.0959
2022-07-29 23:00 | 4.0959
2022-07-30 | 4.0959
2022-07-30 01:00 | 4.0959
2022-07-30 02:00 | 4.0959
2022-07-30 03:00 | 4.0959
2022-07-30 04:00 | 4.0959
2022-07-30 05:00 | 4.0959
2022-07-30 06:00 | 4.0959
2022-07-30 07:00 | 4.0959
2022-07-30 08:00 | 4.0959
2022-07-30 09:00 | 4.0959
2022-07-30 10:00 | 4.0959
2022-07-30 11:00 | 4.0959
2022-07-30 12:00 | 4.0959
2022-07-30 13:00 | 4.0959
2022-07-30 14:00 | 4.0959
2022-07-30 15:00 | 4.0959
2022-07-30 16:00 | 4.0959
2022-07-30 17:00 | 4.0959
2022-07-30 18:00 | 4.0959
2022-07-30 19:00 | 4.0959
2022-07-30 20:00 | 4.0959
2022-07-30 21:00 | 4.0959
2022-07-30 22:00 | 4.0959
2022-07-30 23:00 | 4.0959
2022-07-31 | 4.0959
2022-07-31 01:00 | 4.0959
2022-07-31 02:00 | 4.0959
2022-07-31 03:00 | 4.0959
2022-07-31 04:00 | 4.0959
2022-07-31 05:00 | 4.0959
2022-07-31 06:00 | 4.0959
2022-07-31 07:00 | 4.0959
2022-07-31 08:00 | 4.0959
2022-07-31 09:00 | 4.0959
2022-07-31 10:00 | 4.0959
2022-07-31 11:00 | 4.0959
2022-07-31 12:00 | 4.0959
2022-07-31 13:00 | 4.0959
2022-07-31 14:00 | 4.0959
2022-07-31 15:00 | 4.0959
2022-07-31 16:00 | 4.0959
2022-07-31 17:00 | 4.0959
2022-07-31 18:00 | 4.0959
2022-07-31 19:00 | 4.0959
2022-07-31 20:00 | 4.0959
2022-07-31 21:00 | 4.0959
2022-07-31 22:00 | 4.0959
2022-07-31 23:00 | 4.0959
2022-08-01 | 4.0959
2022-08-01 01:00 | 4.0959
2022-08-01 02:00 | 4.0959
2022-08-01 03:00 | 4.0959
2022-08-01 04:00 | 4.0959
2022-08-01 05:00 | 4.0959
2022-08-01 06:00 | 4.0959
2022-08-01 07:00 | 4.0959
2022-08-01 08:00 | 4.0959
2022-08-01 09:00 | 4.0959
2022-08-01 10:00 | 4.0959
2022-08-01 11:00 | 4.0959
2022-08-01 12:00 | 4.0959
2022-08-01 13:00 | 4.0959
2022-08-01 14:00 | 4.0959
2022-08-01 15:00 | 4.0959
2022-08-01 16:00 | 4.0959
2022-08-01 17:00 | 4.0959
2022-08-01 18:00 | 4.0959
2022-08-01 19:00 | 4.0959
2022-08-01 20:00 | 4.0959
2022-08-01 21:00 | 4.0959
2022-08-01 22:00 | 4.0959
2022-08-01 23:00 | 4.0959
2022-08-02 | 4.0959
2022-08-02 01:00 | 4.0959
2022-08-02 02:00 | 4.0959
2022-08-02 03:00 | 4.0959
2022-08-02 04:00 | 4.0959
2022-08-02 05:00 | 4.0959
2022-08-02 06:00 | 4.0959
2022-08-02 07:00 | 4.0959
2022-08-02 08:00 | 4.0959
2022-08-02 09:00 | 4.0959
2022-08-02 10:00 | 4.0959
2022-08-02 11:00 | 4.0959
2022-08-02 12:00 | 4.0959
2022-08-02 13:00 | 4.0959
2022-08-02 14:00 | 4.0959
2022-08-02 15:00 | 4.0959
2022-08-02 16:00 | 4.0959
2022-08-02 17:00 | 4.0959
2022-08-02 18:00 | 4.0959
2022-08-02 19:00 | 4.0959
2022-08-02 20:00 | 4.0959
2022-08-02 21:00 | 4.0959
2022-08-02 22:00 | 4.0959
2022-08-02 23:00 | 4.0959
2022-08-03 | 4.0959
2022-08-03 01:00 | 4.0959
2022-08-03 02:00 | 4.0959
2022-08-03 03:00 | 4.0959
2022-08-03 04:00 | 4.0959
2022-08-03 05:00 | 4.0959
2022-08-03 06:00 | 4.0959
2022-08-03 07:00 | 4.0959
2022-08-03 08:00 | 4.0959
2022-08-03 09:00 | 4.0959
2022-08-03 10:00 | 4.0959
2022-08-03 11:00 | 4.0959
2022-08-03 12:00 | 4.0959
2022-08-03 13:00 | 4.0959
2022-08-03 14:00 | 4.0959
2022-08-03 15:00 | 4.0959
2022-08-03 16:00 | 4.0959
2022-08-03 17:00 | 4.0959
2022-08-03 18:00 | 4.0959
2022-08-03 19:00 | 4.0959
2022-08-03 20:00 | 4.0959
2022-08-03 21:00 | 4.0959
2022-08-03 22:00 | 4.0959
2022-08-03 23:00 | 4.0959
2022-08-04 | 4.0959
2022-08-04 01:00 | 4.0959
2022-08-04 02:00 | 4.0959
2022-08-04 03:00 | 4.0959
2022-08-04 04:00 | 4.0959
2022-08-04 05:00 | 4.0959
2022-08-04 06:00 | 4.0959
2022-08-04 07:00 | 4.0959
2022-08-04 08:00 | 4.0959
2022-08-04 09:00 | 4.0959
2022-08-04 10:00 | 4.0959
2022-08-04 11:00 | 4.0959
2022-08-04 12:00 | 4.0959
2022-08-04 13:00 | 4.0959
2022-08-04 14:00 | 4.0959
2022-08-04 15:00 | 4.0959
2022-08-04 16:00 | 4.0959
2022-08-04 17:00 | 4.0959
2022-08-04 18:00 | 4.0959
2022-08-04 19:00 | 4.0959
2022-08-04 20:00 | 4.0959
2022-08-04 21:00 | 4.0959
2022-08-04 22:00 | 4.0959
2022-08-04 23:00 | 4.0959
2022-08-05 | 4.0959
2022-08-05 01:00 | 4.0959
2022-08-05 02:00 | 4.0959
2022-08-05 03:00 | 4.0959
2022-08-05 04:00 | 4.0959
2022-08-05 05:00 | 4.0959
2022-08-05 06:00 | 4.0959
2022-08-05 07:00 | 4.0959
2022-08-05 08:00 | 4.0959
2022-08-05 09:00 | 4.0959
2022-08-05 10:00 | 4.0959
2022-08-05 11:00 | 4.0959
2022-08-05 12:00 | 4.0959
2022-08-05 13:00 | 4.0959
2022-08-05 14:00 | 2.8825
2022-08-05 15:00 | 2.8719
2022-08-05 16:00 | 2.2361
2022-08-05 17:00 | 0.11194
2022-08-05 18:00 | 0.11194
2022-08-05 19:00 | 4.0959
2022-08-05 20:00 | 4.0959
2022-08-05 21:00 | 4.0959
2022-08-05 22:00 | 4.0959
2022-08-05 23:00 | 4.0959
2022-08-06 | 4.0959
2022-08-06 01:00 | 4.0959
2022-08-06 02:00 | 4.0959
2022-08-06 03:00 | 4.0959
2022-08-06 04:00 | 4.0959
2022-08-06 05:00 | 4.0959
2022-08-06 06:00 | 4.0959
2022-08-06 07:00 | 4.0959
2022-08-06 08:00 | 4.0959
2022-08-06 09:00 | 4.0959
2022-08-06 10:00 | 4.0959
2022-08-06 11:00 | 4.0959
2022-08-06 12:00 | 4.0959
2022-08-06 13:00 | 4.0959
2022-08-06 14:00 | 4.0959
2022-08-06 15:00 | 4.0959
2022-08-06 16:00 | 4.0959
2022-08-06 17:00 | 4.0959
2022-08-06 18:00 | 4.0959
2022-08-06 19:00 | 4.0959
2022-08-06 20:00 | 4.0959
2022-08-06 21:00 | 4.0959
2022-08-06 22:00 | 4.0959
2022-08-06 23:00 | 4.0959
2022-08-07 | 4.0959
2022-08-07 01:00 | 4.0959
2022-08-07 02:00 | 4.0959
2022-08-07 03:00 | 4.0959
2022-08-07 04:00 | 4.0959
2022-08-07 05:00 | 4.0959
2022-08-07 06:00 | 4.0959
2022-08-07 07:00 | 4.0959
2022-08-07 08:00 | 4.0959
2022-08-07 09:00 | 4.0959
2022-08-07 10:00 | 4.0959
2022-08-07 11:00 | 4.0959
2022-08-07 12:00 | 4.0959
2022-08-07 13:00 | 4.0959
2022-08-07 14:00 | 4.0959
2022-08-07 15:00 | 4.0959
2022-08-07 16:00 | 4.0959
2022-08-07 17:00 | 4.0959
2022-08-07 18:00 | 4.0959
2022-08-07 19:00 | 4.0959
2022-08-07 20:00 | 4.0959
2022-08-07 21:00 | 4.0959
2022-08-07 22:00 | 4.0959
2022-08-07 23:00 | 4.0959
2022-08-08 | 4.0959
2022-08-08 01:00 | 4.0959
2022-08-08 02:00 | 4.0959
2022-08-08 03:00 | 4.0959
2022-08-08 04:00 | 4.0959
2022-08-08 05:00 | 4.0959
2022-08-08 06:00 | 4.0959
2022-08-08 07:00 | 4.0959
2022-08-08 08:00 | 4.0959
2022-08-08 09:00 | 4.0959
2022-08-08 10:00 | 4.0959
2022-08-08 11:00 | 4.0959
2022-08-08 12:00 | 4.0959
2022-08-08 13:00 | 4.0959
2022-08-08 14:00 | 2.7197
2022-08-08 15:00 | 2.7119
2022-08-08 16:00 | 2.7225
2022-08-08 17:00 | 2.7326
2022-08-08 18:00 | 2.7258
2022-08-08 19:00 | 2.7606
2022-08-08 20:00 | 2.7864
2022-08-08 21:00 | 2.7713
2022-08-08 22:00 | 2.767
2022-08-08 23:00 | 2.7538
2022-08-09 | 2.7648
2022-08-09 01:00 | 2.7654
2022-08-09 02:00 | 2.7725
2022-08-09 03:00 | 2.773
2022-08-09 04:00 | 2.7758
2022-08-09 05:00 | 4.0959
2022-08-09 06:00 | 4.0959
2022-08-09 07:00 | 4.0959
2022-08-09 08:00 | 4.0959
2022-08-09 09:00 | 4.0959
2022-08-09 10:00 | 4.0959
2022-08-09 11:00 | 4.0959
2022-08-09 12:00 | 4.0959
2022-08-09 13:00 | 4.0959
2022-08-09 14:00 | 2.6603
2022-08-09 15:00 | 2.6563
2022-08-09 16:00 | 2.7038
2022-08-09 17:00 | 2.7078
2022-08-09 18:00 | 4.0959
2022-08-09 19:00 | 4.0959
2022-08-09 20:00 | 4.0959
2022-08-09 21:00 | 4.0959
2022-08-09 22:00 | 4.0959
2022-08-09 23:00 | 4.0959
2022-08-10 | 4.0959
2022-08-10 01:00 | 4.0959
2022-08-10 02:00 | 4.0959
2022-08-10 03:00 | 4.0959
2022-08-10 04:00 | 4.0959
2022-08-10 05:00 | 4.0959
2022-08-10 06:00 | 4.0959
2022-08-10 07:00 | 4.0959
2022-08-10 08:00 | 4.0959
2022-08-10 09:00 | 4.0959
2022-08-10 10:00 | 4.0959
2022-08-10 11:00 | 4.0959
2022-08-10 12:00 | 4.0959
2022-08-10 13:00 | 4.0959
2022-08-10 14:00 | 4.0959
2022-08-10 15:00 | 4.0959
2022-08-10 16:00 | 4.0959
2022-08-10 17:00 | 4.0959
2022-08-10 18:00 | 2.8629
2022-08-10 19:00 | 2.833
2022-08-10 20:00 | 2.8356
2022-08-10 21:00 | 2.7945
2022-08-10 22:00 | 2.773
2022-08-10 23:00 | 2.7627
2022-08-11 | 2.7627
2022-08-11 01:00 | 2.7648
2022-08-11 02:00 | 2.7882
2022-08-11 03:00 | 2.7899
2022-08-11 04:00 | 2.8292
2022-08-11 05:00 | 2.8173
2022-08-11 06:00 | 4.0959
2022-08-11 07:00 | 4.0959
2022-08-11 08:00 | 4.0959
2022-08-11 09:00 | 4.0959
2022-08-11 10:00 | 4.0959
2022-08-11 11:00 | 4.0959
2022-08-11 12:00 | 4.0959
2022-08-11 13:00 | 4.0959
2022-08-11 14:00 | 4.0959
2022-08-11 15:00 | 4.0959
2022-08-11 16:00 | 4.0959
2022-08-11 17:00 | 4.0959
2022-08-11 18:00 | 4.0959
2022-08-11 19:00 | 4.0959
2022-08-11 20:00 | 4.0959
2022-08-11 21:00 | 4.0959
2022-08-11 22:00 | 4.0959
2022-08-11 23:00 | 4.0959
2022-08-12 | 4.0959
2022-08-12 01:00 | 4.0959
2022-08-12 02:00 | 4.0959
2022-08-12 03:00 | 4.0959
2022-08-12 04:00 | 4.0959
2022-08-12 05:00 | 4.0959
2022-08-12 06:00 | 4.0959
2022-08-12 07:00 | 4.0959
2022-08-12 08:00 | 4.0959
2022-08-12 09:00 | 4.0959
2022-08-12 10:00 | 4.0959
2022-08-12 11:00 | 4.0959
2022-08-12 12:00 | 4.0959
2022-08-12 13:00 | 4.0959
2022-08-12 14:00 | 4.0959
2022-08-12 15:00 | 4.0959
2022-08-12 16:00 | 4.0959
2022-08-12 17:00 | 4.0959
2022-08-12 18:00 | 2.8363
2022-08-12 19:00 | 2.8363
2022-08-12 20:00 | 2.8487
2022-08-12 21:00 | 2.8242
2022-08-12 22:00 | 2.8198
2022-08-12 23:00 | 2.8223
2022-08-13 | 2.8629
2022-08-13 01:00 | 2.8712
2022-08-13 02:00 | 2.8882
2022-08-13 03:00 | 2.8846
2022-08-13 04:00 | 2.9007
2022-08-13 05:00 | 2.8911
2022-08-13 06:00 | 2.8948
2022-08-13 07:00 | 2.9219
2022-08-13 08:00 | 2.8854
2022-08-13 09:00 | 2.8474
2022-08-13 10:00 | 2.8691
2022-08-13 11:00 | 2.8846
2022-08-13 12:00 | 2.8882
2022-08-13 13:00 | 2.8768
2022-08-13 14:00 | 2.8803
2022-08-13 15:00 | 2.8487
2022-08-13 16:00 | 2.8229
2022-08-13 17:00 | 2.8204
2022-08-13 18:00 | 2.807
2022-08-13 19:00 | 2.8229
2022-08-13 20:00 | 2.8636
2022-08-13 21:00 | 2.8575
2022-08-13 22:00 | 2.8337
2022-08-13 23:00 | 2.8317
2022-08-14 | 2.8311
2022-08-14 01:00 | 2.8248
2022-08-14 02:00 | 2.8494
2022-08-14 03:00 | 2.8649
2022-08-14 04:00 | 2.8839
2022-08-14 05:00 | 2.8726
2022-08-14 06:00 | 2.8933
2022-08-14 07:00 | 2.8868
2022-08-14 08:00 | 2.8441
2022-08-14 09:00 | 2.826
2022-08-14 10:00 | 2.8337
2022-08-14 11:00 | 2.821
2022-08-14 12:00 | 2.8022
2022-08-14 13:00 | 2.8136
2022-08-14 14:00 | 2.8016
2022-08-14 15:00 | 2.7933
2022-08-14 16:00 | 2.7876
2022-08-14 17:00 | 2.7864
2022-08-14 18:00 | 2.7785
2022-08-14 19:00 | 2.7697
2022-08-14 20:00 | 2.7922
2022-08-14 21:00 | 2.8034
2022-08-14 22:00 | 2.7819
2022-08-14 23:00 | 2.8088
2022-08-15 | 2.8369
2022-08-15 01:00 | 2.8461
2022-08-15 02:00 | 2.8376
2022-08-15 03:00 | 2.8273
2022-08-15 04:00 | 2.8832
2022-08-15 05:00 | 2.8825
2022-08-15 06:00 | 4.0959
2022-08-15 07:00 | 4.0959
2022-08-15 08:00 | 4.0959
2022-08-15 09:00 | 4.0959
2022-08-15 10:00 | 4.0959
2022-08-15 11:00 | 4.0959
2022-08-15 12:00 | 4.0959
2022-08-15 13:00 | 4.0959
2022-08-15 14:00 | 4.0959
2022-08-15 15:00 | 4.0959
2022-08-15 16:00 | 4.0959
2022-08-15 17:00 | 4.0959
2022-08-15 18:00 | 4.0959
2022-08-15 19:00 | 4.0959
2022-08-15 20:00 | 4.0959
2022-08-15 21:00 | 4.0959
2022-08-15 22:00 | 4.0959
2022-08-15 23:00 | 4.0959
2022-08-16 | 4.0959
2022-08-16 01:00 | 4.0959
2022-08-16 02:00 | 4.0959
2022-08-16 03:00 | 4.0959
2022-08-16 04:00 | 4.0959
2022-08-16 05:00 | 4.0959
2022-08-16 06:00 | 4.0959
2022-08-16 07:00 | 4.0959
2022-08-16 08:00 | 4.0959
2022-08-16 09:00 | 4.0959
2022-08-16 10:00 | 4.0959
2022-08-16 11:00 | 4.0959
2022-08-16 12:00 | 4.0959
2022-08-16 13:00 | 4.0959
2022-08-16 14:00 | 4.0959
2022-08-16 15:00 | 4.0959
2022-08-16 16:00 | 4.0959
2022-08-16 17:00 | 4.0959
2022-08-16 18:00 | 4.0959
2022-08-16 19:00 | 4.0959
2022-08-16 20:00 | 4.0959
2022-08-16 21:00 | 4.0959
2022-08-16 22:00 | 4.0959
2022-08-16 23:00 | 4.0959
2022-08-17 | 4.0959
2022-08-17 01:00 | 4.0959
2022-08-17 02:00 | 4.0959
2022-08-17 03:00 | 4.0959
2022-08-17 04:00 | 4.0959
2022-08-17 05:00 | 4.0959
2022-08-17 06:00 | 4.0959
2022-08-17 07:00 | 4.0959
2022-08-17 08:00 | 4.0959
2022-08-17 09:00 | 4.0959
2022-08-17 10:00 | 4.0959
2022-08-17 11:00 | 4.0959
2022-08-17 12:00 | 4.0959
2022-08-17 13:00 | 4.0959
2022-08-17 14:00 | 4.0959
2022-08-17 15:00 | 4.0959
2022-08-17 16:00 | 4.0959
2022-08-17 17:00 | 4.0959
2022-08-17 18:00 | 4.0959
2022-08-17 19:00 | 4.0959
2022-08-17 20:00 | 4.0959
2022-08-17 21:00 | 4.0959
2022-08-17 22:00 | 4.0959
2022-08-17 23:00 | 4.0959
2022-08-18 | 4.0959
2022-08-18 01:00 | 4.0959
2022-08-18 02:00 | 4.0959
2022-08-18 03:00 | 4.0959
2022-08-18 04:00 | 4.0959
2022-08-18 05:00 | 4.0959
2022-08-18 06:00 | 4.0959
2022-08-18 07:00 | 4.0959
2022-08-18 08:00 | 4.0959
2022-08-18 09:00 | 4.0959
2022-08-18 10:00 | 4.0959
2022-08-18 11:00 | 4.0959
2022-08-18 12:00 | 4.0959
2022-08-18 13:00 | 4.0959
2022-08-18 14:00 | 4.0959
2022-08-18 15:00 | 4.0959
2022-08-18 16:00 | 4.0959
2022-08-18 17:00 | 4.0959
2022-08-18 18:00 | 4.0959
2022-08-18 19:00 | 4.0959
2022-08-18 20:00 | 4.0959
2022-08-18 21:00 | 4.0959
2022-08-18 22:00 | 4.0959
2022-08-18 23:00 | 4.0959
2022-08-19 | 4.0959
2022-08-19 01:00 | 4.0959
2022-08-19 02:00 | 4.0959
2022-08-19 03:00 | 4.0959
2022-08-19 04:00 | 4.0959
2022-08-19 05:00 | 4.0959
2022-08-19 06:00 | 4.0959
2022-08-19 07:00 | 4.0959
2022-08-19 08:00 | 4.0959
2022-08-19 09:00 | 4.0959
2022-08-19 10:00 | 4.0959
2022-08-19 11:00 | 4.0959
2022-08-19 12:00 | 4.0959
2022-08-19 13:00 | 4.0959
2022-08-19 14:00 | 4.0959
2022-08-19 15:00 | 4.0959
2022-08-19 16:00 | 4.0959
2022-08-19 17:00 | 4.0959
2022-08-19 18:00 | 4.0959
2022-08-19 19:00 | 4.0959
2022-08-19 20:00 | 4.0959
2022-08-19 21:00 | 4.0959
2022-08-19 22:00 | 4.0959
2022-08-19 23:00 | 4.0959
2022-08-20 | 4.0959
2022-08-20 01:00 | 4.0959
2022-08-20 02:00 | 4.0959
2022-08-20 03:00 | 4.0959
2022-08-20 04:00 | 4.0959
2022-08-20 05:00 | 4.0959
2022-08-20 06:00 | 4.0959
2022-08-20 07:00 | 4.0959
2022-08-20 08:00 | 4.0959
2022-08-20 09:00 | 4.0959
2022-08-20 10:00 | 4.0959
2022-08-20 11:00 | 4.0959
2022-08-20 12:00 | 4.0959
2022-08-20 13:00 | 4.0959
2022-08-20 14:00 | 4.0959
2022-08-20 15:00 | 4.0959
2022-08-20 16:00 | 4.0959
2022-08-20 17:00 | 4.0959
2022-08-20 18:00 | 4.0959
2022-08-20 19:00 | 4.0959
2022-08-20 20:00 | 4.0959
2022-08-20 21:00 | 4.0959
2022-08-20 22:00 | 4.0959
2022-08-20 23:00 | 4.0959
2022-08-21 | 4.0959
2022-08-21 01:00 | 4.0959
2022-08-21 02:00 | 4.0959
2022-08-21 03:00 | 4.0959
2022-08-21 04:00 | 4.0959
2022-08-21 05:00 | 4.0959
2022-08-21 06:00 | 4.0959
2022-08-21 07:00 | 4.0959
2022-08-21 08:00 | 4.0959
2022-08-21 09:00 | 4.0959
2022-08-21 10:00 | 4.0959
2022-08-21 11:00 | 4.0959
2022-08-21 12:00 | 4.0959
2022-08-21 13:00 | 4.0959
2022-08-21 14:00 | 4.0959
2022-08-21 15:00 | 4.0959
2022-08-21 16:00 | 4.0959
2022-08-21 17:00 | 4.0959
2022-08-21 18:00 | 4.0959
2022-08-21 19:00 | 4.0959
2022-08-21 20:00 | 4.0959
2022-08-21 21:00 | 4.0959
2022-08-21 22:00 | 4.0959
2022-08-21 23:00 | 4.0959
2022-08-22 | 4.0959
2022-08-22 01:00 | 4.0959
2022-08-22 02:00 | 4.0959
2022-08-22 03:00 | 4.0959
2022-08-22 04:00 | 4.0959
2022-08-22 05:00 | 4.0959
2022-08-22 06:00 | 4.0959
2022-08-22 07:00 | 4.0959
2022-08-22 08:00 | 4.0959
2022-08-22 09:00 | 4.0959
2022-08-22 10:00 | 4.0959
2022-08-22 11:00 | 4.0959
2022-08-22 12:00 | 4.0959
2022-08-22 13:00 | 4.0959
2022-08-22 14:00 | 4.0959
2022-08-22 15:00 | 4.0959
2022-08-22 16:00 | 4.0959
2022-08-22 17:00 | 4.0959
2022-08-22 18:00 | 2.8204
2022-08-22 19:00 | 2.8317
2022-08-22 20:00 | 2.8064
2022-08-22 21:00 | 2.8088
2022-08-22 22:00 | 2.7847
2022-08-22 23:00 | 2.7802
2022-08-23 | 2.7974
2022-08-23 01:00 | 2.8082
2022-08-23 02:00 | 2.8267
2022-08-23 03:00 | 2.813
2022-08-23 04:00 | 2.8217
2022-08-23 05:00 | 2.8527
2022-08-23 06:00 | 4.0959
2022-08-23 07:00 | 4.0959
2022-08-23 08:00 | 4.0959
2022-08-23 09:00 | 4.0959
2022-08-23 10:00 | 4.0959
2022-08-23 11:00 | 4.0959
2022-08-23 12:00 | 4.0959
2022-08-23 13:00 | 4.0959
2022-08-23 14:00 | 4.0959
2022-08-23 15:00 | 4.0959
2022-08-23 16:00 | 4.0959
2022-08-23 17:00 | 4.0959
2022-08-23 18:00 | 4.0959
2022-08-23 19:00 | 4.0959
2022-08-23 20:00 | 4.0959
2022-08-23 21:00 | 4.0959
2022-08-23 22:00 | 4.0959
2022-08-23 23:00 | 4.0959
2022-08-24 | 4.0959
2022-08-24 01:00 | 4.0959
2022-08-24 02:00 | 4.0959
2022-08-24 03:00 | 4.0959
2022-08-24 04:00 | 4.0959
2022-08-24 05:00 | 4.0959
2022-08-24 06:00 | 4.0959
2022-08-24 07:00 | 4.0959
2022-08-24 08:00 | 4.0959
2022-08-24 09:00 | 4.0959
2022-08-24 10:00 | 4.0959
2022-08-24 11:00 | 4.0959
2022-08-24 12:00 | 4.0959
2022-08-24 13:00 | 4.0959
2022-08-24 14:00 | 2.743
2022-08-24 15:00 | 4.0959
2022-08-24 16:00 | 4.0959
2022-08-24 17:00 | 4.0959
2022-08-24 18:00 | 4.0959
2022-08-24 19:00 | 4.0959
2022-08-24 20:00 | 4.0959
2022-08-24 21:00 | 4.0959
2022-08-24 22:00 | 4.0959
2022-08-24 23:00 | 4.0959
2022-08-25 | 4.0959
2022-08-25 01:00 | 4.0959
2022-08-25 02:00 | 4.0959
2022-08-25 03:00 | 4.0959
2022-08-25 04:00 | 4.0959
2022-08-25 05:00 | 4.0959
2022-08-25 06:00 | 4.0959
2022-08-25 07:00 | 4.0959
2022-08-25 08:00 | 4.0959
2022-08-25 09:00 | 4.0959
2022-08-25 10:00 | 4.0959
2022-08-25 11:00 | 4.0959
2022-08-25 12:00 | 4.0959
2022-08-25 13:00 | 4.0959
2022-08-25 14:00 | 4.0959
2022-08-25 15:00 | 4.0959
2022-08-25 16:00 | 4.0959
2022-08-25 17:00 | 4.0959
2022-08-25 18:00 | 4.0959
2022-08-25 19:00 | 4.0959
2022-08-25 20:00 | 4.0959
2022-08-25 21:00 | 4.0959
2022-08-25 22:00 | 4.0959
2022-08-25 23:00 | 4.0959
2022-08-26 | 4.0959
2022-08-26 01:00 | 4.0959
2022-08-26 02:00 | 4.0959
2022-08-26 03:00 | 4.0959
2022-08-26 04:00 | 4.0959
2022-08-26 05:00 | 4.0959
2022-08-26 06:00 | 4.0959
2022-08-26 07:00 | 4.0959
2022-08-26 08:00 | 4.0959
2022-08-26 09:00 | 4.0959
2022-08-26 10:00 | 4.0959
2022-08-26 11:00 | 4.0959
2022-08-26 12:00 | 4.0959
2022-08-26 13:00 | 4.0959
2022-08-26 14:00 | 4.0959
2022-08-26 15:00 | 4.0959
2022-08-26 16:00 | 4.0959
2022-08-26 17:00 | 4.0959
2022-08-26 18:00 | 3.3132
2022-08-26 19:00 | 3.2819
2022-08-26 20:00 | 3.253
2022-08-26 21:00 | 3.2819
2022-08-26 22:00 | 3.2457
2022-08-26 23:00 | 3.1672
2022-08-27 | 3.253
2022-08-27 01:00 | 3.2718
2022-08-27 02:00 | 3.2311
2022-08-27 03:00 | 3.2756
2022-08-27 04:00 | 3.2445
2022-08-27 05:00 | 3.2807
2022-08-27 06:00 | 3.2668
2022-08-27 07:00 | 3.2756
2022-08-27 08:00 | 3.3358
2022-08-27 09:00 | 3.2731
2022-08-27 10:00 | 3.3211
2022-08-27 11:00 | 3.2858
2022-08-27 12:00 | 3.3027
2022-08-27 13:00 | 3.2494
2022-08-27 14:00 | 3.2469
2022-08-27 15:00 | 3.1649
2022-08-27 16:00 | 3.1864
2022-08-27 17:00 | 3.1594
2022-08-27 18:00 | 3.2155
2022-08-27 19:00 | 3.212
2022-08-27 20:00 | 3.1979
2022-08-27 21:00 | 3.2347
2022-08-27 22:00 | 3.2481
2022-08-27 23:00 | 3.1864
2022-08-28 | 3.242
2022-08-28 01:00 | 3.225
2022-08-28 02:00 | 3.2408
2022-08-28 03:00 | 3.2605
2022-08-28 04:00 | 3.2858
2022-08-28 05:00 | 3.2286
2022-08-28 06:00 | 3.3224
2022-08-28 07:00 | 3.2845
2022-08-28 08:00 | 3.3171
2022-08-28 09:00 | 3.3535
2022-08-28 10:00 | 3.3291
2022-08-28 11:00 | 3.3158
2022-08-28 12:00 | 3.2568
2022-08-28 13:00 | 3.242
2022-08-28 14:00 | 3.2323
2022-08-28 15:00 | 3.2593
2022-08-28 16:00 | 3.2794
2022-08-28 17:00 | 3.3251
2022-08-28 18:00 | 3.3052
2022-08-28 19:00 | 3.3467
2022-08-28 20:00 | 3.3358
2022-08-28 21:00 | 3.3118
2022-08-28 22:00 | 3.2693
2022-08-28 23:00 | 3.263
2022-08-29 | 3.253
2022-08-29 01:00 | 3.2845
2022-08-29 02:00 | 3.3132
2022-08-29 03:00 | 3.3145
2022-08-29 04:00 | 3.3145
2022-08-29 05:00 | 3.3674
2022-08-29 06:00 | 4.0959
2022-08-29 07:00 | 4.0959
2022-08-29 08:00 | 4.0959
2022-08-29 09:00 | 4.0959
2022-08-29 10:00 | 4.0959
2022-08-29 11:00 | 4.0959
2022-08-29 12:00 | 4.0959
2022-08-29 13:00 | 4.0959
2022-08-29 14:00 | 4.0959
2022-08-29 15:00 | 4.0959
2022-08-29 16:00 | 4.0959
2022-08-29 17:00 | 4.0959
2022-08-29 18:00 | 3.5039
2022-08-29 19:00 | 2.3574
2022-08-29 20:00 | 2.3503
2022-08-29 21:00 | 2.3679
2022-08-29 22:00 | 2.3705
2022-08-29 23:00 | 2.3557
2022-08-30 | 2.3465
2022-08-30 01:00 | 2.361
2022-08-30 02:00 | 2.3612
2022-08-30 03:00 | 2.3607
2022-08-30 04:00 | 2.3671
2022-08-30 05:00 | 4.0959
2022-08-30 06:00 | 4.0959
2022-08-30 07:00 | 4.0959
2022-08-30 08:00 | 4.0959
2022-08-30 09:00 | 4.0959
2022-08-30 10:00 | 4.0959
2022-08-30 11:00 | 4.0959
2022-08-30 12:00 | 4.0959
2022-08-30 13:00 | 4.0959
2022-08-30 14:00 | 4.0959
2022-08-30 15:00 | 4.0959
2022-08-30 16:00 | 4.0959
2022-08-30 17:00 | 4.0959
2022-08-30 18:00 | 2.7638
2022-08-30 19:00 | 2.7511
2022-08-30 20:00 | 2.7585
2022-08-30 21:00 | 2.739
2022-08-30 22:00 | 2.7405
2022-08-30 23:00 | 2.7632
2022-08-31 | 2.759
2022-08-31 01:00 | 2.7553
2022-08-31 02:00 | 2.7622
2022-08-31 03:00 | 2.801
2022-08-31 04:00 | 2.7899
2022-08-31 05:00 | 2.9399
2022-08-31 06:00 | 4.0959
2022-08-31 07:00 | 4.0959
2022-08-31 08:00 | 4.0959
2022-08-31 09:00 | 4.0959
2022-08-31 10:00 | 4.0959
2022-08-31 11:00 | 4.0959
2022-08-31 12:00 | 4.0959
2022-08-31 13:00 | 4.0959
2022-08-31 14:00 | 4.0959
2022-08-31 15:00 | 4.0959
2022-08-31 16:00 | 4.0959
2022-08-31 17:00 | 4.0959
2022-08-31 18:00 | 2.8088
2022-08-31 19:00 | 2.8016
2022-08-31 20:00 | 2.813
2022-08-31 21:00 | 2.7876
2022-08-31 22:00 | 2.8106
2022-08-31 23:00 | 2.7998
2022-09-01 | 2.8112
2022-09-01 01:00 | 2.7974
2022-09-01 02:00 | 2.8167
2022-09-01 03:00 | 2.8161
2022-09-01 04:00 | 2.828
2022-09-01 05:00 | 4.0959
2022-09-01 06:00 | 4.0959
2022-09-01 07:00 | 4.0959
2022-09-01 08:00 | 4.0959
2022-09-01 09:00 | 4.0959
2022-09-01 10:00 | 4.0959
2022-09-01 11:00 | 4.0959
2022-09-01 12:00 | 4.0959
2022-09-01 13:00 | 4.0959
2022-09-01 14:00 | 4.0959
2022-09-01 15:00 | 4.0959
2022-09-01 16:00 | 4.0959
2022-09-01 17:00 | 4.0959
2022-09-01 18:00 | 2.8441
2022-09-01 19:00 | 2.8356
2022-09-01 20:00 | 2.8286
2022-09-01 21:00 | 2.804
2022-09-01 22:00 | 2.8161
2022-09-01 23:00 | 2.8649
2022-09-02 | 2.8747
2022-09-02 01:00 | 2.8548
2022-09-02 02:00 | 2.8719
2022-09-02 03:00 | 2.8768
2022-09-02 04:00 | 2.9022
2022-09-02 05:00 | 4.0959
2022-09-02 06:00 | 4.0959
2022-09-02 07:00 | 4.0959
2022-09-02 08:00 | 4.0959
2022-09-02 09:00 | 4.0959
2022-09-02 10:00 | 4.0959
2022-09-02 11:00 | 4.0959
2022-09-02 12:00 | 4.0959
2022-09-02 13:00 | 4.0959
2022-09-02 14:00 | 4.0959
2022-09-02 15:00 | 4.0959
2022-09-02 16:00 | 4.0959
2022-09-02 17:00 | 4.0959
2022-09-02 18:00 | 2.8926
2022-09-02 19:00 | 2.8782
2022-09-02 20:00 | 2.8595
2022-09-02 21:00 | 2.8311
2022-09-02 22:00 | 2.8223
2022-09-02 23:00 | 2.8148
2022-09-03 | 2.8075
2022-09-03 01:00 | 2.8317
2022-09-03 02:00 | 2.8575
2022-09-03 03:00 | 2.8507
2022-09-03 04:00 | 2.8514
2022-09-03 05:00 | 2.8691
2022-09-03 06:00 | 2.9059
2022-09-03 07:00 | 2.8868
2022-09-03 08:00 | 2.8963
2022-09-03 09:00 | 2.8434
2022-09-03 10:00 | 2.8223
2022-09-03 11:00 | 2.8434
2022-09-03 12:00 | 2.8192
2022-09-03 13:00 | 2.8311
2022-09-03 14:00 | 2.8223
2022-09-03 15:00 | 2.828
2022-09-03 16:00 | 2.821
2022-09-03 17:00 | 2.8155
2022-09-03 18:00 | 2.8273
2022-09-03 19:00 | 2.8507
2022-09-03 20:00 | 2.8388
2022-09-03 21:00 | 2.8223
2022-09-03 22:00 | 2.8217
2022-09-03 23:00 | 2.807
2022-09-04 | 2.8155
2022-09-04 01:00 | 2.8148
2022-09-04 02:00 | 2.8428
2022-09-04 03:00 | 2.8395
2022-09-04 04:00 | 2.8487
2022-09-04 05:00 | 2.8082
2022-09-04 06:00 | 2.8317
2022-09-04 07:00 | 2.8254
2022-09-04 08:00 | 2.8167
2022-09-04 09:00 | 2.8428
2022-09-04 10:00 | 2.8192
2022-09-04 11:00 | 2.7876
2022-09-04 12:00 | 2.7916
2022-09-04 13:00 | 2.7747
2022-09-04 14:00 | 2.7945
2022-09-04 15:00 | 2.7708
2022-09-04 16:00 | 2.7697
2022-09-04 17:00 | 2.7527
2022-09-04 18:00 | 2.7713
2022-09-04 19:00 | 2.7543
2022-09-04 20:00 | 2.7336
2022-09-04 21:00 | 2.7486
2022-09-04 22:00 | 2.736
2022-09-04 23:00 | 2.7455
2022-09-05 | 2.7847
2022-09-05 01:00 | 2.7606
2022-09-05 02:00 | 2.7564
2022-09-05 03:00 | 2.7543
2022-09-05 04:00 | 2.7638
2022-09-05 05:00 | 2.7697
2022-09-05 06:00 | 2.773
2022-09-05 07:00 | 2.7825
2022-09-05 08:00 | 3.1429
2022-09-05 09:00 | 4.0959
2022-09-05 10:00 | 4.0959
2022-09-05 11:00 | 4.0959
2022-09-05 12:00 | 4.0959
2022-09-05 13:00 | 4.0959
2022-09-05 14:00 | 4.0959
2022-09-05 15:00 | 4.0959
2022-09-05 16:00 | 4.0959
2022-09-05 17:00 | 4.0959
2022-09-05 18:00 | 4.0959
2022-09-05 19:00 | 4.0959
2022-09-05 20:00 | 4.0959
2022-09-05 21:00 | 4.0959
2022-09-05 22:00 | 4.0959
2022-09-05 23:00 | 4.0959
2022-09-06 | 4.0959
2022-09-06 01:00 | 4.0959
2022-09-06 02:00 | 4.0959
2022-09-06 03:00 | 4.0959
2022-09-06 04:00 | 4.0959
2022-09-06 05:00 | 4.0959
2022-09-06 06:00 | 4.0959
2022-09-06 07:00 | 4.0959
2022-09-06 08:00 | 4.0959
2022-09-06 09:00 | 4.0959
2022-09-06 10:00 | 4.0959
2022-09-06 11:00 | 4.0959
2022-09-06 12:00 | 4.0959
2022-09-06 13:00 | 4.0959
2022-09-06 14:00 | 4.0959
2022-09-06 15:00 | 4.0959
2022-09-06 16:00 | 4.0959
2022-09-06 17:00 | 4.0959
2022-09-06 18:00 | 4.0959
2022-09-06 19:00 | 4.0959
2022-09-06 20:00 | 4.0959
2022-09-06 21:00 | 2.8058
2022-09-06 22:00 | 2.8223
2022-09-06 23:00 | 2.7802
2022-09-07 | 2.7951
2022-09-07 01:00 | 2.7893
2022-09-07 02:00 | 2.8198
2022-09-07 03:00 | 2.8142
2022-09-07 04:00 | 2.8204
2022-09-07 05:00 | 4.0959
2022-09-07 06:00 | 4.0959
2022-09-07 07:00 | 4.0959
2022-09-07 08:00 | 4.0959
2022-09-07 09:00 | 4.0959
2022-09-07 10:00 | 4.0959
2022-09-07 11:00 | 4.0959
2022-09-07 12:00 | 4.0959
2022-09-07 13:00 | 4.0959
2022-09-07 14:00 | 4.0959
2022-09-07 15:00 | 4.0959
2022-09-07 16:00 | 4.0959
2022-09-07 17:00 | 4.0959
2022-09-07 18:00 | 2.7992
2022-09-07 19:00 | 2.8192
2022-09-07 20:00 | 2.8051
2022-09-07 21:00 | 2.7905
2022-09-07 22:00 | 2.7899
2022-09-07 23:00 | 2.7847
2022-09-08 | 2.8004
2022-09-08 01:00 | 2.7853
2022-09-08 02:00 | 2.8022
2022-09-08 03:00 | 2.8356
2022-09-08 04:00 | 2.8192
2022-09-08 05:00 | 4.0959
2022-09-08 06:00 | 4.0959
2022-09-08 07:00 | 4.0959
2022-09-08 08:00 | 4.0959
2022-09-08 09:00 | 4.0959
2022-09-08 10:00 | 4.0959
2022-09-08 11:00 | 4.0959
2022-09-08 12:00 | 4.0959
2022-09-08 13:00 | 4.0959
2022-09-08 14:00 | 4.0959
2022-09-08 15:00 | 4.0959
2022-09-08 16:00 | 4.0959
2022-09-08 17:00 | 4.0959
2022-09-08 18:00 | 2.798
2022-09-08 19:00 | 2.8382
2022-09-08 20:00 | 2.813
2022-09-08 21:00 | 2.8155
2022-09-08 22:00 | 2.8016
2022-09-08 23:00 | 2.791
2022-09-09 | 2.807
2022-09-09 01:00 | 2.8474
2022-09-09 02:00 | 2.8242
2022-09-09 03:00 | 2.8369
2022-09-09 04:00 | 2.8421
2022-09-09 05:00 | 4.0959
2022-09-09 06:00 | 4.0959
2022-09-09 07:00 | 4.0959
2022-09-09 08:00 | 4.0959
2022-09-09 09:00 | 4.0959
2022-09-09 10:00 | 4.0959
2022-09-09 11:00 | 4.0959
2022-09-09 12:00 | 4.0959
2022-09-09 13:00 | 4.0959
2022-09-09 14:00 | 4.0959
2022-09-09 15:00 | 4.0959
2022-09-09 16:00 | 4.0959
2022-09-09 17:00 | 2.8434
2022-09-09 18:00 | 2.8501
2022-09-09 19:00 | 2.8521
2022-09-09 20:00 | 2.8004
2022-09-09 21:00 | 2.81
2022-09-09 22:00 | 2.8363
2022-09-09 23:00 | 2.8028
2022-09-10 | 2.8242
2022-09-10 01:00 | 2.8712
2022-09-10 02:00 | 2.8861
2022-09-10 03:00 | 2.8768
2022-09-10 04:00 | 2.8789
2022-09-10 05:00 | 2.8684
2022-09-10 06:00 | 2.8789
2022-09-10 07:00 | 2.8977
2022-09-10 08:00 | 2.897
2022-09-10 09:00 | 2.8992
2022-09-10 10:00 | 2.8846
2022-09-10 11:00 | 2.8712
2022-09-10 12:00 | 2.8408
2022-09-10 13:00 | 2.8311
2022-09-10 14:00 | 2.8454
2022-09-10 15:00 | 2.8267
2022-09-10 16:00 | 2.8344
2022-09-10 17:00 | 2.8369
2022-09-10 18:00 | 2.8046
2022-09-10 19:00 | 2.8376
2022-09-10 20:00 | 2.8254
2022-09-10 21:00 | 2.8299
2022-09-10 22:00 | 2.826
2022-09-10 23:00 | 2.8142
2022-09-11 | 2.8142
2022-09-11 01:00 | 2.8548
2022-09-11 02:00 | 2.8733
2022-09-11 03:00 | 2.8663
2022-09-11 04:00 | 2.8698
2022-09-11 05:00 | 2.8567
2022-09-11 06:00 | 2.8698
2022-09-11 07:00 | 2.8825
2022-09-11 08:00 | 2.9112
2022-09-11 09:00 | 2.8796
2022-09-11 10:00 | 2.867
2022-09-11 11:00 | 2.8461
2022-09-11 12:00 | 2.8561
2022-09-11 13:00 | 2.8487
2022-09-11 14:00 | 2.8649
2022-09-11 15:00 | 2.8608
2022-09-11 16:00 | 2.8514
2022-09-11 17:00 | 2.8217
2022-09-11 18:00 | 2.8376
2022-09-11 19:00 | 2.8292
2022-09-11 20:00 | 2.8428
2022-09-11 21:00 | 2.8204
2022-09-11 22:00 | 2.7916
2022-09-11 23:00 | 2.8299
2022-09-12 | 2.8705
2022-09-12 01:00 | 2.8501
2022-09-12 02:00 | 2.8629
2022-09-12 03:00 | 2.8501
2022-09-12 04:00 | 2.874
2022-09-12 05:00 | 4.0959
2022-09-12 06:00 | 4.0959
2022-09-12 07:00 | 4.0959
2022-09-12 08:00 | 4.0959
2022-09-12 09:00 | 4.0959
2022-09-12 10:00 | 4.0959
2022-09-12 11:00 | 4.0959
2022-09-12 12:00 | 4.0959
2022-09-12 13:00 | 4.0959
2022-09-12 14:00 | 4.0959
2022-09-12 15:00 | 4.0959
2022-09-12 16:00 | 4.0959
2022-09-12 17:00 | 4.0959
2022-09-12 18:00 | 4.0959
2022-09-12 19:00 | 4.0959
2022-09-12 20:00 | 4.0959
2022-09-12 21:00 | 4.0959
2022-09-12 22:00 | 4.0959
2022-09-12 23:00 | 4.0959
2022-09-13 | 4.0959
2022-09-13 01:00 | 4.0959
2022-09-13 02:00 | 4.0959
2022-09-13 03:00 | 4.0959
2022-09-13 04:00 | 4.0959
2022-09-13 05:00 | 4.0959
2022-09-13 06:00 | 4.0959
2022-09-13 07:00 | 4.0959
2022-09-13 08:00 | 4.0959
2022-09-13 09:00 | 4.0959
2022-09-13 10:00 | 4.0959
2022-09-13 11:00 | 4.0959
2022-09-13 12:00 | 4.0959
2022-09-13 13:00 | 4.0959
2022-09-13 14:00 | 4.0959
2022-09-13 15:00 | 4.0959
2022-09-13 16:00 | 4.0959
2022-09-13 17:00 | 4.0959
2022-09-13 18:00 | 4.0959
2022-09-13 19:00 | 2.7435
2022-09-13 20:00 | 2.7527
2022-09-13 21:00 | 2.778
2022-09-13 22:00 | 2.7501
2022-09-13 23:00 | 2.7893
2022-09-14 | 2.801
2022-09-14 01:00 | 2.8167
2022-09-14 02:00 | 2.8142
2022-09-14 03:00 | 2.833
2022-09-14 04:00 | 2.8657
2022-09-14 05:00 | 4.0959
2022-09-14 06:00 | 4.0959
2022-09-14 07:00 | 4.0959
2022-09-14 08:00 | 4.0959
2022-09-14 09:00 | 4.0959
2022-09-14 10:00 | 4.0959
2022-09-14 11:00 | 4.0959
2022-09-14 12:00 | 4.0959
2022-09-14 13:00 | 4.0959
2022-09-14 14:00 | 4.0959
2022-09-14 15:00 | 4.0959
2022-09-14 16:00 | 4.0959
2022-09-14 17:00 | 4.0959
2022-09-14 18:00 | 4.0959
2022-09-14 19:00 | 4.0959
2022-09-14 20:00 | 4.0959
2022-09-14 21:00 | 4.0959
2022-09-14 22:00 | 4.0959
2022-09-14 23:00 | 4.0959
2022-09-15 | 4.0959
2022-09-15 01:00 | 4.0959
2022-09-15 02:00 | 4.0959
2022-09-15 03:00 | 4.0959
2022-09-15 04:00 | 4.0959
2022-09-15 05:00 | 4.0959
2022-09-15 06:00 | 4.0959
2022-09-15 07:00 | 4.0959
2022-09-15 08:00 | 4.0959
2022-09-15 09:00 | 4.0959
2022-09-15 10:00 | 4.0959
2022-09-15 11:00 | 4.0959
2022-09-15 12:00 | 4.0959
2022-09-15 13:00 | 4.0959
2022-09-15 14:00 | 4.0959
2022-09-15 15:00 | 4.0959
2022-09-15 16:00 | 4.0959
2022-09-15 17:00 | 2.8534
2022-09-15 18:00 | 2.8548
2022-09-15 19:00 | 2.8803
2022-09-15 20:00 | 2.8775
2022-09-15 21:00 | 2.8818
2022-09-15 22:00 | 2.9096
2022-09-15 23:00 | 2.9407
2022-09-16 | 2.9996
2022-09-16 01:00 | 2.952
2022-09-16 02:00 | 3.0103
2022-09-16 03:00 | 3.0094
2022-09-16 04:00 | 3.013
2022-09-16 05:00 | 4.0959
2022-09-16 06:00 | 4.0959
2022-09-16 07:00 | 4.0959
2022-09-16 08:00 | 4.0959
2022-09-16 09:00 | 4.0959
2022-09-16 10:00 | 4.0959
2022-09-16 11:00 | 4.0959
2022-09-16 12:00 | 4.0959
2022-09-16 13:00 | 4.0959
2022-09-16 14:00 | 4.0959
2022-09-16 15:00 | 4.0959
2022-09-16 16:00 | 4.0959
2022-09-16 17:00 | 4.0959
2022-09-16 18:00 | 4.0959
2022-09-16 19:00 | 2.8985
2022-09-16 20:00 | 2.8818
2022-09-16 21:00 | 2.9059
2022-09-16 22:00 | 2.8803
2022-09-16 23:00 | 2.9112
2022-09-17 | 2.8933
2022-09-17 01:00 | 2.881
2022-09-17 02:00 | 2.8861
2022-09-17 03:00 | 2.8719
2022-09-17 04:00 | 2.8595
2022-09-17 05:00 | 2.9157
2022-09-17 06:00 | 2.8955
2022-09-17 07:00 | 2.8861
2022-09-17 08:00 | 2.8846
2022-09-17 09:00 | 2.881
2022-09-17 10:00 | 2.881
2022-09-17 11:00 | 2.8803
2022-09-17 12:00 | 2.8839
2022-09-17 13:00 | 2.8501
2022-09-17 14:00 | 2.8747
2022-09-17 15:00 | 2.8818
2022-09-17 16:00 | 2.8796
2022-09-17 17:00 | 2.8698
2022-09-17 18:00 | 2.8461
2022-09-17 19:00 | 2.8698
2022-09-17 20:00 | 2.854
2022-09-17 21:00 | 2.8448
2022-09-17 22:00 | 2.8305
2022-09-17 23:00 | 2.8136
2022-09-18 | 2.8242
2022-09-18 01:00 | 2.8507
2022-09-18 02:00 | 2.8441
2022-09-18 03:00 | 2.8186
2022-09-18 04:00 | 2.8825
2022-09-18 05:00 | 2.8796
2022-09-18 06:00 | 2.8608
2022-09-18 07:00 | 2.874
2022-09-18 08:00 | 2.9081
2022-09-18 09:00 | 2.8948
2022-09-18 10:00 | 2.8402
2022-09-18 11:00 | 2.8124
2022-09-18 12:00 | 2.8094
2022-09-18 13:00 | 2.8217
2022-09-18 14:00 | 2.8223
2022-09-18 15:00 | 2.7893
2022-09-18 16:00 | 2.7758
2022-09-18 17:00 | 2.7847
2022-09-18 18:00 | 2.7836
2022-09-18 19:00 | 2.798
2022-09-18 20:00 | 2.807
2022-09-18 21:00 | 2.81
2022-09-18 22:00 | 2.807
2022-09-18 23:00 | 2.7825
2022-09-19 | 2.8161
2022-09-19 01:00 | 2.7747
2022-09-19 02:00 | 2.8414
2022-09-19 03:00 | 2.804
2022-09-19 04:00 | 2.8155
2022-09-19 05:00 | 4.0959
2022-09-19 06:00 | 4.0959
2022-09-19 07:00 | 4.0959
2022-09-19 08:00 | 4.0959
2022-09-19 09:00 | 4.0959
2022-09-19 10:00 | 4.0959
2022-09-19 11:00 | 4.0959
2022-09-19 12:00 | 4.0959
2022-09-19 13:00 | 4.0959
2022-09-19 14:00 | 4.0959
2022-09-19 15:00 | 4.0959
2022-09-19 16:00 | 4.0959
2022-09-19 17:00 | 4.0959
2022-09-19 18:00 | 2.7725
2022-09-19 19:00 | 2.7643
2022-09-19 20:00 | 2.7558
2022-09-19 21:00 | 2.7769
2022-09-19 22:00 | 2.7455
2022-09-19 23:00 | 2.7606
2022-09-20 | 2.7569
2022-09-20 01:00 | 2.7558
2022-09-20 02:00 | 2.8305
2022-09-20 03:00 | 2.8148
2022-09-20 04:00 | 2.821
2022-09-20 05:00 | 4.0959
2022-09-20 06:00 | 4.0959
2022-09-20 07:00 | 4.0959
2022-09-20 08:00 | 4.0959
2022-09-20 09:00 | 4.0959
2022-09-20 10:00 | 4.0959
2022-09-20 11:00 | 4.0959
2022-09-20 12:00 | 4.0959
2022-09-20 13:00 | 4.0959
2022-09-20 14:00 | 4.0959
2022-09-20 15:00 | 4.0959
2022-09-20 16:00 | 4.0959
2022-09-20 17:00 | 4.0959
2022-09-20 18:00 | 4.0959
2022-09-20 19:00 | 4.0959
2022-09-20 20:00 | 4.0959
2022-09-20 21:00 | 4.0959
2022-09-20 22:00 | 4.0959
2022-09-20 23:00 | 4.0959
2022-09-21 | 4.0959
2022-09-21 01:00 | 4.0959
2022-09-21 02:00 | 4.0959
2022-09-21 03:00 | 4.0959
2022-09-21 04:00 | 4.0959
2022-09-21 05:00 | 4.0959
2022-09-21 06:00 | 4.0959
2022-09-21 07:00 | 4.0959
2022-09-21 08:00 | 4.0959
2022-09-21 09:00 | 4.0959
2022-09-21 10:00 | 4.0959
2022-09-21 11:00 | 4.0959
2022-09-21 12:00 | 4.0959
2022-09-21 13:00 | 4.0959
2022-09-21 14:00 | 4.0959
2022-09-21 15:00 | 4.0959
2022-09-21 16:00 | 4.0959
2022-09-21 17:00 | 4.0959
2022-09-21 18:00 | 2.7893
2022-09-21 19:00 | 2.7681
2022-09-21 20:00 | 2.7643
2022-09-21 21:00 | 2.7758
2022-09-21 22:00 | 2.7735
2022-09-21 23:00 | 2.7532
2022-09-22 | 2.7963
2022-09-22 01:00 | 2.798
2022-09-22 02:00 | 2.7836
2022-09-22 03:00 | 2.7814
2022-09-22 04:00 | 2.7692
2022-09-22 05:00 | 4.0959
2022-09-22 06:00 | 4.0959
2022-09-22 07:00 | 4.0959
2022-09-22 08:00 | 4.0959
2022-09-22 09:00 | 4.0959
2022-09-22 10:00 | 4.0959
2022-09-22 11:00 | 4.0959
2022-09-22 12:00 | 4.0959
2022-09-22 13:00 | 4.0959
2022-09-22 14:00 | 4.0959
2022-09-22 15:00 | 4.0959
2022-09-22 16:00 | 4.0959
2022-09-22 17:00 | 4.0959
2022-09-22 18:00 | 2.7616
2022-09-22 19:00 | 2.8173
2022-09-22 20:00 | 2.7945
2022-09-22 21:00 | 2.7939
2022-09-22 22:00 | 2.81
2022-09-22 23:00 | 2.8782
2022-09-23 | 2.8481
2022-09-23 01:00 | 2.8677
2022-09-23 02:00 | 2.8376
2022-09-23 03:00 | 2.8363
2022-09-23 04:00 | 2.8608
2022-09-23 05:00 | 4.0959
2022-09-23 06:00 | 4.0959
2022-09-23 07:00 | 4.0959
2022-09-23 08:00 | 4.0959
2022-09-23 09:00 | 4.0959
2022-09-23 10:00 | 4.0959
2022-09-23 11:00 | 4.0959
2022-09-23 12:00 | 4.0959
2022-09-23 13:00 | 4.0959
2022-09-23 14:00 | 4.0959
2022-09-23 15:00 | 4.0959
2022-09-23 16:00 | 4.0959
2022-09-23 17:00 | 4.0959
2022-09-23 18:00 | 4.0959
2022-09-23 19:00 | 4.0959
2022-09-23 20:00 | 4.0959
2022-09-23 21:00 | 4.0959
2022-09-23 22:00 | 4.0959
2022-09-23 23:00 | 4.0959
2022-09-24 | 4.0959
2022-09-24 01:00 | 4.0959
2022-09-24 02:00 | 4.0959
2022-09-24 03:00 | 4.0959
2022-09-24 04:00 | 4.0959
2022-09-24 05:00 | 4.0959
2022-09-24 06:00 | 4.0959
2022-09-24 07:00 | 4.0959
2022-09-24 08:00 | 4.0959
2022-09-24 09:00 | 4.0959
2022-09-24 10:00 | 4.0959
2022-09-24 11:00 | 4.0959
2022-09-24 12:00 | 4.0959
2022-09-24 13:00 | 4.0959
2022-09-24 14:00 | 4.0959
2022-09-24 15:00 | 4.0959
2022-09-24 16:00 | 4.0959
2022-09-24 17:00 | 4.0959
2022-09-24 18:00 | 4.0959
2022-09-24 19:00 | 4.0959
2022-09-24 20:00 | 4.0959
2022-09-24 21:00 | 4.0959
2022-09-24 22:00 | 4.0959
2022-09-24 23:00 | 4.0959
2022-09-25 | 4.0959
2022-09-25 01:00 | 4.0959
2022-09-25 02:00 | 4.0959
2022-09-25 03:00 | 4.0959
2022-09-25 04:00 | 4.0959
2022-09-25 05:00 | 4.0959
2022-09-25 06:00 | 4.0959
2022-09-25 07:00 | 4.0959
2022-09-25 08:00 | 4.0959
2022-09-25 09:00 | 4.0959
2022-09-25 10:00 | 4.0959
2022-09-25 11:00 | 4.0959
2022-09-25 12:00 | 4.0959
2022-09-25 13:00 | 4.0959
2022-09-25 14:00 | 4.0959
2022-09-25 15:00 | 4.0959
2022-09-25 16:00 | 4.0959
2022-09-25 17:00 | 4.0959
2022-09-25 18:00 | 4.0959
2022-09-25 19:00 | 4.0959
2022-09-25 20:00 | 4.0959
2022-09-25 21:00 | 4.0959
2022-09-25 22:00 | 4.0959
2022-09-25 23:00 | 4.0959
2022-09-26 | 4.0959
2022-09-26 01:00 | 4.0959
2022-09-26 02:00 | 4.0959
2022-09-26 03:00 | 4.0959
2022-09-26 04:00 | 4.0959
2022-09-26 05:00 | 4.0959
2022-09-26 06:00 | 4.0959
2022-09-26 07:00 | 4.0959
2022-09-26 08:00 | 4.0959
2022-09-26 09:00 | 4.0959
2022-09-26 10:00 | 4.0959
2022-09-26 11:00 | 4.0959
2022-09-26 12:00 | 4.0959
2022-09-26 13:00 | 4.0959
2022-09-26 14:00 | 4.0959
2022-09-26 15:00 | 4.0959
2022-09-26 16:00 | 4.0959
2022-09-26 17:00 | 4.0959
2022-09-26 18:00 | 4.0959
2022-09-26 19:00 | 4.0959
2022-09-26 20:00 | 4.0959
2022-09-26 21:00 | 4.0959
2022-09-26 22:00 | 4.0959
2022-09-26 23:00 | 4.0959
2022-09-27 | 4.0959
2022-09-27 01:00 | 4.0959
2022-09-27 02:00 | 4.0959
2022-09-27 03:00 | 4.0959
2022-09-27 04:00 | 4.0959
2022-09-27 05:00 | 4.0959
2022-09-27 06:00 | 4.0959
2022-09-27 07:00 | 4.0959
2022-09-27 08:00 | 4.0959
2022-09-27 09:00 | 4.0959
2022-09-27 10:00 | 4.0959
2022-09-27 11:00 | 4.0959
2022-09-27 12:00 | 4.0959
2022-09-27 13:00 | 4.0959
2022-09-27 14:00 | 4.0959
2022-09-27 15:00 | 4.0959
2022-09-27 16:00 | 4.0959
2022-09-27 17:00 | 4.0959
2022-09-27 18:00 | 2.7003
2022-09-27 19:00 | 2.8382
2022-09-27 20:00 | 2.8242
2022-09-27 21:00 | 2.8421
2022-09-27 22:00 | 2.8311
2022-09-27 23:00 | 2.8933
2022-09-28 | 2.867
2022-09-28 01:00 | 2.8854
2022-09-28 02:00 | 2.9211
2022-09-28 03:00 | 2.9226
2022-09-28 04:00 | 2.9399
2022-09-28 05:00 | 4.0959
2022-09-28 06:00 | 4.0959
2022-09-28 07:00 | 4.0959
2022-09-28 08:00 | 4.0959
2022-09-28 09:00 | 4.0959
2022-09-28 10:00 | 4.0959
2022-09-28 11:00 | 4.0959
2022-09-28 12:00 | 4.0959
2022-09-28 13:00 | 4.0959
2022-09-28 14:00 | 4.0959
2022-09-28 15:00 | 4.0959
2022-09-28 16:00 | 4.0959
2022-09-28 17:00 | 4.0959
2022-09-28 18:00 | 2.7142
2022-09-28 19:00 | 2.874
2022-09-28 20:00 | 2.833
2022-09-28 21:00 | 2.8726
2022-09-28 22:00 | 2.9172
2022-09-28 23:00 | 2.9119
2022-09-29 | 2.961
2022-09-29 01:00 | 2.9165
2022-09-29 02:00 | 2.9296
2022-09-29 03:00 | 2.9569
2022-09-29 04:00 | 2.9415
2022-09-29 05:00 | 4.0959
2022-09-29 06:00 | 4.0959
2022-09-29 07:00 | 4.0959
2022-09-29 08:00 | 4.0959
2022-09-29 09:00 | 4.0959
2022-09-29 10:00 | 4.0959
2022-09-29 11:00 | 4.0959
2022-09-29 12:00 | 4.0959
2022-09-29 13:00 | 4.0959
2022-09-29 14:00 | 4.0959
2022-09-29 15:00 | 4.0959
2022-09-29 16:00 | 4.0959
2022-09-29 17:00 | 4.0959
2022-09-29 18:00 | 2.7292
2022-09-29 19:00 | 2.8608
2022-09-29 20:00 | 2.8789
2022-09-29 21:00 | 2.8534
2022-09-29 22:00 | 2.9304
2022-09-29 23:00 | 2.9569
2022-09-30 | 2.9762
2022-09-30 01:00 | 2.9839
2022-09-30 02:00 | 2.9661
2022-09-30 03:00 | 2.9873
2022-09-30 04:00 | 3.0031
2022-09-30 05:00 | 4.0959
2022-09-30 06:00 | 4.0959
2022-09-30 07:00 | 4.0959
2022-09-30 08:00 | 4.0959
2022-09-30 09:00 | 4.0959
2022-09-30 10:00 | 4.0959
2022-09-30 11:00 | 4.0959
2022-09-30 12:00 | 4.0959
2022-09-30 13:00 | 4.0959
2022-09-30 14:00 | 4.0959
2022-09-30 15:00 | 4.0959
2022-09-30 16:00 | 4.0959
2022-09-30 17:00 | 4.0959
2022-09-30 18:00 | 2.8448
2022-09-30 19:00 | 2.8142
2022-09-30 20:00 | 2.8254
2022-09-30 21:00 | 2.8926
2022-09-30 22:00 | 2.8747
2022-09-30 23:00 | 2.881
2022-10-01 | 2.8643
2022-10-01 01:00 | 2.9203
2022-10-01 02:00 | 2.8726
2022-10-01 03:00 | 2.8999
2022-10-01 04:00 | 2.8963
2022-10-01 05:00 | 2.8977
2022-10-01 06:00 | 2.9367
2022-10-01 07:00 | 2.9203
2022-10-01 08:00 | 2.8897
2022-10-01 09:00 | 2.9074
2022-10-01 10:00 | 2.8691
2022-10-01 11:00 | 2.8356
2022-10-01 12:00 | 2.8388
2022-10-01 13:00 | 2.7957
2022-10-01 14:00 | 2.8004
2022-10-01 15:00 | 2.778
2022-10-01 16:00 | 2.7808
2022-10-01 17:00 | 2.7747
2022-10-01 18:00 | 2.7697
2022-10-01 19:00 | 2.7543
2022-10-01 20:00 | 2.7491
2022-10-01 21:00 | 2.7522
2022-10-01 22:00 | 2.7853
2022-10-01 23:00 | 2.7774
2022-10-02 | 2.8363
2022-10-02 01:00 | 2.8254
2022-10-02 02:00 | 2.8428
2022-10-02 03:00 | 2.8395
2022-10-02 04:00 | 2.8382
2022-10-02 05:00 | 2.867
2022-10-02 06:00 | 2.8911
2022-10-02 07:00 | 2.9096
2022-10-02 08:00 | 2.8875
2022-10-02 09:00 | 2.8918
2022-10-02 10:00 | 2.8775
2022-10-02 11:00 | 2.8106
2022-10-02 12:00 | 2.8034
2022-10-02 13:00 | 2.8124
2022-10-02 14:00 | 2.8112
2022-10-02 15:00 | 2.8223
2022-10-02 16:00 | 2.801
2022-10-02 17:00 | 2.8705
2022-10-02 18:00 | 2.8428
2022-10-02 19:00 | 2.9014
2022-10-02 20:00 | 2.9119
2022-10-02 21:00 | 2.8999
2022-10-02 22:00 | 2.8904
2022-10-02 23:00 | 2.9014
2022-10-03 | 2.9089
2022-10-03 01:00 | 2.8948
2022-10-03 02:00 | 2.9669
2022-10-03 03:00 | 2.9219
2022-10-03 04:00 | 2.9431
2022-10-03 05:00 | 4.0959
2022-10-03 06:00 | 4.0959
2022-10-03 07:00 | 4.0959
2022-10-03 08:00 | 4.0959
2022-10-03 09:00 | 4.0959
2022-10-03 10:00 | 4.0959
2022-10-03 11:00 | 4.0959
2022-10-03 12:00 | 4.0959
2022-10-03 13:00 | 4.0959
2022-10-03 14:00 | 4.0959
2022-10-03 15:00 | 4.0959
2022-10-03 16:00 | 4.0959
2022-10-03 17:00 | 0.72737
2022-10-03 18:00 | 0.8346
2022-10-03 19:00 | 0.82953
2022-10-03 20:00 | 0.79704
2022-10-03 21:00 | 0.8234
2022-10-03 22:00 | 0.8336
2022-10-03 23:00 | 0.82446
2022-10-04 | 0.8499
2022-10-04 01:00 | 0.8336
2022-10-04 02:00 | 0.84682
2022-10-04 03:00 | 0.85505
2022-10-04 04:00 | 0.86623
2022-10-04 05:00 | 1.5481
2022-10-04 06:00 | 4.2665
2022-10-04 07:00 | 4.2589
2022-10-04 08:00 | 4.1978
2022-10-04 09:00 | 3.9877
2022-10-04 10:00 | 3.9224
2022-10-04 11:00 | 3.8968
2022-10-04 12:00 | 3.6584
2022-10-04 13:00 | 3.6319
2022-10-04 14:00 | 3.6601
2022-10-04 15:00 | 3.6406
2022-10-04 16:00 | 3.6161
2022-10-04 17:00 | 3.6111
2022-10-04 18:00 | 2.7496
2022-10-04 19:00 | 2.7665
2022-10-04 20:00 | 2.7511
2022-10-04 21:00 | 2.7425
2022-10-04 22:00 | 2.7445
2022-10-04 23:00 | 2.7659
2022-10-05 | 2.7355
2022-10-05 01:00 | 2.743
2022-10-05 02:00 | 2.759
2022-10-05 03:00 | 2.7405
2022-10-05 04:00 | 2.7713
2022-10-05 05:00 | 4.0959
2022-10-05 06:00 | 4.0959
2022-10-05 07:00 | 4.0959
2022-10-05 08:00 | 4.0959
2022-10-05 09:00 | 4.0959
2022-10-05 10:00 | 4.0959
2022-10-05 11:00 | 4.0959
2022-10-05 12:00 | 4.0959
2022-10-05 13:00 | 4.0959
2022-10-05 14:00 | 4.0959
2022-10-05 15:00 | 4.0959
2022-10-05 16:00 | 4.0959
2022-10-05 17:00 | 4.0959
2022-10-05 18:00 | 4.0959
2022-10-05 19:00 | 4.0959
2022-10-05 20:00 | 4.0959
2022-10-05 21:00 | 4.0959
2022-10-05 22:00 | 4.0959
2022-10-05 23:00 | 4.0959
2022-10-06 | 4.0959
2022-10-06 01:00 | 4.0959
2022-10-06 02:00 | 4.0959
2022-10-06 03:00 | 4.0959
2022-10-06 04:00 | 4.0959
2022-10-06 05:00 | 4.0959
2022-10-06 06:00 | 4.0959
2022-10-06 07:00 | 4.0959
2022-10-06 08:00 | 4.0959
2022-10-06 09:00 | 4.0959
2022-10-06 10:00 | 4.0959
2022-10-06 11:00 | 4.0959
2022-10-06 12:00 | 4.0959
2022-10-06 13:00 | 4.0959
2022-10-06 14:00 | 4.0959
2022-10-06 15:00 | 4.0959
2022-10-06 16:00 | 4.0959
2022-10-06 17:00 | 4.0959
2022-10-06 18:00 | 4.0959
2022-10-06 19:00 | 4.0959
2022-10-06 20:00 | 4.0959
2022-10-06 21:00 | 4.0959
2022-10-06 22:00 | 4.0959
2022-10-06 23:00 | 4.0959
2022-10-07 | 4.0959
2022-10-07 01:00 | 4.0959
2022-10-07 02:00 | 4.0959
2022-10-07 03:00 | 4.0959
2022-10-07 04:00 | 4.0959
2022-10-07 05:00 | 4.0959
2022-10-07 06:00 | 4.0959
2022-10-07 07:00 | 4.0959
2022-10-07 08:00 | 4.0959
2022-10-07 09:00 | 4.0959
2022-10-07 10:00 | 4.0959
2022-10-07 11:00 | 4.0959
2022-10-07 12:00 | 4.0959
2022-10-07 13:00 | 4.0959
2022-10-07 14:00 | 4.0959
2022-10-07 15:00 | 4.0959
2022-10-07 16:00 | 4.0959
2022-10-07 17:00 | 4.0959
2022-10-07 18:00 | 4.0959
2022-10-07 19:00 | 2.7445
2022-10-07 20:00 | 2.7675
2022-10-07 21:00 | 2.7842
2022-10-07 22:00 | 2.7859
2022-10-07 23:00 | 2.7797
2022-10-08 | 2.7969
2022-10-08 01:00 | 2.7974
2022-10-08 02:00 | 2.8376
2022-10-08 03:00 | 2.8441
2022-10-08 04:00 | 2.8474
2022-10-08 05:00 | 2.8911
2022-10-08 06:00 | 2.8948
2022-10-08 07:00 | 2.8897
2022-10-08 08:00 | 2.9119
2022-10-08 09:00 | 2.8754
2022-10-08 10:00 | 2.8369
2022-10-08 11:00 | 2.7564
2022-10-08 12:00 | 2.7579
2022-10-08 13:00 | 2.7538
2022-10-08 14:00 | 2.7511
2022-10-08 15:00 | 2.7522
2022-10-08 16:00 | 2.7532
2022-10-08 17:00 | 2.7395
2022-10-08 18:00 | 2.7506
2022-10-08 19:00 | 2.7692
2022-10-08 20:00 | 2.7654
2022-10-08 21:00 | 2.7675
2022-10-08 22:00 | 2.744
2022-10-08 23:00 | 2.7638
2022-10-09 | 2.7758
2022-10-09 01:00 | 2.7887
2022-10-09 02:00 | 2.7974
2022-10-09 03:00 | 2.8034
2022-10-09 04:00 | 2.7963
2022-10-09 05:00 | 2.8112
2022-10-09 06:00 | 2.8167
2022-10-09 07:00 | 2.8179
2022-10-09 08:00 | 2.8305
2022-10-09 09:00 | 2.8286
2022-10-09 10:00 | 2.8192
2022-10-09 11:00 | 2.8155
2022-10-09 12:00 | 2.8064
2022-10-09 13:00 | 2.801
2022-10-09 14:00 | 2.8082
2022-10-09 15:00 | 2.7905
2022-10-09 16:00 | 2.7802
2022-10-09 17:00 | 2.7769
2022-10-09 18:00 | 2.7797
2022-10-09 19:00 | 2.7808
2022-10-09 20:00 | 2.7785
2022-10-09 21:00 | 2.759
2022-10-09 22:00 | 2.7692
2022-10-09 23:00 | 2.7808
2022-10-10 | 2.7703
2022-10-10 01:00 | 2.8016
2022-10-10 02:00 | 2.8051
2022-10-10 03:00 | 2.8022
2022-10-10 04:00 | 2.807
2022-10-10 05:00 | 2.8198
2022-10-10 06:00 | 2.8344
2022-10-10 07:00 | 2.7336
2022-10-10 08:00 | 2.7974
2022-10-10 09:00 | 2.7969
2022-10-10 10:00 | 2.7522
2022-10-10 11:00 | 2.7321
2022-10-10 12:00 | 2.7114
2022-10-10 13:00 | 2.716
2022-10-10 14:00 | 2.6934
2022-10-10 15:00 | 2.6977
2022-10-10 16:00 | 2.6977
2022-10-10 17:00 | 2.7016
2022-10-10 18:00 | 2.6888
2022-10-10 19:00 | 2.7928
2022-10-10 20:00 | 2.7785
2022-10-10 21:00 | 2.7916
2022-10-10 22:00 | 2.7969
2022-10-10 23:00 | 2.804
2022-10-11 | 2.8217
2022-10-11 01:00 | 2.8273
2022-10-11 02:00 | 2.8305
2022-10-11 03:00 | 2.8305
2022-10-11 04:00 | 2.8369
2022-10-11 05:00 | 2.854
2022-10-11 06:00 | 2.9059
2022-10-11 07:00 | 2.7579
2022-10-11 08:00 | 2.8911
2022-10-11 09:00 | 2.8286
2022-10-11 10:00 | 2.8022
2022-10-11 11:00 | 2.7703
2022-10-11 12:00 | 2.7842
2022-10-11 13:00 | 2.7725
2022-10-11 14:00 | 2.7825
2022-10-11 15:00 | 2.7719
2022-10-11 16:00 | 2.7611
2022-10-11 17:00 | 2.7713
2022-10-11 18:00 | 2.7686
2022-10-11 19:00 | 2.7853
2022-10-11 20:00 | 2.7595
2022-10-11 21:00 | 2.7569
2022-10-11 22:00 | 2.7627
2022-10-11 23:00 | 2.7622
2022-10-12 | 2.7675
2022-10-12 01:00 | 2.7893
2022-10-12 02:00 | 2.787
2022-10-12 03:00 | 2.8028
2022-10-12 04:00 | 2.8311
2022-10-12 05:00 | 2.8481
2022-10-12 06:00 | 2.8501
2022-10-12 07:00 | 2.8487
2022-10-12 08:00 | 4.0959
2022-10-12 09:00 | 4.0959
2022-10-12 10:00 | 4.0959
2022-10-12 11:00 | 4.0959
2022-10-12 12:00 | 4.0959
2022-10-12 13:00 | 4.0959
2022-10-12 14:00 | 4.0959
2022-10-12 15:00 | 4.0959
2022-10-12 16:00 | 4.0959
2022-10-12 17:00 | 2.745
2022-10-12 18:00 | 2.745
2022-10-12 19:00 | 2.7425
2022-10-12 20:00 | 2.7481
2022-10-12 21:00 | 2.7538
2022-10-12 22:00 | 2.7511
2022-10-12 23:00 | 2.743
2022-10-13 | 2.7516
2022-10-13 01:00 | 2.7616
2022-10-13 02:00 | 2.7654
2022-10-13 03:00 | 2.7627
2022-10-13 04:00 | 2.7606
2022-10-13 05:00 | 4.0959
2022-10-13 06:00 | 4.0959
2022-10-13 07:00 | 4.0959
2022-10-13 08:00 | 4.0959
2022-10-13 09:00 | 4.0959
2022-10-13 10:00 | 4.0959
2022-10-13 11:00 | 4.0959
2022-10-13 12:00 | 4.0959
2022-10-13 13:00 | 4.0959
2022-10-13 14:00 | 4.0959
2022-10-13 15:00 | 4.0959
2022-10-13 16:00 | 4.0959
2022-10-13 17:00 | 4.0959
2022-10-13 18:00 | 4.0959
2022-10-13 19:00 | 4.0959
2022-10-13 20:00 | 4.0959
2022-10-13 21:00 | 4.0959
2022-10-13 22:00 | 4.0959
2022-10-13 23:00 | 4.0959
2022-10-14 | 4.0959
2022-10-14 01:00 | 4.0959
2022-10-14 02:00 | 4.0959
2022-10-14 03:00 | 4.0959
2022-10-14 04:00 | 4.0959
2022-10-14 05:00 | 4.0959
2022-10-14 06:00 | 4.0959
2022-10-14 07:00 | 4.0959
2022-10-14 08:00 | 4.0959
2022-10-14 09:00 | 4.0959
2022-10-14 10:00 | 4.0959
2022-10-14 11:00 | 4.0959
2022-10-14 12:00 | 4.0959
2022-10-14 13:00 | 4.0959
2022-10-14 14:00 | 2.7802
2022-10-14 15:00 | 2.7752
2022-10-14 16:00 | 2.7632
2022-10-14 17:00 | 2.7887
2022-10-14 18:00 | 2.7648
2022-10-14 19:00 | 2.7249
2022-10-14 20:00 | 2.736
2022-10-14 21:00 | 2.7611
2022-10-14 22:00 | 2.7899
2022-10-14 23:00 | 2.7969
2022-10-15 | 2.7675
2022-10-15 01:00 | 2.7922
2022-10-15 02:00 | 2.8179
2022-10-15 03:00 | 2.8112
2022-10-15 04:00 | 2.8267
2022-10-15 05:00 | 2.8534
2022-10-15 06:00 | 2.8684
2022-10-15 07:00 | 2.8454
2022-10-15 08:00 | 2.8217
2022-10-15 09:00 | 2.821
2022-10-15 10:00 | 2.8186
2022-10-15 11:00 | 2.8136
2022-10-15 12:00 | 2.8034
2022-10-15 13:00 | 2.787
2022-10-15 14:00 | 2.7774
2022-10-15 15:00 | 2.7951
2022-10-15 16:00 | 2.7763
2022-10-15 17:00 | 2.7769
2022-10-15 18:00 | 2.7763
2022-10-15 19:00 | 2.7681
2022-10-15 20:00 | 2.7616
2022-10-15 21:00 | 2.7627
2022-10-15 22:00 | 2.7741
2022-10-15 23:00 | 2.7769
2022-10-16 | 2.7697
2022-10-16 01:00 | 2.7957
2022-10-16 02:00 | 2.7928
2022-10-16 03:00 | 2.8167
2022-10-16 04:00 | 2.81
2022-10-16 05:00 | 2.8235
2022-10-16 06:00 | 2.8167
2022-10-16 07:00 | 2.8324
2022-10-16 08:00 | 2.8106
2022-10-16 09:00 | 2.8286
2022-10-16 10:00 | 2.8248
2022-10-16 11:00 | 2.7758
2022-10-16 12:00 | 2.7632
2022-10-16 13:00 | 2.7532
2022-10-16 14:00 | 2.746
2022-10-16 15:00 | 2.7405
2022-10-16 16:00 | 2.7501
2022-10-16 17:00 | 2.7585
2022-10-16 18:00 | 2.7527
2022-10-16 19:00 | 2.7522
2022-10-16 20:00 | 2.7713
2022-10-16 21:00 | 2.778
2022-10-16 22:00 | 2.7564
2022-10-16 23:00 | 2.801
2022-10-17 | 2.8064
2022-10-17 01:00 | 2.7992
2022-10-17 02:00 | 2.8161
2022-10-17 03:00 | 2.8075
2022-10-17 04:00 | 2.8173
2022-10-17 05:00 | 2.8317
2022-10-17 06:00 | 2.8242
2022-10-17 07:00 | 4.0959
2022-10-17 08:00 | 4.0959
2022-10-17 09:00 | 4.0959
2022-10-17 10:00 | 4.0959
2022-10-17 11:00 | 4.0959
2022-10-17 12:00 | 4.0959
2022-10-17 13:00 | 4.0959
2022-10-17 14:00 | 4.0959
2022-10-17 15:00 | 4.0959
2022-10-17 16:00 | 4.0959
2022-10-17 17:00 | 4.0959
2022-10-17 18:00 | 3.053
2022-10-17 19:00 | 3.0617
2022-10-17 20:00 | 3.1321
2022-10-17 21:00 | 3.1278
2022-10-17 22:00 | 3.0955
2022-10-17 23:00 | 3.1407
2022-10-18 | 3.191
2022-10-18 01:00 | 3.2347
2022-10-18 02:00 | 3.2618
2022-10-18 03:00 | 3.3118
2022-10-18 04:00 | 3.3105
2022-10-18 05:00 | 4.0959
2022-10-18 06:00 | 4.0959
2022-10-18 07:00 | 4.0959
2022-10-18 08:00 | 4.0959
2022-10-18 09:00 | 4.0959
2022-10-18 10:00 | 4.0959
2022-10-18 11:00 | 4.0959
2022-10-18 12:00 | 4.0959
2022-10-18 13:00 | 4.0959
2022-10-18 14:00 | 4.0959
2022-10-18 15:00 | 4.0959
2022-10-18 16:00 | 4.0959
2022-10-18 17:00 | 4.0959
2022-10-18 18:00 | 4.0959
2022-10-18 19:00 | 4.0959
2022-10-18 20:00 | 2.7558
2022-10-18 21:00 | 2.7791
2022-10-18 22:00 | 2.7725
2022-10-18 23:00 | 2.7791
2022-10-19 | 2.8337
2022-10-19 01:00 | 2.8344
2022-10-19 02:00 | 2.8548
2022-10-19 03:00 | 2.8588
2022-10-19 04:00 | 2.8454
2022-10-19 05:00 | 2.8782
2022-10-19 06:00 | 2.9134
2022-10-19 07:00 | 2.8918
2022-10-19 08:00 | 2.8712
2022-10-19 09:00 | 2.8273
2022-10-19 10:00 | 2.81
2022-10-19 11:00 | 2.798
2022-10-19 12:00 | 2.7785
2022-10-19 13:00 | 2.773
2022-10-19 14:00 | 2.7506
2022-10-19 15:00 | 2.741
2022-10-19 16:00 | 2.7475
2022-10-19 17:00 | 2.7585
2022-10-19 18:00 | 2.7455
2022-10-19 19:00 | 2.7719
2022-10-19 20:00 | 2.6411
2022-10-19 21:00 | 2.3287
2022-10-19 22:00 | 2.3297
2022-10-19 23:00 | 2.3249
2022-10-20 | 2.3335
2022-10-20 01:00 | 2.3432
2022-10-20 02:00 | 2.3453
2022-10-20 03:00 | 2.3471
2022-10-20 04:00 | 2.3488
2022-10-20 05:00 | 2.362
2022-10-20 06:00 | 2.8698
2022-10-20 07:00 | 2.8337
2022-10-20 08:00 | 2.867
2022-10-20 09:00 | 2.8161
2022-10-20 10:00 | 2.7945
2022-10-20 11:00 | 2.7769
2022-10-20 12:00 | 2.7814
2022-10-20 13:00 | 2.7887
2022-10-20 14:00 | 2.7627
2022-10-20 15:00 | 2.7752
2022-10-20 16:00 | 2.7675
2022-10-20 17:00 | 2.7819
2022-10-20 18:00 | 2.7638
2022-10-20 19:00 | 2.7405
2022-10-20 20:00 | 2.7475
2022-10-20 21:00 | 2.759
2022-10-20 22:00 | 2.7585
2022-10-20 23:00 | 2.807
2022-10-21 | 2.7814
2022-10-21 01:00 | 2.7752
2022-10-21 02:00 | 2.7825
2022-10-21 03:00 | 2.798
2022-10-21 04:00 | 2.8028
2022-10-21 05:00 | 2.8507
2022-10-21 06:00 | 2.8629
2022-10-21 07:00 | 2.8567
2022-10-21 08:00 | 2.8344
2022-10-21 09:00 | 2.8118
2022-10-21 10:00 | 2.8046
2022-10-21 11:00 | 2.7933
2022-10-21 12:00 | 2.7916
2022-10-21 13:00 | 2.7893
2022-10-21 14:00 | 2.7675
2022-10-21 15:00 | 2.7735
2022-10-21 16:00 | 2.7758
2022-10-21 17:00 | 2.7741
2022-10-21 18:00 | 2.7675
2022-10-21 19:00 | 2.7606
2022-10-21 20:00 | 2.7564
2022-10-21 21:00 | 2.7842
2022-10-21 22:00 | 2.7713
2022-10-21 23:00 | 2.773
2022-10-22 | 2.7882
2022-10-22 01:00 | 2.8204
2022-10-22 02:00 | 2.8376
2022-10-22 03:00 | 2.8051
2022-10-22 04:00 | 2.8192
2022-10-22 05:00 | 2.8186
2022-10-22 06:00 | 2.8567
2022-10-22 07:00 | 2.8448
2022-10-22 08:00 | 2.8754
2022-10-22 09:00 | 2.8554
2022-10-22 10:00 | 2.8588
2022-10-22 11:00 | 2.8254
2022-10-22 12:00 | 2.7899
2022-10-22 13:00 | 2.7916
2022-10-22 14:00 | 2.804
2022-10-22 15:00 | 2.81
2022-10-22 16:00 | 2.8112
2022-10-22 17:00 | 2.8016
2022-10-22 18:00 | 2.8094
2022-10-22 19:00 | 2.8046
2022-10-22 20:00 | 2.8082
2022-10-22 21:00 | 2.8064
2022-10-22 22:00 | 2.7992
2022-10-22 23:00 | 2.801
2022-10-23 | 2.7998
2022-10-23 01:00 | 2.7945
2022-10-23 02:00 | 2.8363
2022-10-23 03:00 | 2.8337
2022-10-23 04:00 | 2.8369
2022-10-23 05:00 | 2.8548
2022-10-23 06:00 | 2.8428
2022-10-23 07:00 | 2.8719
2022-10-23 08:00 | 2.9066
2022-10-23 09:00 | 2.8918
2022-10-23 10:00 | 2.8514
2022-10-23 11:00 | 2.8514
2022-10-23 12:00 | 2.8179
2022-10-23 13:00 | 2.8311
2022-10-23 14:00 | 2.8337
2022-10-23 15:00 | 2.8198
2022-10-23 16:00 | 2.8305
2022-10-23 17:00 | 2.8636
2022-10-23 18:00 | 2.8305
2022-10-23 19:00 | 2.8337
2022-10-23 20:00 | 2.8441
2022-10-23 21:00 | 2.8235
2022-10-23 22:00 | 2.8173
2022-10-23 23:00 | 2.833
2022-10-24 | 2.8046
2022-10-24 01:00 | 2.8324
2022-10-24 02:00 | 2.8388
2022-10-24 03:00 | 2.8414
2022-10-24 04:00 | 2.8324
2022-10-24 05:00 | 2.8622
2022-10-24 06:00 | 2.8581
2022-10-24 07:00 | 2.8588
2022-10-24 08:00 | 4.0959
2022-10-24 09:00 | 4.0959
2022-10-24 10:00 | 4.0959
2022-10-24 11:00 | 4.0959
2022-10-24 12:00 | 4.0959
2022-10-24 13:00 | 4.0959
2022-10-24 14:00 | 4.0959
2022-10-24 15:00 | 4.0959
2022-10-24 16:00 | 4.0959
2022-10-24 17:00 | 2.8161
2022-10-24 18:00 | 2.7735
2022-10-24 19:00 | 2.7769
2022-10-24 20:00 | 2.7638
2022-10-24 21:00 | 2.7752
2022-10-24 22:00 | 2.787
2022-10-24 23:00 | 2.8094
2022-10-25 | 2.7814
2022-10-25 01:00 | 2.804
2022-10-25 02:00 | 2.807
2022-10-25 03:00 | 2.7945
2022-10-25 04:00 | 2.7992
2022-10-25 05:00 | 2.8229
2022-10-25 06:00 | 4.0959
2022-10-25 07:00 | 4.0959
2022-10-25 08:00 | 4.0959
2022-10-25 09:00 | 4.0959
2022-10-25 10:00 | 4.0959
2022-10-25 11:00 | 4.0959
2022-10-25 12:00 | 4.0959
2022-10-25 13:00 | 4.0959
2022-10-25 14:00 | 4.0959
2022-10-25 15:00 | 4.0959
2022-10-25 16:00 | 4.0959
2022-10-25 17:00 | 4.0959
2022-10-25 18:00 | 4.0959
2022-10-25 19:00 | 4.0959
2022-10-25 20:00 | 4.0959
2022-10-25 21:00 | 4.0959
2022-10-25 22:00 | 4.0959
2022-10-25 23:00 | 4.0959
2022-10-26 | 4.0959
2022-10-26 01:00 | 4.0959
2022-10-26 02:00 | 4.0959
2022-10-26 03:00 | 4.0959
2022-10-26 04:00 | 4.0959
2022-10-26 05:00 | 4.0959
2022-10-26 06:00 | 4.0959
2022-10-26 07:00 | 4.0959
2022-10-26 08:00 | 4.0959
2022-10-26 09:00 | 4.0959
2022-10-26 10:00 | 4.0959
2022-10-26 11:00 | 4.0959
2022-10-26 12:00 | 4.0959
2022-10-26 13:00 | 4.0959
2022-10-26 14:00 | 4.0959
2022-10-26 15:00 | 4.0959
2022-10-26 16:00 | 4.0959
2022-10-26 17:00 | 4.0959
2022-10-26 18:00 | 4.0959
2022-10-26 19:00 | 4.0959
2022-10-26 20:00 | 4.0959
2022-10-26 21:00 | 2.8046
2022-10-26 22:00 | 2.8106
2022-10-26 23:00 | 2.8324
2022-10-27 | 2.8527
2022-10-27 01:00 | 2.8608
2022-10-27 02:00 | 2.8521
2022-10-27 03:00 | 2.874
2022-10-27 04:00 | 2.9081
2022-10-27 05:00 | 4.0959
2022-10-27 06:00 | 4.0959
2022-10-27 07:00 | 4.0959
2022-10-27 08:00 | 4.0959
2022-10-27 09:00 | 4.0959
2022-10-27 10:00 | 4.0959
2022-10-27 11:00 | 4.0959
2022-10-27 12:00 | 4.0959
2022-10-27 13:00 | 4.0959
2022-10-27 14:00 | 4.0959
2022-10-27 15:00 | 4.0959
2022-10-27 16:00 | 4.0959
2022-10-27 17:00 | 4.0959
2022-10-27 18:00 | 4.0959
2022-10-27 19:00 | 4.0959
2022-10-27 20:00 | 4.0959
2022-10-27 21:00 | 4.0959
2022-10-27 22:00 | 4.0959
2022-10-27 23:00 | 4.0959
2022-10-28 | 4.0959
2022-10-28 01:00 | 4.0959
2022-10-28 02:00 | 4.0959
2022-10-28 03:00 | 4.0959
2022-10-28 04:00 | 4.0959
2022-10-28 05:00 | 4.0959
2022-10-28 06:00 | 4.0959
2022-10-28 07:00 | 4.0959
2022-10-28 08:00 | 4.0959
2022-10-28 09:00 | 4.0959
2022-10-28 10:00 | 4.0959
2022-10-28 11:00 | 4.0959
2022-10-28 12:00 | 4.0959
2022-10-28 13:00 | 4.0959
2022-10-28 14:00 | 4.0959
2022-10-28 15:00 | 4.0959
2022-10-28 16:00 | 4.0959
2022-10-28 17:00 | 4.0959
2022-10-28 18:00 | 0.85505
2022-10-28 19:00 | 0.86214
2022-10-28 20:00 | 0.85297
2022-10-28 21:00 | 0.8499
2022-10-28 22:00 | 0.83867
2022-10-28 23:00 | 0.83667
2022-10-29 | 0.84074
2022-10-29 01:00 | 0.88057
2022-10-29 02:00 | 0.86422
2022-10-29 03:00 | 0.85297
2022-10-29 04:00 | 0.85398
2022-10-29 05:00 | 0.87648
2022-10-29 06:00 | 0.89903
2022-10-29 07:00 | 0.90414
2022-10-29 08:00 | 0.89184
2022-10-29 09:00 | 0.90313
2022-10-29 10:00 | 0.86522
2022-10-29 11:00 | 0.87031
2022-10-29 12:00 | 0.90514
2022-10-29 13:00 | 0.89184
2022-10-29 14:00 | 0.88775
2022-10-29 15:00 | 0.87849
2022-10-29 16:00 | 0.87956
2022-10-29 17:00 | 0.88674
2022-10-29 18:00 | 0.86623
2022-10-29 19:00 | 0.8744
2022-10-29 20:00 | 0.86114
2022-10-29 21:00 | 0.87339
2022-10-29 22:00 | 0.85197
2022-10-29 23:00 | 0.86522
2022-10-30 | 0.88365
2022-10-30 01:00 | 0.88567
2022-10-30 02:00 | 0.88157
2022-10-30 03:00 | 0.88466
2022-10-30 04:00 | 0.89184
2022-10-30 05:00 | 0.88775
2022-10-30 06:00 | 0.90004
2022-10-30 07:00 | 0.91133
2022-10-30 08:00 | 0.90104
2022-10-30 09:00 | 0.90824
2022-10-30 10:00 | 0.89903
2022-10-30 11:00 | 0.87031
2022-10-30 12:00 | 0.88157
2022-10-30 13:00 | 0.87748
2022-10-30 14:00 | 0.86422
2022-10-30 15:00 | 0.8683
2022-10-30 16:00 | 0.86931
2022-10-30 17:00 | 0.87138
2022-10-30 18:00 | 0.86522
2022-10-30 19:00 | 0.88157
2022-10-30 20:00 | 0.87748
2022-10-30 21:00 | 0.87239
2022-10-30 22:00 | 0.87547
2022-10-30 23:00 | 0.86522
2022-10-31 | 0.87138
2022-10-31 01:00 | 0.88057
2022-10-31 02:00 | 0.8744
2022-10-31 03:00 | 0.88057
2022-10-31 04:00 | 0.88567
2022-10-31 05:00 | 2.3766
2022-10-31 06:00 | 4.0959
2022-10-31 07:00 | 4.0959
2022-10-31 08:00 | 4.0959
2022-10-31 09:00 | 4.0959
2022-10-31 10:00 | 4.0959
2022-10-31 11:00 | 4.0959
2022-10-31 12:00 | 4.0959
2022-10-31 13:00 | 4.0959
2022-10-31 14:00 | 4.0959
2022-10-31 15:00 | 4.0959
2022-10-31 16:00 | 4.0959
2022-10-31 17:00 | 4.0959
2022-10-31 18:00 | 2.4155
2022-10-31 19:00 | 2.405
2022-10-31 20:00 | 2.404
2022-10-31 21:00 | 2.4106
2022-10-31 22:00 | 2.4206
2022-10-31 23:00 | 2.4108
2022-11-01 | 2.4227
2022-11-01 01:00 | 2.4201
2022-11-01 02:00 | 2.4161
2022-11-01 03:00 | 2.4155
2022-11-01 04:00 | 2.4225
2022-11-01 05:00 | 2.4254
2022-11-01 06:00 | 4.0959
2022-11-01 07:00 | 4.0959
2022-11-01 08:00 | 4.0959
2022-11-01 09:00 | 4.0959
2022-11-01 10:00 | 4.0959
2022-11-01 11:00 | 4.0959
2022-11-01 12:00 | 4.0959
2022-11-01 13:00 | 4.0959
2022-11-01 14:00 | 4.0959
2022-11-01 15:00 | 4.0959
2022-11-01 16:00 | 4.0959
2022-11-01 17:00 | 4.0959
2022-11-01 18:00 | 2.7616
2022-11-01 19:00 | 2.7455
2022-11-01 20:00 | 2.7638
2022-11-01 21:00 | 2.7758
2022-11-01 22:00 | 2.791
2022-11-01 23:00 | 2.7836
2022-11-02 | 2.8058
2022-11-02 01:00 | 2.8608
2022-11-02 02:00 | 2.8636
2022-11-02 03:00 | 2.8761
2022-11-02 04:00 | 2.8548
2022-11-02 05:00 | 4.0959
2022-11-02 06:00 | 4.0959
2022-11-02 07:00 | 4.0959
2022-11-02 08:00 | 4.0959
2022-11-02 09:00 | 4.0959
2022-11-02 10:00 | 4.0959
2022-11-02 11:00 | 4.0959
2022-11-02 12:00 | 4.0959
2022-11-02 13:00 | 4.0959
2022-11-02 14:00 | 4.0959
2022-11-02 15:00 | 4.0959
2022-11-02 16:00 | 4.0959
2022-11-02 17:00 | 4.0959
2022-11-02 18:00 | 4.0959
2022-11-02 19:00 | 2.7808
2022-11-02 20:00 | 2.807
2022-11-02 21:00 | 2.807
2022-11-02 22:00 | 2.8124
2022-11-02 23:00 | 2.8204
2022-11-03 | 2.8388
2022-11-03 01:00 | 2.8636
2022-11-03 02:00 | 2.8684
2022-11-03 03:00 | 2.8581
2022-11-03 04:00 | 2.8868
2022-11-03 05:00 | 2.9089
2022-11-03 06:00 | 2.9257
2022-11-03 07:00 | 2.8977
2022-11-03 08:00 | 2.8882
2022-11-03 09:00 | 2.8622
2022-11-03 10:00 | 2.821
2022-11-03 11:00 | 2.828
2022-11-03 12:00 | 2.7945
2022-11-03 13:00 | 2.7957
2022-11-03 14:00 | 2.7998
2022-11-03 15:00 | 2.7659
2022-11-03 16:00 | 2.7611
2022-11-03 17:00 | 2.8058
2022-11-03 18:00 | 2.8034
2022-11-03 19:00 | 2.7957
2022-11-03 20:00 | 2.8242
2022-11-03 21:00 | 2.8421
2022-11-03 22:00 | 2.8344
2022-11-03 23:00 | 2.8223
2022-11-04 | 2.8402
2022-11-04 01:00 | 2.8754
2022-11-04 02:00 | 2.8846
2022-11-04 03:00 | 2.867
2022-11-04 04:00 | 2.8897
2022-11-04 05:00 | 4.0959
2022-11-04 06:00 | 4.0959
2022-11-04 07:00 | 4.0959
2022-11-04 08:00 | 4.0959
2022-11-04 09:00 | 4.0959
2022-11-04 10:00 | 4.0959
2022-11-04 11:00 | 4.0959
2022-11-04 12:00 | 4.0959
2022-11-04 13:00 | 4.0959
2022-11-04 14:00 | 4.0959
2022-11-04 15:00 | 4.0959
2022-11-04 16:00 | 4.0959
2022-11-04 17:00 | 4.0959
2022-11-04 18:00 | 4.0959
2022-11-04 19:00 | 4.0959
2022-11-04 20:00 | 2.8705
2022-11-04 21:00 | 2.8461
2022-11-04 22:00 | 2.8118
2022-11-04 23:00 | 2.81
2022-11-05 | 2.8229
2022-11-05 01:00 | 2.8046
2022-11-05 02:00 | 2.833
2022-11-05 03:00 | 2.835
2022-11-05 04:00 | 2.8369
2022-11-05 05:00 | 2.8311
2022-11-05 06:00 | 2.8467
2022-11-05 07:00 | 2.8454
2022-11-05 08:00 | 2.8507
2022-11-05 09:00 | 2.8376
2022-11-05 10:00 | 2.8382
2022-11-05 11:00 | 2.8487
2022-11-05 12:00 | 2.7842
2022-11-05 13:00 | 2.7986
2022-11-05 14:00 | 2.7719
2022-11-05 15:00 | 2.7916
2022-11-05 16:00 | 2.7814
2022-11-05 17:00 | 2.7675
2022-11-05 18:00 | 2.8382
2022-11-05 19:00 | 2.8363
2022-11-05 20:00 | 2.8229
2022-11-05 21:00 | 2.8235
2022-11-05 22:00 | 2.7893
2022-11-05 23:00 | 2.7905
2022-11-06 | 2.7814
2022-11-06 01:00 | 2.7928
2022-11-06 02:00 | 2.8022
2022-11-06 03:00 | 2.801
2022-11-06 04:00 | 2.8075
2022-11-06 05:00 | 2.804
2022-11-06 06:00 | 2.813
2022-11-06 07:00 | 2.8155
2022-11-06 08:00 | 2.8273
2022-11-06 09:00 | 2.8467
2022-11-06 10:00 | 2.8186
2022-11-06 11:00 | 2.8376
2022-11-06 12:00 | 2.813
2022-11-06 13:00 | 2.8167
2022-11-06 14:00 | 2.7741
2022-11-06 15:00 | 2.7681
2022-11-06 16:00 | 2.7916
2022-11-06 17:00 | 2.8016
2022-11-06 18:00 | 2.81
2022-11-06 19:00 | 2.7998
2022-11-06 20:00 | 2.8022
2022-11-06 21:00 | 2.8046
2022-11-06 22:00 | 2.8094
2022-11-06 23:00 | 2.7974
2022-11-07 | 2.7939
2022-11-07 01:00 | 2.7769
2022-11-07 02:00 | 2.7864
2022-11-07 03:00 | 2.7842
2022-11-07 04:00 | 2.821
2022-11-07 05:00 | 2.7905
2022-11-07 06:00 | 4.0959
2022-11-07 07:00 | 4.0959
2022-11-07 08:00 | 4.0959
2022-11-07 09:00 | 4.0959
2022-11-07 10:00 | 4.0959
2022-11-07 11:00 | 4.0959
2022-11-07 12:00 | 4.0959
2022-11-07 13:00 | 4.0959
2022-11-07 14:00 | 4.0959
2022-11-07 15:00 | 4.0959
2022-11-07 16:00 | 4.0959
2022-11-07 17:00 | 4.0959
2022-11-07 18:00 | 4.0959
2022-11-07 19:00 | 2.2915
2022-11-07 20:00 | 2.2974
2022-11-07 21:00 | 2.2978
2022-11-07 22:00 | 2.369
2022-11-07 23:00 | 2.356
2022-11-08 | 2.3687
2022-11-08 01:00 | 2.3723
2022-11-08 02:00 | 2.3769
2022-11-08 03:00 | 2.3776
2022-11-08 04:00 | 2.3762
2022-11-08 05:00 | 2.3821
2022-11-08 06:00 | 2.3854
2022-11-08 07:00 | 2.3892
2022-11-08 08:00 | 2.3903
2022-11-08 09:00 | 2.3978
2022-11-08 10:00 | 2.3922
2022-11-08 11:00 | 2.3847
2022-11-08 12:00 | 2.3828
2022-11-08 13:00 | 2.3779
2022-11-08 14:00 | 2.3779
2022-11-08 15:00 | 2.3774
2022-11-08 16:00 | 2.3653
2022-11-08 17:00 | 2.3637
2022-11-08 18:00 | 2.3618
2022-11-08 19:00 | 2.3601
2022-11-08 20:00 | 2.3375
2022-11-08 21:00 | 2.356
2022-11-08 22:00 | 2.3734
2022-11-08 23:00 | 2.369
2022-11-09 | 2.3679
2022-11-09 01:00 | 2.365
2022-11-09 02:00 | 2.3739
2022-11-09 03:00 | 2.3796
2022-11-09 04:00 | 2.3713
2022-11-09 05:00 | 2.3781
2022-11-09 06:00 | 2.3871
2022-11-09 07:00 | 2.3951
2022-11-09 08:00 | 2.3901
2022-11-09 09:00 | 2.3949
2022-11-09 10:00 | 2.3794
2022-11-09 11:00 | 2.3826
2022-11-09 12:00 | 2.369
2022-11-09 13:00 | 2.3639
2022-11-09 14:00 | 2.3671
2022-11-09 15:00 | 2.3723
2022-11-09 16:00 | 2.3661
2022-11-09 17:00 | 2.3721
2022-11-09 18:00 | 2.3756
2022-11-09 19:00 | 2.3685
2022-11-09 20:00 | 2.3674
2022-11-09 21:00 | 2.3523
2022-11-09 22:00 | 2.3685
2022-11-09 23:00 | 2.3626
2022-11-10 | 2.3637
2022-11-10 01:00 | 2.3685
2022-11-10 02:00 | 2.3685
2022-11-10 03:00 | 2.3708
2022-11-10 04:00 | 2.3716
2022-11-10 05:00 | 2.3731
2022-11-10 06:00 | 2.3799
2022-11-10 07:00 | 2.3928
2022-11-10 08:00 | 2.362
2022-11-10 09:00 | 2.3716
2022-11-10 10:00 | 2.3759
2022-11-10 11:00 | 2.362
2022-11-10 12:00 | 2.3577
2022-11-10 13:00 | 2.3491
2022-11-10 14:00 | 2.3509
2022-11-10 15:00 | 2.3444
2022-11-10 16:00 | 2.345
2022-11-10 17:00 | 2.3426
2022-11-10 18:00 | 2.3607
2022-11-10 19:00 | 2.3483
2022-11-10 20:00 | 2.3239
2022-11-10 21:00 | 2.3249
2022-11-10 22:00 | 2.3226
2022-11-10 23:00 | 2.3287
2022-11-11 | 2.3239
2022-11-11 01:00 | 2.3206
2022-11-11 02:00 | 2.339
2022-11-11 03:00 | 2.3402
2022-11-11 04:00 | 2.3347
2022-11-11 05:00 | 2.3417
2022-11-11 06:00 | 2.3399
2022-11-11 07:00 | 2.3588
2022-11-11 08:00 | 2.3512
2022-11-11 09:00 | 2.3596
2022-11-11 10:00 | 2.3485
2022-11-11 11:00 | 2.348
2022-11-11 12:00 | 2.3375
2022-11-11 13:00 | 2.3405
2022-11-11 14:00 | 2.3356
2022-11-11 15:00 | 2.3328
2022-11-11 16:00 | 2.3278
2022-11-11 17:00 | 2.3222
2022-11-11 18:00 | 2.3255
2022-11-11 19:00 | 2.3105
2022-11-11 20:00 | 2.3038
2022-11-11 21:00 | 2.2985
2022-11-11 22:00 | 2.307
2022-11-11 23:00 | 2.2988
2022-11-12 | 2.3258
2022-11-12 01:00 | 2.3105
2022-11-12 02:00 | 2.2919
2022-11-12 03:00 | 2.3003
2022-11-12 04:00 | 2.2855
2022-11-12 05:00 | 2.2988
2022-11-12 06:00 | 2.2992
2022-11-12 07:00 | 2.3136
2022-11-12 08:00 | 2.3059
2022-11-12 09:00 | 2.3235
2022-11-12 10:00 | 2.3255
2022-11-12 11:00 | 2.3274
2022-11-12 12:00 | 2.3378
2022-11-12 13:00 | 2.3199
2022-11-12 14:00 | 2.3328
2022-11-12 15:00 | 2.3258
2022-11-12 16:00 | 2.3255
2022-11-12 17:00 | 2.3242
2022-11-12 18:00 | 2.3319
2022-11-12 19:00 | 2.3149
2022-11-12 20:00 | 2.3297
2022-11-12 21:00 | 2.3196
2022-11-12 22:00 | 2.3219
2022-11-12 23:00 | 2.3255
2022-11-13 | 2.3049
2022-11-13 01:00 | 2.3219
2022-11-13 02:00 | 2.3193
2022-11-13 03:00 | 2.3294
2022-11-13 04:00 | 2.3258
2022-11-13 05:00 | 2.3344
2022-11-13 06:00 | 2.3408
2022-11-13 07:00 | 2.3417
2022-11-13 08:00 | 2.3435
2022-11-13 09:00 | 2.3438
2022-11-13 10:00 | 2.3488
2022-11-13 11:00 | 2.35
2022-11-13 12:00 | 2.3408
2022-11-13 13:00 | 2.3483
2022-11-13 14:00 | 2.3517
2022-11-13 15:00 | 2.3462
2022-11-13 16:00 | 2.352
2022-11-13 17:00 | 2.3471
2022-11-13 18:00 | 2.3537
2022-11-13 19:00 | 2.3429
2022-11-13 20:00 | 2.3488
2022-11-13 21:00 | 2.3456
2022-11-13 22:00 | 2.3435
2022-11-13 23:00 | 2.3514
2022-11-14 | 2.352
2022-11-14 01:00 | 2.3588
2022-11-14 02:00 | 2.3588
2022-11-14 03:00 | 2.3692
2022-11-14 04:00 | 2.3766
2022-11-14 05:00 | 2.3734
2022-11-14 06:00 | 2.3857
2022-11-14 07:00 | 2.3818
2022-11-14 08:00 | 2.3813
2022-11-14 09:00 | 2.4912
2022-11-14 10:00 | 2.4886
2022-11-14 11:00 | 2.4824
2022-11-14 12:00 | 2.4772
2022-11-14 13:00 | 2.4731
2022-11-14 14:00 | 2.4742
2022-11-14 15:00 | 2.4761
2022-11-14 16:00 | 2.4706
2022-11-14 17:00 | 2.4729
2022-11-14 18:00 | 2.4811
2022-11-14 19:00 | 2.4779
2022-11-14 20:00 | 1.8108
2022-11-14 21:00 | 1.8043
2022-11-14 22:00 | 1.7877
2022-11-14 23:00 | 1.7951
2022-11-15 | 1.7951
2022-11-15 01:00 | 1.8344
2022-11-15 02:00 | 1.8108
2022-11-15 03:00 | 1.8108
2022-11-15 04:00 | 1.8353
2022-11-15 05:00 | 1.8393
2022-11-15 06:00 | 1.8536
2022-11-15 07:00 | 1.8756
2022-11-15 08:00 | 1.8694
2022-11-15 09:00 | 1.8568
2022-11-15 10:00 | 1.8279
2022-11-15 11:00 | 1.8231
2022-11-15 12:00 | 1.8026
2022-11-15 13:00 | 1.81
2022-11-15 14:00 | 1.8043
2022-11-15 15:00 | 1.819
2022-11-15 16:00 | 1.8149
2022-11-15 17:00 | 1.8116
2022-11-15 18:00 | 1.8464
2022-11-15 19:00 | 1.8231
2022-11-15 20:00 | 1.8116
2022-11-15 21:00 | 1.819
2022-11-15 22:00 | 1.7751
2022-11-15 23:00 | 1.7742
2022-11-16 | 1.8067
2022-11-16 01:00 | 1.8108
2022-11-16 02:00 | 1.8108
2022-11-16 03:00 | 1.8076
2022-11-16 04:00 | 1.801
2022-11-16 05:00 | 1.8034
2022-11-16 06:00 | 1.8174
2022-11-16 07:00 | 1.939
2022-11-16 08:00 | 4.0959
2022-11-16 09:00 | 4.0959
2022-11-16 10:00 | 4.0959
2022-11-16 11:00 | 4.0959
2022-11-16 12:00 | 4.0959
2022-11-16 13:00 | 4.0959
2022-11-16 14:00 | 4.0959
2022-11-16 15:00 | 4.0959
2022-11-16 16:00 | 4.0959
2022-11-16 17:00 | 4.0959
2022-11-16 18:00 | 4.0959
2022-11-16 19:00 | 4.0959
2022-11-16 20:00 | 4.0959
2022-11-16 21:00 | 4.0959
2022-11-16 22:00 | 2.4214
2022-11-16 23:00 | 0.87339
2022-11-17 | 0.91335
2022-11-17 01:00 | 0.91335
2022-11-17 02:00 | 0.91544
2022-11-17 03:00 | 0.91335
2022-11-17 04:00 | 0.91853
2022-11-17 05:00 | 0.92466
2022-11-17 06:00 | 0.9411
2022-11-17 07:00 | 2.5329
2022-11-17 08:00 | 4.0959
2022-11-17 09:00 | 4.0959
2022-11-17 10:00 | 4.0959
2022-11-17 11:00 | 4.0959
2022-11-17 12:00 | 4.0959
2022-11-17 13:00 | 4.0959
2022-11-17 14:00 | 4.0959
2022-11-17 15:00 | 4.0959
2022-11-17 16:00 | 4.0959
2022-11-17 17:00 | 4.0959
2022-11-17 18:00 | 4.0959
2022-11-17 19:00 | 4.0959
2022-11-17 20:00 | 4.0959
2022-11-17 21:00 | 4.0959
2022-11-17 22:00 | 4.0959
2022-11-17 23:00 | 2.7928
2022-11-18 | 2.8046
2022-11-18 01:00 | 2.8112
2022-11-18 02:00 | 2.8173
2022-11-18 03:00 | 2.8179
2022-11-18 04:00 | 2.8677
2022-11-18 05:00 | 2.8761
2022-11-18 06:00 | 2.9022
2022-11-18 07:00 | 2.9203
2022-11-18 08:00 | 2.9226
2022-11-18 09:00 | 3.1694
2022-11-18 10:00 | 4.0959
2022-11-18 11:00 | 4.0959
2022-11-18 12:00 | 4.0959
2022-11-18 13:00 | 4.0959
2022-11-18 14:00 | 4.0959
2022-11-18 15:00 | 4.0959
2022-11-18 16:00 | 4.0959
2022-11-18 17:00 | 4.0959
2022-11-18 18:00 | 4.0959
2022-11-18 19:00 | 4.0959
2022-11-18 20:00 | 4.0959
2022-11-18 21:00 | 4.0959
2022-11-18 22:00 | 4.0959
2022-11-18 23:00 | 4.0959
2022-11-19 | 4.0959
2022-11-19 01:00 | 4.0959
2022-11-19 02:00 | 4.0959
2022-11-19 03:00 | 4.0959
2022-11-19 04:00 | 4.0959
2022-11-19 05:00 | 4.0959
2022-11-19 06:00 | 4.0959
2022-11-19 07:00 | 4.0959
2022-11-19 08:00 | 4.0959
2022-11-19 09:00 | 4.0959
2022-11-19 10:00 | 4.0959
2022-11-19 11:00 | 4.0959
2022-11-19 12:00 | 4.0959
2022-11-19 13:00 | 4.0959
2022-11-19 14:00 | 4.0959
2022-11-19 15:00 | 4.0959
2022-11-19 16:00 | 4.0959
2022-11-19 17:00 | 4.0959
2022-11-19 18:00 | 4.0959
2022-11-19 19:00 | 4.0959
2022-11-19 20:00 | 4.0959
2022-11-19 21:00 | 4.0959
2022-11-19 22:00 | 4.0959
2022-11-19 23:00 | 4.0959
2022-11-20 | 4.0959
2022-11-20 01:00 | 4.0959
2022-11-20 02:00 | 4.0959
2022-11-20 03:00 | 4.0959
2022-11-20 04:00 | 4.0959
2022-11-20 05:00 | 4.0959
2022-11-20 06:00 | 4.0959
2022-11-20 07:00 | 4.0959
2022-11-20 08:00 | 4.0959
2022-11-20 09:00 | 4.0959
2022-11-20 10:00 | 4.0959
2022-11-20 11:00 | 4.0959
2022-11-20 12:00 | 4.0959
2022-11-20 13:00 | 4.0959
2022-11-20 14:00 | 4.0959
2022-11-20 15:00 | 4.0959
2022-11-20 16:00 | 4.0959
2022-11-20 17:00 | 4.0959
2022-11-20 18:00 | 4.0959
2022-11-20 19:00 | 4.0959
2022-11-20 20:00 | 4.0959
2022-11-20 21:00 | 4.0959
2022-11-20 22:00 | 4.0959
2022-11-20 23:00 | 4.0959
2022-11-21 | 4.0959
2022-11-21 01:00 | 4.0959
2022-11-21 02:00 | 4.0959
2022-11-21 03:00 | 4.0959
2022-11-21 04:00 | 4.0959
2022-11-21 05:00 | 4.0959
2022-11-21 06:00 | 4.0959
2022-11-21 07:00 | 4.0959
2022-11-21 08:00 | 4.0959
2022-11-21 09:00 | 4.0959
2022-11-21 10:00 | 4.0959
2022-11-21 11:00 | 4.0959
2022-11-21 12:00 | 4.0959
2022-11-21 13:00 | 4.0959
2022-11-21 14:00 | 4.0959
2022-11-21 15:00 | 4.0959
2022-11-21 16:00 | 4.0959
2022-11-21 17:00 | 4.0959
2022-11-21 18:00 | 4.0959
2022-11-21 19:00 | 4.0959
2022-11-21 20:00 | 4.0959
2022-11-21 21:00 | 4.0959
2022-11-21 22:00 | 4.0959
2022-11-21 23:00 | 4.0959
2022-11-22 | 4.0959
2022-11-22 01:00 | 4.0959
2022-11-22 02:00 | 4.0959
2022-11-22 03:00 | 4.0959
2022-11-22 04:00 | 4.0959
2022-11-22 05:00 | 4.0959
2022-11-22 06:00 | 4.0959
2022-11-22 07:00 | 4.0959
2022-11-22 08:00 | 4.0959
2022-11-22 09:00 | 4.0959
2022-11-22 10:00 | 4.0959
2022-11-22 11:00 | 4.0959
2022-11-22 12:00 | 4.0959
2022-11-22 13:00 | 4.0959
2022-11-22 14:00 | 4.0959
2022-11-22 15:00 | 4.0959
2022-11-22 16:00 | 4.0959
2022-11-22 17:00 | 4.0959
2022-11-22 18:00 | 4.0959
2022-11-22 19:00 | 4.0959
2022-11-22 20:00 | 4.0959
2022-11-22 21:00 | 4.0959
2022-11-22 22:00 | 4.0959
2022-11-22 23:00 | 4.0959
2022-11-23 | 4.0959
2022-11-23 01:00 | 4.0959
2022-11-23 02:00 | 4.0959
2022-11-23 03:00 | 4.0959
2022-11-23 04:00 | 4.0959
2022-11-23 05:00 | 4.0959
2022-11-23 06:00 | 4.0959
2022-11-23 07:00 | 4.0959
2022-11-23 08:00 | 4.0959
2022-11-23 09:00 | 0.8744
2022-11-23 10:00 | 0.8336
2022-11-23 11:00 | 0.81833
2022-11-23 12:00 | 0.8326
2022-11-23 13:00 | 0.80309
2022-11-23 14:00 | 0.81634
2022-11-23 15:00 | 0.81121
2022-11-23 16:00 | 0.8509
2022-11-23 17:00 | 1.1757
2022-11-23 18:00 | 4.0959
2022-11-23 19:00 | 4.0959
2022-11-23 20:00 | 4.0959
2022-11-23 21:00 | 4.0959
2022-11-23 22:00 | 4.0959
2022-11-23 23:00 | 4.0959
2022-11-24 | 4.0959
2022-11-24 01:00 | 4.0959
2022-11-24 02:00 | 4.0959
2022-11-24 03:00 | 4.0959
2022-11-24 04:00 | 4.0959
2022-11-24 05:00 | 4.0959
2022-11-24 06:00 | 4.0959
2022-11-24 07:00 | 4.0959
2022-11-24 08:00 | 4.0959
2022-11-24 09:00 | 4.0959
2022-11-24 10:00 | 4.0959
2022-11-24 11:00 | 4.0959
2022-11-24 12:00 | 4.0959
2022-11-24 13:00 | 4.0959
2022-11-24 14:00 | 4.0959
2022-11-24 15:00 | 4.0959
2022-11-24 16:00 | 4.0959
2022-11-24 17:00 | 4.0959
2022-11-24 18:00 | 4.0959
2022-11-24 19:00 | 4.0959
2022-11-24 20:00 | 4.0959
2022-11-24 21:00 | 4.0959
2022-11-24 22:00 | 4.0959
2022-11-24 23:00 | 4.0959
2022-11-25 | 4.0959
2022-11-25 01:00 | 4.0959
2022-11-25 02:00 | 4.0959
2022-11-25 03:00 | 4.0959
2022-11-25 04:00 | 4.0959
2022-11-25 05:00 | 4.0959
2022-11-25 06:00 | 4.0959
2022-11-25 07:00 | 4.0959
2022-11-25 08:00 | 4.0959
2022-11-25 09:00 | 4.0959
2022-11-25 10:00 | 4.0959
2022-11-25 11:00 | 4.0959
2022-11-25 12:00 | 4.0959
2022-11-25 13:00 | 4.0959
2022-11-25 14:00 | 4.0959
2022-11-25 15:00 | 4.0959
2022-11-25 16:00 | 4.0959
2022-11-25 17:00 | 4.0959
2022-11-25 18:00 | 4.0959
2022-11-25 19:00 | 4.0959
2022-11-25 20:00 | 4.0959
2022-11-25 21:00 | 4.0959
2022-11-25 22:00 | 4.0959
2022-11-25 23:00 | 4.0959
2022-11-26 | 4.0959
2022-11-26 01:00 | 4.0959
2022-11-26 02:00 | 4.0959
2022-11-26 03:00 | 4.0959
2022-11-26 04:00 | 4.0959
2022-11-26 05:00 | 4.0959
2022-11-26 06:00 | 4.0959
2022-11-26 07:00 | 4.0959
2022-11-26 08:00 | 4.0959
2022-11-26 09:00 | 4.0959
2022-11-26 10:00 | 4.0959
2022-11-26 11:00 | 4.0959
2022-11-26 12:00 | 4.0959
2022-11-26 13:00 | 4.0959
2022-11-26 14:00 | 4.0959
2022-11-26 15:00 | 4.0959
2022-11-26 16:00 | 4.0959
2022-11-26 17:00 | 4.0959
2022-11-26 18:00 | 4.0959
2022-11-26 19:00 | 4.0959
2022-11-26 20:00 | 4.0959
2022-11-26 21:00 | 4.0959
2022-11-26 22:00 | 4.0959
2022-11-26 23:00 | 4.0959
2022-11-27 | 4.0959
2022-11-27 01:00 | 4.0959
2022-11-27 02:00 | 4.0959
2022-11-27 03:00 | 4.0959
2022-11-27 04:00 | 4.0959
2022-11-27 05:00 | 4.0959
2022-11-27 06:00 | 4.0959
2022-11-27 07:00 | 4.0959
2022-11-27 08:00 | 4.0959
2022-11-27 09:00 | 4.0959
2022-11-27 10:00 | 4.0959
2022-11-27 11:00 | 4.0959
2022-11-27 12:00 | 4.0959
2022-11-27 13:00 | 4.0959
2022-11-27 14:00 | 4.0959
2022-11-27 15:00 | 4.0959
2022-11-27 16:00 | 4.0959
2022-11-27 17:00 | 4.0959
2022-11-27 18:00 | 4.0959
2022-11-27 19:00 | 4.0959
2022-11-27 20:00 | 4.0959
2022-11-27 21:00 | 4.0959
2022-11-27 22:00 | 4.0959
2022-11-27 23:00 | 4.0959
2022-11-28 | 4.0959
2022-11-28 01:00 | 4.0959
2022-11-28 02:00 | 4.0959
2022-11-28 03:00 | 4.0959
2022-11-28 04:00 | 4.0959
2022-11-28 05:00 | 4.0959
2022-11-28 06:00 | 4.0959
2022-11-28 07:00 | 4.0959
2022-11-28 08:00 | 4.0959
2022-11-28 09:00 | 4.0959
2022-11-28 10:00 | 4.0959
2022-11-28 11:00 | 4.0959
2022-11-28 12:00 | 4.0959
2022-11-28 13:00 | 4.0959
2022-11-28 14:00 | 4.0959
2022-11-28 15:00 | 4.0959
2022-11-28 16:00 | 4.0959
2022-11-28 17:00 | 4.0959
2022-11-28 18:00 | 4.0959
2022-11-28 19:00 | 4.0959
2022-11-28 20:00 | 4.0959
2022-11-28 21:00 | 4.0959
2022-11-28 22:00 | 4.0959
2022-11-28 23:00 | 4.0959
2022-11-29 | 4.0959
2022-11-29 01:00 | 4.0959
2022-11-29 02:00 | 4.0959
2022-11-29 03:00 | 4.0959
2022-11-29 04:00 | 4.0959
2022-11-29 05:00 | 4.0959
2022-11-29 06:00 | 4.0959
2022-11-29 07:00 | 4.0959
2022-11-29 08:00 | 4.0959
2022-11-29 09:00 | 4.0959
2022-11-29 10:00 | 4.0959
2022-11-29 11:00 | 4.0959
2022-11-29 12:00 | 4.0959
2022-11-29 13:00 | 4.0959
2022-11-29 14:00 | 4.0959
2022-11-29 15:00 | 4.0959
2022-11-29 16:00 | 4.0959
2022-11-29 17:00 | 4.0959
2022-11-29 18:00 | 4.0959
2022-11-29 19:00 | 4.0959
2022-11-29 20:00 | 4.0959
2022-11-29 21:00 | 4.0959
2022-11-29 22:00 | 4.0959
2022-11-29 23:00 | 4.0959
2022-11-30 | 4.0959
2022-11-30 01:00 | 4.0959
2022-11-30 02:00 | 4.0959
2022-11-30 03:00 | 4.0959
2022-11-30 04:00 | 4.0959
2022-11-30 05:00 | 4.0959
2022-11-30 06:00 | 4.0959
2022-11-30 07:00 | 4.0959
2022-11-30 08:00 | 4.0959
2022-11-30 09:00 | 4.0959
2022-11-30 10:00 | 4.0959
2022-11-30 11:00 | 4.0959
2022-11-30 12:00 | 4.0959
2022-11-30 13:00 | 4.0959
2022-11-30 14:00 | 4.0959
2022-11-30 15:00 | 4.0959
2022-11-30 16:00 | 4.0959
2022-11-30 17:00 | 4.0959
2022-11-30 18:00 | 4.0959
2022-11-30 19:00 | 4.0959
2022-11-30 20:00 | 4.0959
2022-11-30 21:00 | 4.0959
2022-11-30 22:00 | 4.0959
2022-11-30 23:00 | 4.0959
2022-12-01 | 4.0959
2022-12-01 01:00 | 4.0959
2022-12-01 02:00 | 4.0959
2022-12-01 03:00 | 4.0959
2022-12-01 04:00 | 4.0959
2022-12-01 05:00 | 4.0959
2022-12-01 06:00 | 4.0959
2022-12-01 07:00 | 4.0959
2022-12-01 08:00 | 4.0959
2022-12-01 09:00 | 4.0959
2022-12-01 10:00 | 4.0959
2022-12-01 11:00 | 4.0959
2022-12-01 12:00 | 4.0959
2022-12-01 13:00 | 4.0959
2022-12-01 14:00 | 4.0959
2022-12-01 15:00 | 4.0959
2022-12-01 16:00 | 4.0959
2022-12-01 17:00 | 4.0959
2022-12-01 18:00 | 4.0959
2022-12-01 19:00 | 4.0959
2022-12-01 20:00 | 4.0959
2022-12-01 21:00 | 4.0959
2022-12-01 22:00 | 4.0959
2022-12-01 23:00 | 4.0959
2022-12-02 | 4.0959
2022-12-02 01:00 | 4.0959
2022-12-02 02:00 | 4.0959
2022-12-02 03:00 | 4.0959
2022-12-02 04:00 | 4.0959
2022-12-02 05:00 | 4.0959
2022-12-02 06:00 | 4.0959
2022-12-02 07:00 | 4.0959
2022-12-02 08:00 | 4.0959
2022-12-02 09:00 | 4.0959
2022-12-02 10:00 | 4.0959
2022-12-02 11:00 | 4.0959
2022-12-02 12:00 | 4.0959
2022-12-02 13:00 | 4.0959
2022-12-02 14:00 | 4.0959
2022-12-02 15:00 | 4.0959
2022-12-02 16:00 | 4.0959
2022-12-02 17:00 | 4.0959
2022-12-02 18:00 | 4.0959
2022-12-02 19:00 | 4.0959
2022-12-02 20:00 | 4.0959
2022-12-02 21:00 | 4.0959
2022-12-02 22:00 | 4.0959
2022-12-02 23:00 | 4.0959
2022-12-03 | 4.0959
2022-12-03 01:00 | 4.0959
2022-12-03 02:00 | 4.0959
2022-12-03 03:00 | 4.0959
2022-12-03 04:00 | 4.0959
2022-12-03 05:00 | 4.0959
2022-12-03 06:00 | 4.0959
2022-12-03 07:00 | 4.0959
2022-12-03 08:00 | 4.0959
2022-12-03 09:00 | 4.0959
2022-12-03 10:00 | 4.0959
2022-12-03 11:00 | 4.0959
2022-12-03 12:00 | 4.0959
2022-12-03 13:00 | 4.0959
2022-12-03 14:00 | 4.0959
2022-12-03 15:00 | 4.0959
2022-12-03 16:00 | 4.0959
2022-12-03 17:00 | 4.0959
2022-12-03 18:00 | 4.0959
2022-12-03 19:00 | 4.0959
2022-12-03 20:00 | 4.0959
2022-12-03 21:00 | 4.0959
2022-12-03 22:00 | 4.0959
2022-12-03 23:00 | 4.0959
2022-12-04 | 4.0959
2022-12-04 01:00 | 4.0959
2022-12-04 02:00 | 4.0959
2022-12-04 03:00 | 4.0959
2022-12-04 04:00 | 4.0959
2022-12-04 05:00 | 4.0959
2022-12-04 06:00 | 4.0959
2022-12-04 07:00 | 4.0959
2022-12-04 08:00 | 4.0959
2022-12-04 09:00 | 4.0959
2022-12-04 10:00 | 4.0959
2022-12-04 11:00 | 4.0959
2022-12-04 12:00 | 4.0959
2022-12-04 13:00 | 4.0959
2022-12-04 14:00 | 4.0959
2022-12-04 15:00 | 4.0959
2022-12-04 16:00 | 4.0959
2022-12-04 17:00 | 4.0959
2022-12-04 18:00 | 4.0959
2022-12-04 19:00 | 4.0959
2022-12-04 20:00 | 4.0959
2022-12-04 21:00 | 4.0959
2022-12-04 22:00 | 4.0959
2022-12-04 23:00 | 4.0959
2022-12-05 | 4.0959
2022-12-05 01:00 | 4.0959
2022-12-05 02:00 | 4.0959
2022-12-05 03:00 | 4.0959
2022-12-05 04:00 | 4.0959
2022-12-05 05:00 | 4.0959
2022-12-05 06:00 | 4.0959
2022-12-05 07:00 | 4.0959
2022-12-05 08:00 | 4.0959
2022-12-05 09:00 | 4.0959
2022-12-05 10:00 | 4.0959
2022-12-05 11:00 | 4.0959
2022-12-05 12:00 | 4.0959
2022-12-05 13:00 | 4.0959
2022-12-05 14:00 | 4.0959
2022-12-05 15:00 | 4.0959
2022-12-05 16:00 | 4.0959
2022-12-05 17:00 | 4.0959
2022-12-05 18:00 | 4.0959
2022-12-05 19:00 | 4.0959
2022-12-05 20:00 | 4.0959
2022-12-05 21:00 | 4.0959
2022-12-05 22:00 | 4.0959
2022-12-05 23:00 | 4.0959
2022-12-06 | 4.0959
2022-12-06 01:00 | 4.0959
2022-12-06 02:00 | 4.0959
2022-12-06 03:00 | 4.0959
2022-12-06 04:00 | 4.0959
2022-12-06 05:00 | 4.0959
2022-12-06 06:00 | 4.0959
2022-12-06 07:00 | 4.0959
2022-12-06 08:00 | 4.0959
2022-12-06 09:00 | 3.1853
2022-12-06 10:00 | 3.1494
2022-12-06 11:00 | 3.1152
2022-12-06 12:00 | 3.0725
2022-12-06 13:00 | 3.0935
2022-12-06 14:00 | 3.0341
2022-12-06 15:00 | 3.1472
2022-12-06 16:00 | 3.0774
2022-12-06 17:00 | 3.0754
2022-12-06 18:00 | 3.144
2022-12-06 19:00 | 3.112
2022-12-06 20:00 | 3.0685
2022-12-06 21:00 | 3.0076
2022-12-06 22:00 | 3.0945
2022-12-06 23:00 | 3.1516
2022-12-07 | 3.0685
2022-12-07 01:00 | 3.1728
2022-12-07 02:00 | 3.2432
2022-12-07 03:00 | 3.2518
2022-12-07 04:00 | 3.2782
2022-12-07 05:00 | 3.2481
2022-12-07 06:00 | 3.2909
2022-12-07 07:00 | 3.3786
2022-12-07 08:00 | 3.3577
2022-12-07 09:00 | 3.2948
2022-12-07 10:00 | 3.2108
2022-12-07 11:00 | 3.2311
2022-12-07 12:00 | 3.144
2022-12-07 13:00 | 3.1236
2022-12-07 14:00 | 3.1582
2022-12-07 15:00 | 3.1278
2022-12-07 16:00 | 3.1683
2022-12-07 17:00 | 3.1898
2022-12-07 18:00 | 3.2543
2022-12-07 19:00 | 3.2494
2022-12-07 20:00 | 3.191
2022-12-07 21:00 | 3.191
2022-12-07 22:00 | 3.2215
2022-12-07 23:00 | 3.2084
2022-12-08 | 3.2215
2022-12-08 01:00 | 3.2948
2022-12-08 02:00 | 3.3118
2022-12-08 03:00 | 3.4575
2022-12-08 04:00 | 3.4835
2022-12-08 05:00 | 3.5473
2022-12-08 06:00 | 3.5855
2022-12-08 07:00 | 3.5721
2022-12-08 08:00 | 3.4305
2022-12-08 09:00 | 3.3885
2022-12-08 10:00 | 3.2988
2022-12-08 11:00 | 3.2706
2022-12-08 12:00 | 3.2323
2022-12-08 13:00 | 3.1991
2022-12-08 14:00 | 3.1864
2022-12-08 15:00 | 3.1762
2022-12-08 16:00 | 2.6537
2022-12-08 17:00 | 2.158
2022-12-08 18:00 | 2.7864
2022-12-08 19:00 | 2.778
2022-12-08 20:00 | 2.7808
2022-12-08 21:00 | 2.7475
2022-12-08 22:00 | 2.7385
2022-12-08 23:00 | 2.7638
2022-12-09 | 2.8112
2022-12-09 01:00 | 2.8148
2022-12-09 02:00 | 2.8273
2022-12-09 03:00 | 2.807
2022-12-09 04:00 | 2.8004
2022-12-09 05:00 | 2.8155
2022-12-09 06:00 | 2.8155
2022-12-09 07:00 | 2.854
2022-12-09 08:00 | 3.9224
2022-12-09 09:00 | 4.0959
2022-12-09 10:00 | 4.0959
2022-12-09 11:00 | 4.0959
2022-12-09 12:00 | 4.0959
2022-12-09 13:00 | 4.0959
2022-12-09 14:00 | 4.0959
2022-12-09 15:00 | 4.0959
2022-12-09 16:00 | 4.0959
2022-12-09 17:00 | 4.0959
2022-12-09 18:00 | 4.0959
2022-12-09 19:00 | 4.0959
2022-12-09 20:00 | 4.0959
2022-12-09 21:00 | 4.0959
2022-12-09 22:00 | 4.0959
2022-12-09 23:00 | 4.0959
2022-12-10 | 4.0959
2022-12-10 01:00 | 4.0959
2022-12-10 02:00 | 4.0959
2022-12-10 03:00 | 4.0959
2022-12-10 04:00 | 4.0959
2022-12-10 05:00 | 4.0959
2022-12-10 06:00 | 4.0959
2022-12-10 07:00 | 4.0959
2022-12-10 08:00 | 4.0959
2022-12-10 09:00 | 4.0959
2022-12-10 10:00 | 4.0959
2022-12-10 11:00 | 4.0959
2022-12-10 12:00 | 4.0959
2022-12-10 13:00 | 4.0959
2022-12-10 14:00 | 4.0959
2022-12-10 15:00 | 4.0959
2022-12-10 16:00 | 4.0959
2022-12-10 17:00 | 4.0959
2022-12-10 18:00 | 4.0959
2022-12-10 19:00 | 4.0959
2022-12-10 20:00 | 4.0959
2022-12-10 21:00 | 4.0959
2022-12-10 22:00 | 4.0959
2022-12-10 23:00 | 4.0959
2022-12-11 | 4.0959
2022-12-11 01:00 | 4.0959
2022-12-11 02:00 | 4.0959
2022-12-11 03:00 | 4.0959
2022-12-11 04:00 | 4.0959
2022-12-11 05:00 | 4.0959
2022-12-11 06:00 | 4.0959
2022-12-11 07:00 | 4.0959
2022-12-11 08:00 | 4.0959
2022-12-11 09:00 | 4.0959
2022-12-11 10:00 | 4.0959
2022-12-11 11:00 | 4.0959
2022-12-11 12:00 | 4.0959
2022-12-11 13:00 | 4.0959
2022-12-11 14:00 | 4.0959
2022-12-11 15:00 | 4.0959
2022-12-11 16:00 | 4.0959
2022-12-11 17:00 | 4.0959
2022-12-11 18:00 | 4.0959
2022-12-11 19:00 | 4.0959
2022-12-11 20:00 | 4.0959
2022-12-11 21:00 | 4.0959
2022-12-11 22:00 | 4.0959
2022-12-11 23:00 | 4.0959
2022-12-12 | 4.0959
2022-12-12 01:00 | 4.0959
2022-12-12 02:00 | 4.0959
2022-12-12 03:00 | 4.0959
2022-12-12 04:00 | 4.0959
2022-12-12 05:00 | 4.0959
2022-12-12 06:00 | 4.0959
2022-12-12 07:00 | 4.0959
2022-12-12 08:00 | 4.0959
2022-12-12 09:00 | 4.0959
2022-12-12 10:00 | 4.0959
2022-12-12 11:00 | 4.0959
2022-12-12 12:00 | 4.0959
2022-12-12 13:00 | 4.0959
2022-12-12 14:00 | 4.0959
2022-12-12 15:00 | 4.0959
2022-12-12 16:00 | 4.0959
2022-12-12 17:00 | 4.0959
2022-12-12 18:00 | 4.0959
2022-12-12 19:00 | 4.0959
2022-12-12 20:00 | 4.0959
2022-12-12 21:00 | 4.0959
2022-12-12 22:00 | 4.0959
2022-12-12 23:00 | 4.0959
2022-12-13 | 4.0959
2022-12-13 01:00 | 4.0959
2022-12-13 02:00 | 4.0959
2022-12-13 03:00 | 4.0959
2022-12-13 04:00 | 4.0959
2022-12-13 05:00 | 4.0959
2022-12-13 06:00 | 4.0959
2022-12-13 07:00 | 4.0959
2022-12-13 08:00 | 4.0959
2022-12-13 09:00 | 4.0959
2022-12-13 10:00 | 4.0959
2022-12-13 11:00 | 4.0959
2022-12-13 12:00 | 4.0959
2022-12-13 13:00 | 4.0959
2022-12-13 14:00 | 4.0959
2022-12-13 15:00 | 4.0959
2022-12-13 16:00 | 4.0959
2022-12-13 17:00 | 4.0959
2022-12-13 18:00 | 4.0959
2022-12-13 19:00 | 4.0959
2022-12-13 20:00 | 4.0959
2022-12-13 21:00 | 4.0959
2022-12-13 22:00 | 4.0959
2022-12-13 23:00 | 4.0959
2022-12-14 | 4.0959
2022-12-14 01:00 | 4.0959
2022-12-14 02:00 | 4.0959
2022-12-14 03:00 | 4.0959
2022-12-14 04:00 | 4.0959
2022-12-14 05:00 | 4.0959
2022-12-14 06:00 | 4.0959
2022-12-14 07:00 | 4.0959
2022-12-14 08:00 | 4.0959
2022-12-14 09:00 | 4.0959
2022-12-14 10:00 | 4.0959
2022-12-14 11:00 | 4.0959
2022-12-14 12:00 | 4.0959
2022-12-14 13:00 | 4.0959
2022-12-14 14:00 | 4.0959
2022-12-14 15:00 | 4.0959
2022-12-14 16:00 | 4.0959
2022-12-14 17:00 | 4.0959
2022-12-14 18:00 | 4.0959
2022-12-14 19:00 | 4.0959
2022-12-14 20:00 | 4.0959
2022-12-14 21:00 | 4.0959
2022-12-14 22:00 | 4.0959
2022-12-14 23:00 | 4.0959
2022-12-15 | 4.0959
2022-12-15 01:00 | 4.0959
2022-12-15 02:00 | 4.0959
2022-12-15 03:00 | 4.0959
2022-12-15 04:00 | 4.0959
2022-12-15 05:00 | 4.0959
2022-12-15 06:00 | 4.0959
2022-12-15 07:00 | 4.0959
2022-12-15 08:00 | 4.0959
2022-12-15 09:00 | 4.0959
2022-12-15 10:00 | 4.0959
2022-12-15 11:00 | 4.0959
2022-12-15 12:00 | 4.0959
2022-12-15 13:00 | 4.0959
2022-12-15 14:00 | 4.0959
2022-12-15 15:00 | 4.0959
2022-12-15 16:00 | 4.0959
2022-12-15 17:00 | 4.0959
2022-12-15 18:00 | 4.0959
2022-12-15 19:00 | 4.0959
2022-12-15 20:00 | 4.0959
2022-12-15 21:00 | 4.0959
2022-12-15 22:00 | 4.0959
2022-12-15 23:00 | 4.0959
2022-12-16 | 4.0959
2022-12-16 01:00 | 4.0959
2022-12-16 02:00 | 4.0959
2022-12-16 03:00 | 4.0959
2022-12-16 04:00 | 4.0959
2022-12-16 05:00 | 4.0959
2022-12-16 06:00 | 4.0959
2022-12-16 07:00 | 4.0959
2022-12-16 08:00 | 4.0959
2022-12-16 09:00 | 4.0959
2022-12-16 10:00 | 4.0959
2022-12-16 11:00 | 4.0959
2022-12-16 12:00 | 4.0959
2022-12-16 13:00 | 4.0959
2022-12-16 14:00 | 4.0959
2022-12-16 15:00 | 4.0959
2022-12-16 16:00 | 4.0959
2022-12-16 17:00 | 4.0959
2022-12-16 18:00 | 4.0959
2022-12-16 19:00 | 4.0959
2022-12-16 20:00 | 4.0959
2022-12-16 21:00 | 4.0959
2022-12-16 22:00 | 4.0959
2022-12-16 23:00 | 4.0959
2022-12-17 | 4.0959
2022-12-17 01:00 | 4.0959
2022-12-17 02:00 | 4.0959
2022-12-17 03:00 | 4.0959
2022-12-17 04:00 | 4.0959
2022-12-17 05:00 | 4.0959
2022-12-17 06:00 | 4.0959
2022-12-17 07:00 | 4.0959
2022-12-17 08:00 | 4.0959
2022-12-17 09:00 | 4.0959
2022-12-17 10:00 | 4.0959
2022-12-17 11:00 | 4.0959
2022-12-17 12:00 | 4.0959
2022-12-17 13:00 | 4.0959
2022-12-17 14:00 | 4.0959
2022-12-17 15:00 | 4.0959
2022-12-17 16:00 | 4.0959
2022-12-17 17:00 | 4.0959
2022-12-17 18:00 | 4.0959
2022-12-17 19:00 | 4.0959
2022-12-17 20:00 | 4.0959
2022-12-17 21:00 | 4.0959
2022-12-17 22:00 | 4.0959
2022-12-17 23:00 | 4.0959
2022-12-18 | 4.0959
2022-12-18 01:00 | 4.0959
2022-12-18 02:00 | 4.0959
2022-12-18 03:00 | 4.0959
2022-12-18 04:00 | 4.0959
2022-12-18 05:00 | 4.0959
2022-12-18 06:00 | 4.0959
2022-12-18 07:00 | 4.0959
2022-12-18 08:00 | 4.0959
2022-12-18 09:00 | 4.0959
2022-12-18 10:00 | 4.0959
2022-12-18 11:00 | 4.0959
2022-12-18 12:00 | 4.0959
2022-12-18 13:00 | 4.0959
2022-12-18 14:00 | 4.0959
2022-12-18 15:00 | 4.0959
2022-12-18 16:00 | 4.0959
2022-12-18 17:00 | 4.0959
2022-12-18 18:00 | 4.0959
2022-12-18 19:00 | 4.0959
2022-12-18 20:00 | 4.0959
2022-12-18 21:00 | 4.0959
2022-12-18 22:00 | 4.0959
2022-12-18 23:00 | 4.0959
2022-12-19 | 4.0959
2022-12-19 01:00 | 4.0959
2022-12-19 02:00 | 4.0959
2022-12-19 03:00 | 4.0959
2022-12-19 04:00 | 4.0959
2022-12-19 05:00 | 4.0959
2022-12-19 06:00 | 4.0959
2022-12-19 07:00 | 4.0959
2022-12-19 08:00 | 4.0959
2022-12-19 09:00 | 4.0959
2022-12-19 10:00 | 4.0959
2022-12-19 11:00 | 4.0959
2022-12-19 12:00 | 4.0959
2022-12-19 13:00 | 4.0959
2022-12-19 14:00 | 4.0959
2022-12-19 15:00 | 4.0959
2022-12-19 16:00 | 4.0959
2022-12-19 17:00 | 4.0959
2022-12-19 18:00 | 4.0959
2022-12-19 19:00 | 4.0959
2022-12-19 20:00 | 4.0959
2022-12-19 21:00 | 4.0959
2022-12-19 22:00 | 4.0959
2022-12-19 23:00 | 4.0959
2022-12-20 | 4.0959
2022-12-20 01:00 | 4.0959
2022-12-20 02:00 | 4.0959
2022-12-20 03:00 | 4.0959
2022-12-20 04:00 | 4.0959
2022-12-20 05:00 | 4.0959
2022-12-20 06:00 | 4.0959
2022-12-20 07:00 | 4.0959
2022-12-20 08:00 | 4.0959
2022-12-20 09:00 | 4.0959
2022-12-20 10:00 | 4.0959
2022-12-20 11:00 | 4.0959
2022-12-20 12:00 | 4.0959
2022-12-20 13:00 | 4.0959
2022-12-20 14:00 | 4.0959
2022-12-20 15:00 | 4.0959
2022-12-20 16:00 | 4.0959
2022-12-20 17:00 | 4.0959
2022-12-20 18:00 | 4.0959
2022-12-20 19:00 | 4.0959
2022-12-20 20:00 | 4.0959
2022-12-20 21:00 | 4.0959
2022-12-20 22:00 | 4.0959
2022-12-20 23:00 | 4.0959
2022-12-21 | 4.0959
2022-12-21 01:00 | 4.0959
2022-12-21 02:00 | 4.0959
2022-12-21 03:00 | 4.0959
2022-12-21 04:00 | 4.0959
2022-12-21 05:00 | 4.0959
2022-12-21 06:00 | 4.0959
2022-12-21 07:00 | 4.0959
2022-12-21 08:00 | 4.0959
2022-12-21 09:00 | 4.0959
2022-12-21 10:00 | 4.0959
2022-12-21 11:00 | 4.0959
2022-12-21 12:00 | 4.0959
2022-12-21 13:00 | 4.0959
2022-12-21 14:00 | 4.0959
2022-12-21 15:00 | 4.0959
2022-12-21 16:00 | 4.0959
2022-12-21 17:00 | 4.0959
2022-12-21 18:00 | 4.0959
2022-12-21 19:00 | 4.0959
2022-12-21 20:00 | 4.0959
2022-12-21 21:00 | 4.0959
2022-12-21 22:00 | 4.0959
2022-12-21 23:00 | 4.0959
2022-12-22 | 4.0959
2022-12-22 01:00 | 4.0959
2022-12-22 02:00 | 4.0959
2022-12-22 03:00 | 4.0959
2022-12-22 04:00 | 4.0959
2022-12-22 05:00 | 4.0959
2022-12-22 06:00 | 4.0959
2022-12-22 07:00 | 4.0959
2022-12-22 08:00 | 4.0959
2022-12-22 09:00 | 4.0959
2022-12-22 10:00 | 4.0959
2022-12-22 11:00 | 4.0959
2022-12-22 12:00 | 4.0959
2022-12-22 13:00 | 4.0959
2022-12-22 14:00 | 4.0959
2022-12-22 15:00 | 4.0959
2022-12-22 16:00 | 4.0959
2022-12-22 17:00 | 4.0959
2022-12-22 18:00 | 4.0959
2022-12-22 19:00 | 4.0959
2022-12-22 20:00 | 4.0959
2022-12-22 21:00 | 4.0959
2022-12-22 22:00 | 4.0959
2022-12-22 23:00 | 4.0959
2022-12-23 | 4.0959
2022-12-23 01:00 | 4.0959
2022-12-23 02:00 | 4.0959
2022-12-23 03:00 | 4.0959
2022-12-23 04:00 | 4.0959
2022-12-23 05:00 | 4.0959
2022-12-23 06:00 | 4.0959
2022-12-23 07:00 | 4.0959
2022-12-23 08:00 | 4.0959
2022-12-23 09:00 | 4.0959
2022-12-23 10:00 | 4.0959
2022-12-23 11:00 | 4.0959
2022-12-23 12:00 | 4.0959
2022-12-23 13:00 | 4.0959
2022-12-23 14:00 | 4.0959
2022-12-23 15:00 | 4.0959
2022-12-23 16:00 | 4.0959
2022-12-23 17:00 | 4.0959
2022-12-23 18:00 | 4.0959
2022-12-23 19:00 | 4.0959
2022-12-23 20:00 | 4.0959
2022-12-23 21:00 | 4.0959
2022-12-23 22:00 | 4.0959
2022-12-23 23:00 | 4.0959
2022-12-24 | 4.0959
2022-12-24 01:00 | 4.0959
2022-12-24 02:00 | 4.0959
2022-12-24 03:00 | 4.0959
2022-12-24 04:00 | 4.0959
2022-12-24 05:00 | 4.0959
2022-12-24 06:00 | 4.0959
2022-12-24 07:00 | 4.0959
2022-12-24 08:00 | 4.0959
2022-12-24 09:00 | 4.0959
2022-12-24 10:00 | 4.0959
2022-12-24 11:00 | 4.0959
2022-12-24 12:00 | 4.0959
2022-12-24 13:00 | 4.0959
2022-12-24 14:00 | 4.0959
2022-12-24 15:00 | 4.0959
2022-12-24 16:00 | 4.0959
2022-12-24 17:00 | 4.0959
2022-12-24 18:00 | 4.0959
2022-12-24 19:00 | 4.0959
2022-12-24 20:00 | 4.0959
2022-12-24 21:00 | 4.0959
2022-12-24 22:00 | 4.0959
2022-12-24 23:00 | 4.0959
2022-12-25 | 4.0959
2022-12-25 01:00 | 4.0959
2022-12-25 02:00 | 4.0959
2022-12-25 03:00 | 4.0959
2022-12-25 04:00 | 4.0959
2022-12-25 05:00 | 4.0959
2022-12-25 06:00 | 4.0959
2022-12-25 07:00 | 4.0959
2022-12-25 08:00 | 4.0959
2022-12-25 09:00 | 4.0959
2022-12-25 10:00 | 4.0959
2022-12-25 11:00 | 4.0959
2022-12-25 12:00 | 4.0959
2022-12-25 13:00 | 4.0959
2022-12-25 14:00 | 4.0959
2022-12-25 15:00 | 4.0959
2022-12-25 16:00 | 4.0959
2022-12-25 17:00 | 4.0959
2022-12-25 18:00 | 4.0959
2022-12-25 19:00 | 4.0959
2022-12-25 20:00 | 4.0959
2022-12-25 21:00 | 4.0959
2022-12-25 22:00 | 4.0959
2022-12-25 23:00 | 4.0959
2022-12-26 | 4.0959
2022-12-26 01:00 | 4.0959
2022-12-26 02:00 | 4.0959
2022-12-26 03:00 | 4.0959
2022-12-26 04:00 | 4.0959
2022-12-26 05:00 | 4.0959
2022-12-26 06:00 | 4.0959
2022-12-26 07:00 | 4.0959
2022-12-26 08:00 | 4.0959
2022-12-26 09:00 | 4.0959
2022-12-26 10:00 | 4.0959
2022-12-26 11:00 | 4.0959
2022-12-26 12:00 | 4.0959
2022-12-26 13:00 | 4.0959
2022-12-26 14:00 | 4.0959
2022-12-26 15:00 | 4.0959
2022-12-26 16:00 | 4.0959
2022-12-26 17:00 | 4.0959
2022-12-26 18:00 | 4.0959
2022-12-26 19:00 | 4.0959
2022-12-26 20:00 | 4.0959
2022-12-26 21:00 | 4.0959
2022-12-26 22:00 | 4.0959
2022-12-26 23:00 | 4.0959
2022-12-27 | 4.0959
2022-12-27 01:00 | 4.0959
2022-12-27 02:00 | 4.0959
2022-12-27 03:00 | 4.0959
2022-12-27 04:00 | 4.0959
2022-12-27 05:00 | 4.0959
2022-12-27 06:00 | 4.0959
2022-12-27 07:00 | 4.0959
2022-12-27 08:00 | 4.0959
2022-12-27 09:00 | 4.0959
2022-12-27 10:00 | 4.0959
2022-12-27 11:00 | 4.0959
2022-12-27 12:00 | 4.0959
2022-12-27 13:00 | 4.0959
2022-12-27 14:00 | 4.0959
2022-12-27 15:00 | 4.0959
2022-12-27 16:00 | 4.0959
2022-12-27 17:00 | 4.0959
2022-12-27 18:00 | 4.0959
2022-12-27 19:00 | 4.0959
2022-12-27 20:00 | 4.0959
2022-12-27 21:00 | 4.0959
2022-12-27 22:00 | 4.0959
2022-12-27 23:00 | 4.0959
2022-12-28 | 4.0959
2022-12-28 01:00 | 4.0959
2022-12-28 02:00 | 4.0959
2022-12-28 03:00 | 4.0959
2022-12-28 04:00 | 4.0959
2022-12-28 05:00 | 4.0959
2022-12-28 06:00 | 4.0959
2022-12-28 07:00 | 4.0959
2022-12-28 08:00 | 4.0959
2022-12-28 09:00 | 4.0959
2022-12-28 10:00 | 4.0959
2022-12-28 11:00 | 4.0959
2022-12-28 12:00 | 4.0959
2022-12-28 13:00 | 4.0959
2022-12-28 14:00 | 4.0959
2022-12-28 15:00 | 4.0959
2022-12-28 16:00 | 4.0959
2022-12-28 17:00 | 4.0959
2022-12-28 18:00 | 4.0959
2022-12-28 19:00 | 4.0959
2022-12-28 20:00 | 4.0959
2022-12-28 21:00 | 4.0959
2022-12-28 22:00 | 4.0959
2022-12-28 23:00 | 4.0959
2022-12-29 | 4.0959
2022-12-29 01:00 | 4.0959
2022-12-29 02:00 | 4.0959
2022-12-29 03:00 | 4.0959
2022-12-29 04:00 | 4.0959
2022-12-29 05:00 | 4.0959
2022-12-29 06:00 | 4.0959
2022-12-29 07:00 | 4.0959
2022-12-29 08:00 | 4.0959
2022-12-29 09:00 | 4.0959
2022-12-29 10:00 | 4.0959
2022-12-29 11:00 | 4.0959
2022-12-29 12:00 | 4.0959
2022-12-29 13:00 | 4.0959
2022-12-29 14:00 | 4.0959
2022-12-29 15:00 | 4.0959
2022-12-29 16:00 | 4.0959
2022-12-29 17:00 | 4.0959
2022-12-29 18:00 | 4.0959
2022-12-29 19:00 | 4.0959
2022-12-29 20:00 | 4.0959
2022-12-29 21:00 | 4.0959
2022-12-29 22:00 | 4.0959
2022-12-29 23:00 | 4.0959
2022-12-30 | 4.0959
2022-12-30 01:00 | 4.0959
2022-12-30 02:00 | 4.0959
2022-12-30 03:00 | 4.0959
2022-12-30 04:00 | 4.0959
2022-12-30 05:00 | 4.0959
2022-12-30 06:00 | 4.0959
2022-12-30 07:00 | 4.0959
2022-12-30 08:00 | 4.0959
2022-12-30 09:00 | 4.0959
2022-12-30 10:00 | 4.0959
2022-12-30 11:00 | 4.0959
2022-12-30 12:00 | 4.0959
2022-12-30 13:00 | 4.0959
2022-12-30 14:00 | 4.0959
2022-12-30 15:00 | 4.0959
2022-12-30 16:00 | 4.0959
2022-12-30 17:00 | 4.0959
2022-12-30 18:00 | 4.0959
2022-12-30 19:00 | 4.0959
2022-12-30 20:00 | 4.0959
2022-12-30 21:00 | 4.0959
2022-12-30 22:00 | 4.0959
2022-12-30 23:00 | 4.0959
2022-12-31 | 4.0959
2022-12-31 01:00 | 4.0959
2022-12-31 02:00 | 4.0959
2022-12-31 03:00 | 4.0959
2022-12-31 04:00 | 4.0959
2022-12-31 05:00 | 4.0959
2022-12-31 06:00 | 4.0959
2022-12-31 07:00 | 4.0959
2022-12-31 08:00 | 4.0959
2022-12-31 09:00 | 4.0959
2022-12-31 10:00 | 4.0959
2022-12-31 11:00 | 4.0959
2022-12-31 12:00 | 4.0959
2022-12-31 13:00 | 4.0959
2022-12-31 14:00 | 4.0959
2022-12-31 15:00 | 4.0959
2022-12-31 16:00 | 4.0959
2022-12-31 17:00 | 4.0959
2022-12-31 18:00 | 4.0959
2022-12-31 19:00 | 4.0959
2022-12-31 20:00 | 4.0959
2022-12-31 21:00 | 4.0959
2022-12-31 22:00 | 4.0959
2022-12-31 23:00 | 4.0959

## Step 1.3 OAT Data
Datetime | OAT (F)
2022-01-01 | 49
2022-01-01 01:00 | 49
2022-01-01 02:00 | 49
2022-01-01 03:00 | 49
2022-01-01 04:00 | 49
2022-01-01 05:00 | 50
2022-01-01 06:00 | 50
2022-01-01 07:00 | 50
2022-01-01 08:00 | 51
2022-01-01 09:00 | 51
2022-01-01 10:00 | 50
2022-01-01 11:00 | 50
2022-01-01 12:00 | 51
2022-01-01 13:00 | 51
2022-01-01 14:00 | 52
2022-01-01 15:00 | 53
2022-01-01 16:00 | 52
2022-01-01 17:00 | 51
2022-01-01 18:00 | 52
2022-01-01 19:00 | 51
2022-01-01 20:00 | 52
2022-01-01 21:00 | 52
2022-01-01 22:00 | 52
2022-01-01 23:00 | 53
2022-01-02 | 53
2022-01-02 01:00 | 53
2022-01-02 02:00 | 53
2022-01-02 03:00 | 53
2022-01-02 04:00 | 51
2022-01-02 05:00 | 52
2022-01-02 06:00 | 52
2022-01-02 07:00 | 51
2022-01-02 08:00 | 51
2022-01-02 09:00 | 52
2022-01-02 10:00 | 52
2022-01-02 11:00 | 53
2022-01-02 12:00 | 53
2022-01-02 13:00 | 54
2022-01-02 14:00 | 57
2022-01-02 15:00 | 58
2022-01-02 16:00 | 53
2022-01-02 17:00 | 50
2022-01-02 18:00 | 50
2022-01-02 19:00 | 48
2022-01-02 20:00 | 44
2022-01-02 21:00 | 40
2022-01-02 22:00 | 39
2022-01-02 23:00 | 39
2022-01-03 | 39
2022-01-03 01:00 | 38
2022-01-03 02:00 | 38
2022-01-03 03:00 | 37
2022-01-03 04:00 | 35
2022-01-03 05:00 | 34
2022-01-03 06:00 | 33
2022-01-03 07:00 | 32
2022-01-03 08:00 | 31
2022-01-03 09:00 | 31
2022-01-03 10:00 | 30
2022-01-03 11:00 | 30
2022-01-03 12:00 | 29
2022-01-03 13:00 | 29
2022-01-03 14:00 | 30
2022-01-03 15:00 | 29
2022-01-03 16:00 | 29
2022-01-03 17:00 | 27
2022-01-03 18:00 | 27
2022-01-03 19:00 | 27
2022-01-03 20:00 | 26
2022-01-03 21:00 | 25
2022-01-03 22:00 | 24
2022-01-03 23:00 | 23
2022-01-04 | 22
2022-01-04 01:00 | 22
2022-01-04 02:00 | 22
2022-01-04 03:00 | 21
2022-01-04 04:00 | 21
2022-01-04 05:00 | 20
2022-01-04 06:00 | 20
2022-01-04 07:00 | 20
2022-01-04 08:00 | 20
2022-01-04 09:00 | 23
2022-01-04 10:00 | 25
2022-01-04 11:00 | 28
2022-01-04 12:00 | 29
2022-01-04 13:00 | 31
2022-01-04 14:00 | 32
2022-01-04 15:00 | 32
2022-01-04 16:00 | 32
2022-01-04 17:00 | 29
2022-01-04 18:00 | 31
2022-01-04 19:00 | 32
2022-01-04 20:00 | 32
2022-01-04 21:00 | 32
2022-01-04 22:00 | 32
2022-01-04 23:00 | 31
2022-01-05 | 32
2022-01-05 01:00 | 32
2022-01-05 02:00 | 30
2022-01-05 03:00 | 32
2022-01-05 04:00 | 34
2022-01-05 05:00 | 34
2022-01-05 06:00 | 34
2022-01-05 07:00 | 34
2022-01-05 08:00 | 35
2022-01-05 09:00 | 37
2022-01-05 10:00 | 39
2022-01-05 11:00 | 40
2022-01-05 12:00 | 40
2022-01-05 13:00 | 41
2022-01-05 14:00 | 43
2022-01-05 15:00 | 45
2022-01-05 16:00 | 46
2022-01-05 17:00 | 45
2022-01-05 18:00 | 45
2022-01-05 19:00 | 45
2022-01-05 20:00 | 43
2022-01-05 21:00 | 43
2022-01-05 22:00 | 42
2022-01-05 23:00 | 42
2022-01-06 | 41
2022-01-06 01:00 | 40
2022-01-06 02:00 | 39
2022-01-06 03:00 | 38
2022-01-06 04:00 | 36
2022-01-06 05:00 | 35
2022-01-06 06:00 | 37
2022-01-06 07:00 | 39
2022-01-06 08:00 | 38
2022-01-06 09:00 | 37
2022-01-06 10:00 | 37
2022-01-06 11:00 | 38
2022-01-06 12:00 | 38
2022-01-06 13:00 | 39
2022-01-06 14:00 | 39
2022-01-06 15:00 | 40
2022-01-06 16:00 | 37
2022-01-06 17:00 | 36
2022-01-06 18:00 | 36
2022-01-06 19:00 | 36
2022-01-06 20:00 | 35
2022-01-06 21:00 | 35
2022-01-06 22:00 | 35
2022-01-06 23:00 | 34
2022-01-07 | 35
2022-01-07 01:00 | 34
2022-01-07 02:00 | 32
2022-01-07 03:00 | 30
2022-01-07 04:00 | 30
2022-01-07 05:00 | 30
2022-01-07 06:00 | 29
2022-01-07 07:00 | 29
2022-01-07 08:00 | 29
2022-01-07 09:00 | 29
2022-01-07 10:00 | 30
2022-01-07 11:00 | 31
2022-01-07 12:00 | 33
2022-01-07 13:00 | 33
2022-01-07 14:00 | 33
2022-01-07 15:00 | 33
2022-01-07 16:00 | 33
2022-01-07 17:00 | 31
2022-01-07 18:00 | 30
2022-01-07 19:00 | 29
2022-01-07 20:00 | 28
2022-01-07 21:00 | 27
2022-01-07 22:00 | 27
2022-01-07 23:00 | 26
2022-01-08 | 26
2022-01-08 01:00 | 25
2022-01-08 02:00 | 24
2022-01-08 03:00 | 23
2022-01-08 04:00 | 22
2022-01-08 05:00 | 22
2022-01-08 06:00 | 22
2022-01-08 07:00 | 21
2022-01-08 08:00 | 21
2022-01-08 09:00 | 22
2022-01-08 10:00 | 23
2022-01-08 11:00 | 25
2022-01-08 12:00 | 26
2022-01-08 13:00 | 27
2022-01-08 14:00 | 29
2022-01-08 15:00 | 30
2022-01-08 16:00 | 31
2022-01-08 17:00 | 28
2022-01-08 18:00 | 23
2022-01-08 19:00 | 28
2022-01-08 20:00 | 25
2022-01-08 21:00 | 28
2022-01-08 22:00 | 28
2022-01-08 23:00 | 29
2022-01-09 | 30
2022-01-09 01:00 | 30
2022-01-09 02:00 | 29
2022-01-09 03:00 | 30
2022-01-09 04:00 | 31
2022-01-09 05:00 | 33
2022-01-09 06:00 | 34
2022-01-09 07:00 | 35
2022-01-09 08:00 | 35
2022-01-09 09:00 | 36
2022-01-09 10:00 | 37
2022-01-09 11:00 | 37
2022-01-09 12:00 | 39
2022-01-09 13:00 | 40
2022-01-09 14:00 | 41
2022-01-09 15:00 | 41
2022-01-09 16:00 | 40
2022-01-09 17:00 | 39
2022-01-09 18:00 | 39
2022-01-09 19:00 | 39
2022-01-09 20:00 | 39
2022-01-09 21:00 | 39
2022-01-09 22:00 | 39
2022-01-09 23:00 | 39
2022-01-10 | 40
2022-01-10 01:00 | 40
2022-01-10 02:00 | 40
2022-01-10 03:00 | 39
2022-01-10 04:00 | 36
2022-01-10 05:00 | 34
2022-01-10 06:00 | 32
2022-01-10 07:00 | 30
2022-01-10 08:00 | 29
2022-01-10 09:00 | 29
2022-01-10 10:00 | 30
2022-01-10 11:00 | 31
2022-01-10 12:00 | 32
2022-01-10 13:00 | 31
2022-01-10 14:00 | 32
2022-01-10 15:00 | 30
2022-01-10 16:00 | 29
2022-01-10 17:00 | 27
2022-01-10 18:00 | 27
2022-01-10 19:00 | 27
2022-01-10 20:00 | 27
2022-01-10 21:00 | 27
2022-01-10 22:00 | 26
2022-01-10 23:00 | 26
2022-01-11 | 25
2022-01-11 01:00 | 24
2022-01-11 02:00 | 22
2022-01-11 03:00 | 20
2022-01-11 04:00 | 19
2022-01-11 05:00 | 19
2022-01-11 06:00 | 18
2022-01-11 07:00 | 17
2022-01-11 08:00 | 16
2022-01-11 09:00 | 17
2022-01-11 10:00 | 18
2022-01-11 11:00 | 18
2022-01-11 12:00 | 19
2022-01-11 13:00 | 20
2022-01-11 14:00 | 21
2022-01-11 15:00 | 21
2022-01-11 16:00 | 20
2022-01-11 17:00 | 19
2022-01-11 18:00 | 19
2022-01-11 19:00 | 18
2022-01-11 20:00 | 17
2022-01-11 21:00 | 17
2022-01-11 22:00 | 16
2022-01-11 23:00 | 15
2022-01-12 | 15
2022-01-12 01:00 | 18
2022-01-12 02:00 | 22
2022-01-12 03:00 | 23
2022-01-12 04:00 | 23
2022-01-12 05:00 | 25
2022-01-12 06:00 | 26
2022-01-12 07:00 | 28
2022-01-12 08:00 | 29
2022-01-12 09:00 | 32
2022-01-12 10:00 | 34
2022-01-12 11:00 | 37
2022-01-12 12:00 | 38
2022-01-12 13:00 | 40
2022-01-12 14:00 | 41
2022-01-12 15:00 | 40
2022-01-12 16:00 | 40
2022-01-12 17:00 | 37
2022-01-12 18:00 | 35
2022-01-12 19:00 | 35
2022-01-12 20:00 | 35
2022-01-12 21:00 | 35
2022-01-12 22:00 | 33
2022-01-12 23:00 | 32
2022-01-13 | 33
2022-01-13 01:00 | 34
2022-01-13 02:00 | 29
2022-01-13 03:00 | 32
2022-01-13 04:00 | 30
2022-01-13 05:00 | 30
2022-01-13 06:00 | 32
2022-01-13 07:00 | 30
2022-01-13 08:00 | 35
2022-01-13 09:00 | 38
2022-01-13 10:00 | 42
2022-01-13 11:00 | 46
2022-01-13 12:00 | 47
2022-01-13 13:00 | 48
2022-01-13 14:00 | 47
2022-01-13 15:00 | 47
2022-01-13 16:00 | 45
2022-01-13 17:00 | 43
2022-01-13 18:00 | 41
2022-01-13 19:00 | 40
2022-01-13 20:00 | 39
2022-01-13 21:00 | 37
2022-01-13 22:00 | 39
2022-01-13 23:00 | 40
2022-01-14 | 39
2022-01-14 01:00 | 39
2022-01-14 02:00 | 40
2022-01-14 03:00 | 40
2022-01-14 04:00 | 40
2022-01-14 05:00 | 40
2022-01-14 06:00 | 40
2022-01-14 07:00 | 40
2022-01-14 08:00 | 40
2022-01-14 09:00 | 40
2022-01-14 10:00 | 42
2022-01-14 11:00 | 44
2022-01-14 12:00 | 44
2022-01-14 13:00 | 43
2022-01-14 14:00 | 42
2022-01-14 15:00 | 41
2022-01-14 16:00 | 39
2022-01-14 17:00 | 36
2022-01-14 18:00 | 34
2022-01-14 19:00 | 32
2022-01-14 20:00 | 31
2022-01-14 21:00 | 29
2022-01-14 22:00 | 26
2022-01-14 23:00 | 24
2022-01-15 | 22
2022-01-15 01:00 | 19
2022-01-15 02:00 | 18
2022-01-15 03:00 | 17
2022-01-15 04:00 | 16
2022-01-15 05:00 | 15
2022-01-15 06:00 | 13
2022-01-15 07:00 | 12
2022-01-15 08:00 | 12
2022-01-15 09:00 | 13
2022-01-15 10:00 | 14
2022-01-15 11:00 | 15
2022-01-15 12:00 | 17
2022-01-15 13:00 | 18
2022-01-15 14:00 | 18
2022-01-15 15:00 | 19
2022-01-15 16:00 | 19
2022-01-15 17:00 | 18
2022-01-15 18:00 | 18
2022-01-15 19:00 | 18
2022-01-15 20:00 | 16
2022-01-15 21:00 | 16
2022-01-15 22:00 | 14
2022-01-15 23:00 | 13
2022-01-16 | 13
2022-01-16 01:00 | 12
2022-01-16 02:00 | 12
2022-01-16 03:00 | 11
2022-01-16 04:00 | 11
2022-01-16 05:00 | 10
2022-01-16 06:00 | 10
2022-01-16 07:00 | 10
2022-01-16 08:00 | 11
2022-01-16 09:00 | 14
2022-01-16 10:00 | 19
2022-01-16 11:00 | 23
2022-01-16 12:00 | 26
2022-01-16 13:00 | 28
2022-01-16 14:00 | 30
2022-01-16 15:00 | 28
2022-01-16 16:00 | 28
2022-01-16 17:00 | 29
2022-01-16 18:00 | 31
2022-01-16 19:00 | 33
2022-01-16 20:00 | 33
2022-01-16 21:00 | 37
2022-01-16 22:00 | 40
2022-01-16 23:00 | 41
2022-01-17 | 42
2022-01-17 01:00 | 43
2022-01-17 02:00 | 44
2022-01-17 03:00 | 45
2022-01-17 04:00 | 45
2022-01-17 05:00 | 45
2022-01-17 06:00 | 45
2022-01-17 07:00 | 45
2022-01-17 08:00 | 42
2022-01-17 09:00 | 39
2022-01-17 10:00 | 41
2022-01-17 11:00 | 40
2022-01-17 12:00 | 39
2022-01-17 13:00 | 37
2022-01-17 14:00 | 37
2022-01-17 15:00 | 37
2022-01-17 16:00 | 37
2022-01-17 17:00 | 36
2022-01-17 18:00 | 35
2022-01-17 19:00 | 36
2022-01-17 20:00 | 37
2022-01-17 21:00 | 36
2022-01-17 22:00 | 36
2022-01-17 23:00 | 35
2022-01-18 | 35
2022-01-18 01:00 | 34
2022-01-18 02:00 | 34
2022-01-18 03:00 | 32
2022-01-18 04:00 | 30
2022-01-18 05:00 | 31
2022-01-18 06:00 | 31
2022-01-18 07:00 | 31
2022-01-18 08:00 | 32
2022-01-18 09:00 | 34
2022-01-18 10:00 | 34
2022-01-18 11:00 | 38
2022-01-18 12:00 | 37
2022-01-18 13:00 | 38
2022-01-18 14:00 | 38
2022-01-18 15:00 | 38
2022-01-18 16:00 | 36
2022-01-18 17:00 | 34
2022-01-18 18:00 | 34
2022-01-18 19:00 | 32
2022-01-18 20:00 | 31
2022-01-18 21:00 | 30
2022-01-18 22:00 | 28
2022-01-18 23:00 | 30
2022-01-19 | 26
2022-01-19 01:00 | 25
2022-01-19 02:00 | 25
2022-01-19 03:00 | 24
2022-01-19 04:00 | 27
2022-01-19 05:00 | 30
2022-01-19 06:00 | 33
2022-01-19 07:00 | 35
2022-01-19 08:00 | 38
2022-01-19 09:00 | 38
2022-01-19 10:00 | 41
2022-01-19 11:00 | 41
2022-01-19 12:00 | 43
2022-01-19 13:00 | 48
2022-01-19 14:00 | 49
2022-01-19 15:00 | 47
2022-01-19 16:00 | 45
2022-01-19 17:00 | 43
2022-01-19 18:00 | 42
2022-01-19 19:00 | 44
2022-01-19 20:00 | 43
2022-01-19 21:00 | 42
2022-01-19 22:00 | 42
2022-01-19 23:00 | 44
2022-01-20 | 44
2022-01-20 01:00 | 44
2022-01-20 02:00 | 42
2022-01-20 03:00 | 41
2022-01-20 04:00 | 40
2022-01-20 05:00 | 40
2022-01-20 06:00 | 39
2022-01-20 07:00 | 38
2022-01-20 08:00 | 40
2022-01-20 09:00 | 37
2022-01-20 10:00 | 35
2022-01-20 11:00 | 34
2022-01-20 12:00 | 33
2022-01-20 13:00 | 35
2022-01-20 14:00 | 35
2022-01-20 15:00 | 35
2022-01-20 16:00 | 34
2022-01-20 17:00 | 33
2022-01-20 18:00 | 33
2022-01-20 19:00 | 31
2022-01-20 20:00 | 28
2022-01-20 21:00 | 27
2022-01-20 22:00 | 25
2022-01-20 23:00 | 23
2022-01-21 | 22
2022-01-21 01:00 | 20
2022-01-21 02:00 | 19
2022-01-21 03:00 | 18
2022-01-21 04:00 | 17
2022-01-21 05:00 | 16
2022-01-21 06:00 | 15
2022-01-21 07:00 | 14
2022-01-21 08:00 | 14
2022-01-21 09:00 | 15
2022-01-21 10:00 | 16
2022-01-21 11:00 | 18
2022-01-21 12:00 | 21
2022-01-21 13:00 | 22
2022-01-21 14:00 | 23
2022-01-21 15:00 | 23
2022-01-21 16:00 | 23
2022-01-21 17:00 | 22
2022-01-21 18:00 | 22
2022-01-21 19:00 | 21
2022-01-21 20:00 | 20
2022-01-21 21:00 | 20
2022-01-21 22:00 | 20
2022-01-21 23:00 | 20
2022-01-22 | 20
2022-01-22 01:00 | 19
2022-01-22 02:00 | 18
2022-01-22 03:00 | 17
2022-01-22 04:00 | 16
2022-01-22 05:00 | 16
2022-01-22 06:00 | 15
2022-01-22 07:00 | 15
2022-01-22 08:00 | 15
2022-01-22 09:00 | 18
2022-01-22 10:00 | 22
2022-01-22 11:00 | 25
2022-01-22 12:00 | 27
2022-01-22 13:00 | 29
2022-01-22 14:00 | 31
2022-01-22 15:00 | 32
2022-01-22 16:00 | 31
2022-01-22 17:00 | 26
2022-01-22 18:00 | 24
2022-01-22 19:00 | 24
2022-01-22 20:00 | 23
2022-01-22 21:00 | 24
2022-01-22 22:00 | 27
2022-01-22 23:00 | 26
2022-01-23 | 26
2022-01-23 01:00 | 26
2022-01-23 02:00 | 27
2022-01-23 03:00 | 26
2022-01-23 04:00 | 26
2022-01-23 05:00 | 25
2022-01-23 06:00 | 25
2022-01-23 07:00 | 25
2022-01-23 08:00 | 26
2022-01-23 09:00 | 28
2022-01-23 10:00 | 30
2022-01-23 11:00 | 33
2022-01-23 12:00 | 34
2022-01-23 13:00 | 34
2022-01-23 14:00 | 35
2022-01-23 15:00 | 36
2022-01-23 16:00 | 36
2022-01-23 17:00 | 34
2022-01-23 18:00 | 34
2022-01-23 19:00 | 34
2022-01-23 20:00 | 32
2022-01-23 21:00 | 32
2022-01-23 22:00 | 31
2022-01-23 23:00 | 30
2022-01-24 | 30
2022-01-24 01:00 | 30
2022-01-24 02:00 | 30
2022-01-24 03:00 | 30
2022-01-24 04:00 | 30
2022-01-24 05:00 | 31
2022-01-24 06:00 | 32
2022-01-24 07:00 | 31
2022-01-24 08:00 | 29
2022-01-24 09:00 | 29
2022-01-24 10:00 | 29
2022-01-24 11:00 | 31
2022-01-24 12:00 | 31
2022-01-24 13:00 | 32
2022-01-24 14:00 | 33
2022-01-24 15:00 | 31
2022-01-24 16:00 | 32
2022-01-24 17:00 | 30
2022-01-24 18:00 | 31
2022-01-24 19:00 | 32
2022-01-24 20:00 | 34
2022-01-24 21:00 | 35
2022-01-24 22:00 | 35
2022-01-24 23:00 | 37
2022-01-25 | 38
2022-01-25 01:00 | 39
2022-01-25 02:00 | 40
2022-01-25 03:00 | 39
2022-01-25 04:00 | 38
2022-01-25 05:00 | 37
2022-01-25 06:00 | 36
2022-01-25 07:00 | 32
2022-01-25 08:00 | 34
2022-01-25 09:00 | 38
2022-01-25 10:00 | 40
2022-01-25 11:00 | 40
2022-01-25 12:00 | 39
2022-01-25 13:00 | 40
2022-01-25 14:00 | 42
2022-01-25 15:00 | 43
2022-01-25 16:00 | 43
2022-01-25 17:00 | 39
2022-01-25 18:00 | 38
2022-01-25 19:00 | 35
2022-01-25 20:00 | 34
2022-01-25 21:00 | 33
2022-01-25 22:00 | 32
2022-01-25 23:00 | 30
2022-01-26 | 29
2022-01-26 01:00 | 28
2022-01-26 02:00 | 26
2022-01-26 03:00 | 25
2022-01-26 04:00 | 24
2022-01-26 05:00 | 23
2022-01-26 06:00 | 22
2022-01-26 07:00 | 22
2022-01-26 08:00 | 22
2022-01-26 09:00 | 24
2022-01-26 10:00 | 25
2022-01-26 11:00 | 26
2022-01-26 12:00 | 27
2022-01-26 13:00 | 29
2022-01-26 14:00 | 28
2022-01-26 15:00 | 28
2022-01-26 16:00 | 28
2022-01-26 17:00 | 26
2022-01-26 18:00 | 25
2022-01-26 19:00 | 24
2022-01-26 20:00 | 23
2022-01-26 21:00 | 22
2022-01-26 22:00 | 20
2022-01-26 23:00 | 20
2022-01-27 | 18
2022-01-27 01:00 | 17
2022-01-27 02:00 | 16
2022-01-27 03:00 | 16
2022-01-27 04:00 | 16
2022-01-27 05:00 | 16
2022-01-27 06:00 | 16
2022-01-27 07:00 | 16
2022-01-27 08:00 | 16
2022-01-27 09:00 | 21
2022-01-27 10:00 | 24
2022-01-27 11:00 | 27
2022-01-27 12:00 | 27
2022-01-27 13:00 | 29
2022-01-27 14:00 | 30
2022-01-27 15:00 | 31
2022-01-27 16:00 | 32
2022-01-27 17:00 | 30
2022-01-27 18:00 | 30
2022-01-27 19:00 | 29
2022-01-27 20:00 | 29
2022-01-27 21:00 | 30
2022-01-27 22:00 | 29
2022-01-27 23:00 | 30
2022-01-28 | 30
2022-01-28 01:00 | 30
2022-01-28 02:00 | 30
2022-01-28 03:00 | 31
2022-01-28 04:00 | 31
2022-01-28 05:00 | 31
2022-01-28 06:00 | 31
2022-01-28 07:00 | 31
2022-01-28 08:00 | 31
2022-01-28 09:00 | 29
2022-01-28 10:00 | 29
2022-01-28 11:00 | 30
2022-01-28 12:00 | 31
2022-01-28 13:00 | 32
2022-01-28 14:00 | 34
2022-01-28 15:00 | 34
2022-01-28 16:00 | 34
2022-01-28 17:00 | 33
2022-01-28 18:00 | 32
2022-01-28 19:00 | 31
2022-01-28 20:00 | 31
2022-01-28 21:00 | 31
2022-01-28 22:00 | 30
2022-01-28 23:00 | 30
2022-01-29 | 30
2022-01-29 01:00 | 29
2022-01-29 02:00 | 29
2022-01-29 03:00 | 26
2022-01-29 04:00 | 24
2022-01-29 05:00 | 23
2022-01-29 06:00 | 21
2022-01-29 07:00 | 20
2022-01-29 08:00 | 18
2022-01-29 09:00 | 16
2022-01-29 10:00 | 15
2022-01-29 11:00 | 16
2022-01-29 12:00 | 15
2022-01-29 13:00 | 16
2022-01-29 14:00 | 18
2022-01-29 15:00 | 19
2022-01-29 16:00 | 19
2022-01-29 17:00 | 19
2022-01-29 18:00 | 19
2022-01-29 19:00 | 18
2022-01-29 20:00 | 18
2022-01-29 21:00 | 16
2022-01-29 22:00 | 14
2022-01-29 23:00 | 14
2022-01-30 | 12
2022-01-30 01:00 | 12
2022-01-30 02:00 | 12
2022-01-30 03:00 | 13
2022-01-30 04:00 | 13
2022-01-30 05:00 | 13
2022-01-30 06:00 | 13
2022-01-30 07:00 | 14
2022-01-30 08:00 | 13
2022-01-30 09:00 | 15
2022-01-30 10:00 | 17
2022-01-30 11:00 | 19
2022-01-30 12:00 | 20
2022-01-30 13:00 | 22
2022-01-30 14:00 | 23
2022-01-30 15:00 | 24
2022-01-30 16:00 | 24
2022-01-30 17:00 | 22
2022-01-30 18:00 | 22
2022-01-30 19:00 | 23
2022-01-30 20:00 | 24
2022-01-30 21:00 | 24
2022-01-30 22:00 | 24
2022-01-30 23:00 | 24
2022-01-31 | 24
2022-01-31 01:00 | 22
2022-01-31 02:00 | 22
2022-01-31 03:00 | 21
2022-01-31 04:00 | 20
2022-01-31 05:00 | 17
2022-01-31 06:00 | 18
2022-01-31 07:00 | 18
2022-01-31 08:00 | 18
2022-01-31 09:00 | 21
2022-01-31 10:00 | 24
2022-01-31 11:00 | 27
2022-01-31 12:00 | 29
2022-01-31 13:00 | 28
2022-01-31 14:00 | 29
2022-01-31 15:00 | 30
2022-01-31 16:00 | 30
2022-01-31 17:00 | 28
2022-01-31 18:00 | 26
2022-01-31 19:00 | 24
2022-01-31 20:00 | 23
2022-01-31 21:00 | 23
2022-01-31 22:00 | 22
2022-01-31 23:00 | 22
2022-02-01 | 21
2022-02-01 01:00 | 20
2022-02-01 02:00 | 20
2022-02-01 03:00 | 21
2022-02-01 04:00 | 20
2022-02-01 05:00 | 21
2022-02-01 06:00 | 20
2022-02-01 07:00 | 22
2022-02-01 08:00 | 23
2022-02-01 09:00 | 26
2022-02-01 10:00 | 30
2022-02-01 11:00 | 32
2022-02-01 12:00 | 34
2022-02-01 13:00 | 36
2022-02-01 14:00 | 37
2022-02-01 15:00 | 37
2022-02-01 16:00 | 37
2022-02-01 17:00 | 35
2022-02-01 18:00 | 34
2022-02-01 19:00 | 33
2022-02-01 20:00 | 33
2022-02-01 21:00 | 33
2022-02-01 22:00 | 34
2022-02-01 23:00 | 34
2022-02-02 | 32
2022-02-02 01:00 | 29
2022-02-02 02:00 | 29
2022-02-02 03:00 | 30
2022-02-02 04:00 | 31
2022-02-02 05:00 | 31
2022-02-02 06:00 | 30
2022-02-02 07:00 | 31
2022-02-02 08:00 | 30
2022-02-02 09:00 | 35
2022-02-02 10:00 | 38
2022-02-02 11:00 | 42
2022-02-02 12:00 | 43
2022-02-02 13:00 | 43
2022-02-02 14:00 | 44
2022-02-02 15:00 | 44
2022-02-02 16:00 | 43
2022-02-02 17:00 | 38
2022-02-02 18:00 | 37
2022-02-02 19:00 | 38
2022-02-02 20:00 | 38
2022-02-02 21:00 | 38
2022-02-02 22:00 | 38
2022-02-02 23:00 | 38
2022-02-03 | 39
2022-02-03 01:00 | 38
2022-02-03 02:00 | 39
2022-02-03 03:00 | 39
2022-02-03 04:00 | 37
2022-02-03 05:00 | 38
2022-02-03 06:00 | 38
2022-02-03 07:00 | 39
2022-02-03 08:00 | 40
2022-02-03 09:00 | 41
2022-02-03 10:00 | 42
2022-02-03 11:00 | 42
2022-02-03 12:00 | 43
2022-02-03 13:00 | 43
2022-02-03 14:00 | 43
2022-02-03 15:00 | 44
2022-02-03 16:00 | 45
2022-02-03 17:00 | 44
2022-02-03 18:00 | 44
2022-02-03 19:00 | 44
2022-02-03 20:00 | 44
2022-02-03 21:00 | 45
2022-02-03 22:00 | 46
2022-02-03 23:00 | 46
2022-02-04 | 45
2022-02-04 01:00 | 45
2022-02-04 02:00 | 49
2022-02-04 03:00 | 48
2022-02-04 04:00 | 47
2022-02-04 05:00 | 48
2022-02-04 06:00 | 47
2022-02-04 07:00 | 48
2022-02-04 08:00 | 48
2022-02-04 09:00 | 37
2022-02-04 10:00 | 37
2022-02-04 11:00 | 38
2022-02-04 12:00 | 36
2022-02-04 13:00 | 36
2022-02-04 14:00 | 34
2022-02-04 15:00 | 33
2022-02-04 16:00 | 32
2022-02-04 17:00 | 31
2022-02-04 18:00 | 31
2022-02-04 19:00 | 31
2022-02-04 20:00 | 30
2022-02-04 21:00 | 29
2022-02-04 22:00 | 28
2022-02-04 23:00 | 28
2022-02-05 | 27
2022-02-05 01:00 | 27
2022-02-05 02:00 | 26
2022-02-05 03:00 | 26
2022-02-05 04:00 | 26
2022-02-05 05:00 | 25
2022-02-05 06:00 | 24
2022-02-05 07:00 | 23
2022-02-05 08:00 | 22
2022-02-05 09:00 | 24
2022-02-05 10:00 | 25
2022-02-05 11:00 | 27
2022-02-05 12:00 | 28
2022-02-05 13:00 | 29
2022-02-05 14:00 | 28
2022-02-05 15:00 | 28
2022-02-05 16:00 | 27
2022-02-05 17:00 | 26
2022-02-05 18:00 | 24
2022-02-05 19:00 | 24
2022-02-05 20:00 | 23
2022-02-05 21:00 | 22
2022-02-05 22:00 | 21
2022-02-05 23:00 | 20
2022-02-06 | 19
2022-02-06 01:00 | 19
2022-02-06 02:00 | 18
2022-02-06 03:00 | 18
2022-02-06 04:00 | 17
2022-02-06 05:00 | 17
2022-02-06 06:00 | 16
2022-02-06 07:00 | 16
2022-02-06 08:00 | 19
2022-02-06 09:00 | 21
2022-02-06 10:00 | 23
2022-02-06 11:00 | 24
2022-02-06 12:00 | 26
2022-02-06 13:00 | 28
2022-02-06 14:00 | 29
2022-02-06 15:00 | 30
2022-02-06 16:00 | 30
2022-02-06 17:00 | 29
2022-02-06 18:00 | 27
2022-02-06 19:00 | 26
2022-02-06 20:00 | 27
2022-02-06 21:00 | 27
2022-02-06 22:00 | 28
2022-02-06 23:00 | 29
2022-02-07 | 31
2022-02-07 01:00 | 31
2022-02-07 02:00 | 31
2022-02-07 03:00 | 32
2022-02-07 04:00 | 32
2022-02-07 05:00 | 32
2022-02-07 06:00 | 33
2022-02-07 07:00 | 33
2022-02-07 08:00 | 33
2022-02-07 09:00 | 34
2022-02-07 10:00 | 35
2022-02-07 11:00 | 36
2022-02-07 12:00 | 37
2022-02-07 13:00 | 38
2022-02-07 14:00 | 39
2022-02-07 15:00 | 39
2022-02-07 16:00 | 38
2022-02-07 17:00 | 37
2022-02-07 18:00 | 38
2022-02-07 19:00 | 38
2022-02-07 20:00 | 38
2022-02-07 21:00 | 38
2022-02-07 22:00 | 38
2022-02-07 23:00 | 37
2022-02-08 | 38
2022-02-08 01:00 | 37
2022-02-08 02:00 | 37
2022-02-08 03:00 | 37
2022-02-08 04:00 | 37
2022-02-08 05:00 | 38
2022-02-08 06:00 | 37
2022-02-08 07:00 | 37
2022-02-08 08:00 | 37
2022-02-08 09:00 | 39
2022-02-08 10:00 | 42
2022-02-08 11:00 | 42
2022-02-08 12:00 | 46
2022-02-08 13:00 | 47
2022-02-08 14:00 | 45
2022-02-08 15:00 | 45
2022-02-08 16:00 | 40
2022-02-08 17:00 | 39
2022-02-08 18:00 | 37
2022-02-08 19:00 | 36
2022-02-08 20:00 | 36
2022-02-08 21:00 | 36
2022-02-08 22:00 | 34
2022-02-08 23:00 | 33
2022-02-09 | 32
2022-02-09 01:00 | 32
2022-02-09 02:00 | 31
2022-02-09 03:00 | 30
2022-02-09 04:00 | 30
2022-02-09 05:00 | 29
2022-02-09 06:00 | 28
2022-02-09 07:00 | 30
2022-02-09 08:00 | 30
2022-02-09 09:00 | 33
2022-02-09 10:00 | 36
2022-02-09 11:00 | 37
2022-02-09 12:00 | 37
2022-02-09 13:00 | 39
2022-02-09 14:00 | 40
2022-02-09 15:00 | 40
2022-02-09 16:00 | 40
2022-02-09 17:00 | 39
2022-02-09 18:00 | 38
2022-02-09 19:00 | 39
2022-02-09 20:00 | 39
2022-02-09 21:00 | 39
2022-02-09 22:00 | 37
2022-02-09 23:00 | 37
2022-02-10 | 35
2022-02-10 01:00 | 34
2022-02-10 02:00 | 33
2022-02-10 03:00 | 32
2022-02-10 04:00 | 34
2022-02-10 05:00 | 34
2022-02-10 06:00 | 32
2022-02-10 07:00 | 35
2022-02-10 08:00 | 33
2022-02-10 09:00 | 41
2022-02-10 10:00 | 44
2022-02-10 11:00 | 45
2022-02-10 12:00 | 50
2022-02-10 13:00 | 54
2022-02-10 14:00 | 54
2022-02-10 15:00 | 54
2022-02-10 16:00 | 53
2022-02-10 17:00 | 51
2022-02-10 18:00 | 49
2022-02-10 19:00 | 49
2022-02-10 20:00 | 48
2022-02-10 21:00 | 47
2022-02-10 22:00 | 47
2022-02-10 23:00 | 45
2022-02-11 | 40
2022-02-11 01:00 | 38
2022-02-11 02:00 | 40
2022-02-11 03:00 | 39
2022-02-11 04:00 | 39
2022-02-11 05:00 | 34
2022-02-11 06:00 | 36
2022-02-11 07:00 | 35
2022-02-11 08:00 | 40
2022-02-11 09:00 | 45
2022-02-11 10:00 | 47
2022-02-11 11:00 | 49
2022-02-11 12:00 | 50
2022-02-11 13:00 | 51
2022-02-11 14:00 | 51
2022-02-11 15:00 | 50
2022-02-11 16:00 | 48
2022-02-11 17:00 | 47
2022-02-11 18:00 | 45
2022-02-11 19:00 | 44
2022-02-11 20:00 | 44
2022-02-11 21:00 | 44
2022-02-11 22:00 | 45
2022-02-11 23:00 | 46
2022-02-12 | 46
2022-02-12 01:00 | 46
2022-02-12 02:00 | 46
2022-02-12 03:00 | 44
2022-02-12 04:00 | 45
2022-02-12 05:00 | 43
2022-02-12 06:00 | 41
2022-02-12 07:00 | 42
2022-02-12 08:00 | 45
2022-02-12 09:00 | 50
2022-02-12 10:00 | 53
2022-02-12 11:00 | 58
2022-02-12 12:00 | 60
2022-02-12 13:00 | 59
2022-02-12 14:00 | 57
2022-02-12 15:00 | 58
2022-02-12 16:00 | 55
2022-02-12 17:00 | 53
2022-02-12 18:00 | 52
2022-02-12 19:00 | 52
2022-02-12 20:00 | 50
2022-02-12 21:00 | 48
2022-02-12 22:00 | 47
2022-02-12 23:00 | 45
2022-02-13 | 43
2022-02-13 01:00 | 42
2022-02-13 02:00 | 41
2022-02-13 03:00 | 37
2022-02-13 04:00 | 35
2022-02-13 05:00 | 33
2022-02-13 06:00 | 32
2022-02-13 07:00 | 31
2022-02-13 08:00 | 32
2022-02-13 09:00 | 31
2022-02-13 10:00 | 32
2022-02-13 11:00 | 32
2022-02-13 12:00 | 32
2022-02-13 13:00 | 32
2022-02-13 14:00 | 31
2022-02-13 15:00 | 31
2022-02-13 16:00 | 31
2022-02-13 17:00 | 30
2022-02-13 18:00 | 29
2022-02-13 19:00 | 29
2022-02-13 20:00 | 28
2022-02-13 21:00 | 29
2022-02-13 22:00 | 28
2022-02-13 23:00 | 26
2022-02-14 | 25
2022-02-14 01:00 | 25
2022-02-14 02:00 | 23
2022-02-14 03:00 | 21
2022-02-14 04:00 | 19
2022-02-14 05:00 | 18
2022-02-14 06:00 | 17
2022-02-14 07:00 | 17
2022-02-14 08:00 | 17
2022-02-14 09:00 | 18
2022-02-14 10:00 | 19
2022-02-14 11:00 | 20
2022-02-14 12:00 | 21
2022-02-14 13:00 | 23
2022-02-14 14:00 | 24
2022-02-14 15:00 | 24
2022-02-14 16:00 | 24
2022-02-14 17:00 | 24
2022-02-14 18:00 | 23
2022-02-14 19:00 | 23
2022-02-14 20:00 | 22
2022-02-14 21:00 | 22
2022-02-14 22:00 | 20
2022-02-14 23:00 | 19
2022-02-15 | 19
2022-02-15 01:00 | 19
2022-02-15 02:00 | 18
2022-02-15 03:00 | 17
2022-02-15 04:00 | 17
2022-02-15 05:00 | 17
2022-02-15 06:00 | 17
2022-02-15 07:00 | 17
2022-02-15 08:00 | 18
2022-02-15 09:00 | 20
2022-02-15 10:00 | 22
2022-02-15 11:00 | 24
2022-02-15 12:00 | 25
2022-02-15 13:00 | 28
2022-02-15 14:00 | 28
2022-02-15 15:00 | 28
2022-02-15 16:00 | 28
2022-02-15 17:00 | 28
2022-02-15 18:00 | 27
2022-02-15 19:00 | 26
2022-02-15 20:00 | 27
2022-02-15 21:00 | 27
2022-02-15 22:00 | 26
2022-02-15 23:00 | 25
2022-02-16 | 26
2022-02-16 01:00 | 25
2022-02-16 02:00 | 25
2022-02-16 03:00 | 22
2022-02-16 04:00 | 29
2022-02-16 05:00 | 29
2022-02-16 06:00 | 31
2022-02-16 07:00 | 32
2022-02-16 08:00 | 34
2022-02-16 09:00 | 36
2022-02-16 10:00 | 38
2022-02-16 11:00 | 41
2022-02-16 12:00 | 43
2022-02-16 13:00 | 43
2022-02-16 14:00 | 42
2022-02-16 15:00 | 42
2022-02-16 16:00 | 42
2022-02-16 17:00 | 42
2022-02-16 18:00 | 41
2022-02-16 19:00 | 41
2022-02-16 20:00 | 41
2022-02-16 21:00 | 41
2022-02-16 22:00 | 40
2022-02-16 23:00 | 40
2022-02-17 | 41
2022-02-17 01:00 | 42
2022-02-17 02:00 | 42
2022-02-17 03:00 | 43
2022-02-17 04:00 | 45
2022-02-17 05:00 | 46
2022-02-17 06:00 | 45
2022-02-17 07:00 | 44
2022-02-17 08:00 | 44
2022-02-17 09:00 | 48
2022-02-17 10:00 | 50
2022-02-17 11:00 | 50
2022-02-17 12:00 | 50
2022-02-17 13:00 | 53
2022-02-17 14:00 | 51
2022-02-17 15:00 | 52
2022-02-17 16:00 | 52
2022-02-17 17:00 | 48
2022-02-17 18:00 | 48
2022-02-17 19:00 | 48
2022-02-17 20:00 | 48
2022-02-17 21:00 | 47
2022-02-17 22:00 | 49
2022-02-17 23:00 | 49
2022-02-18 | 49
2022-02-18 01:00 | 49
2022-02-18 02:00 | 48
2022-02-18 03:00 | 50
2022-02-18 04:00 | 51
2022-02-18 05:00 | 51
2022-02-18 06:00 | 52
2022-02-18 07:00 | 51
2022-02-18 08:00 | 58
2022-02-18 09:00 | 49
2022-02-18 10:00 | 45
2022-02-18 11:00 | 43
2022-02-18 12:00 | 44
2022-02-18 13:00 | 43
2022-02-18 14:00 | 45
2022-02-18 15:00 | 44
2022-02-18 16:00 | 41
2022-02-18 17:00 | 38
2022-02-18 18:00 | 35
2022-02-18 19:00 | 34
2022-02-18 20:00 | 32
2022-02-18 21:00 | 32
2022-02-18 22:00 | 29
2022-02-18 23:00 | 28
2022-02-19 | 27
2022-02-19 01:00 | 25
2022-02-19 02:00 | 25
2022-02-19 03:00 | 25
2022-02-19 04:00 | 23
2022-02-19 05:00 | 23
2022-02-19 06:00 | 23
2022-02-19 07:00 | 29
2022-02-19 08:00 | 31
2022-02-19 09:00 | 33
2022-02-19 10:00 | 36
2022-02-19 11:00 | 38
2022-02-19 12:00 | 39
2022-02-19 13:00 | 39
2022-02-19 14:00 | 37
2022-02-19 15:00 | 42
2022-02-19 16:00 | 35
2022-02-19 17:00 | 37
2022-02-19 18:00 | 32
2022-02-19 19:00 | 30
2022-02-19 20:00 | 28
2022-02-19 21:00 | 26
2022-02-19 22:00 | 26
2022-02-19 23:00 | 24
2022-02-20 | 24
2022-02-20 01:00 | 23
2022-02-20 02:00 | 22
2022-02-20 03:00 | 22
2022-02-20 04:00 | 22
2022-02-20 05:00 | 22
2022-02-20 06:00 | 21
2022-02-20 07:00 | 21
2022-02-20 08:00 | 24
2022-02-20 09:00 | 26
2022-02-20 10:00 | 27
2022-02-20 11:00 | 28
2022-02-20 12:00 | 29
2022-02-20 13:00 | 31
2022-02-20 14:00 | 31
2022-02-20 15:00 | 32
2022-02-20 16:00 | 33
2022-02-20 17:00 | 33
2022-02-20 18:00 | 33
2022-02-20 19:00 | 34
2022-02-20 20:00 | 34
2022-02-20 21:00 | 33
2022-02-20 22:00 | 33
2022-02-20 23:00 | 33
2022-02-21 | 33
2022-02-21 01:00 | 32
2022-02-21 02:00 | 32
2022-02-21 03:00 | 33
2022-02-21 04:00 | 31
2022-02-21 05:00 | 31
2022-02-21 06:00 | 31
2022-02-21 07:00 | 32
2022-02-21 08:00 | 36
2022-02-21 09:00 | 38
2022-02-21 10:00 | 38
2022-02-21 11:00 | 42
2022-02-21 12:00 | 43
2022-02-21 13:00 | 45
2022-02-21 14:00 | 47
2022-02-21 15:00 | 48
2022-02-21 16:00 | 46
2022-02-21 17:00 | 46
2022-02-21 18:00 | 41
2022-02-21 19:00 | 39
2022-02-21 20:00 | 38
2022-02-21 21:00 | 37
2022-02-21 22:00 | 39
2022-02-21 23:00 | 38
2022-02-22 | 35
2022-02-22 01:00 | 37
2022-02-22 02:00 | 35
2022-02-22 03:00 | 34
2022-02-22 04:00 | 34
2022-02-22 05:00 | 35
2022-02-22 06:00 | 37
2022-02-22 07:00 | 38
2022-02-22 08:00 | 40
2022-02-22 09:00 | 45
2022-02-22 10:00 | 49
2022-02-22 11:00 | 51
2022-02-22 12:00 | 51
2022-02-22 13:00 | 51
2022-02-22 14:00 | 50
2022-02-22 15:00 | 50
2022-02-22 16:00 | 50
2022-02-22 17:00 | 49
2022-02-22 18:00 | 48
2022-02-22 19:00 | 48
2022-02-22 20:00 | 49
2022-02-22 21:00 | 50
2022-02-22 22:00 | 49
2022-02-22 23:00 | 49
2022-02-23 | 50
2022-02-23 01:00 | 50
2022-02-23 02:00 | 47
2022-02-23 03:00 | 45
2022-02-23 04:00 | 46
2022-02-23 05:00 | 45
2022-02-23 06:00 | 47
2022-02-23 07:00 | 48
2022-02-23 08:00 | 49
2022-02-23 09:00 | 51
2022-02-23 10:00 | 57
2022-02-23 11:00 | 57
2022-02-23 12:00 | 62
2022-02-23 13:00 | 63
2022-02-23 14:00 | 63
2022-02-23 15:00 | 68
2022-02-23 16:00 | 68
2022-02-23 17:00 | 65
2022-02-23 18:00 | 61
2022-02-23 19:00 | 52
2022-02-23 20:00 | 46
2022-02-23 21:00 | 42
2022-02-23 22:00 | 40
2022-02-23 23:00 | 37
2022-02-24 | 36
2022-02-24 01:00 | 34
2022-02-24 02:00 | 34
2022-02-24 03:00 | 32
2022-02-24 04:00 | 31
2022-02-24 05:00 | 31
2022-02-24 06:00 | 30
2022-02-24 07:00 | 30
2022-02-24 08:00 | 30
2022-02-24 09:00 | 30
2022-02-24 10:00 | 31
2022-02-24 11:00 | 32
2022-02-24 12:00 | 32
2022-02-24 13:00 | 33
2022-02-24 14:00 | 33
2022-02-24 15:00 | 33
2022-02-24 16:00 | 33
2022-02-24 17:00 | 33
2022-02-24 18:00 | 33
2022-02-24 19:00 | 33
2022-02-24 20:00 | 33
2022-02-24 21:00 | 33
2022-02-24 22:00 | 33
2022-02-24 23:00 | 32
2022-02-25 | 32
2022-02-25 01:00 | 31
2022-02-25 02:00 | 30
2022-02-25 03:00 | 31
2022-02-25 04:00 | 31
2022-02-25 05:00 | 32
2022-02-25 06:00 | 33
2022-02-25 07:00 | 33
2022-02-25 08:00 | 33
2022-02-25 09:00 | 33
2022-02-25 10:00 | 32
2022-02-25 11:00 | 33
2022-02-25 12:00 | 34
2022-02-25 13:00 | 34
2022-02-25 14:00 | 38
2022-02-25 15:00 | 40
2022-02-25 16:00 | 44
2022-02-25 17:00 | 43
2022-02-25 18:00 | 40
2022-02-25 19:00 | 37
2022-02-25 20:00 | 34
2022-02-25 21:00 | 32
2022-02-25 22:00 | 30
2022-02-25 23:00 | 27
2022-02-26 | 26
2022-02-26 01:00 | 26
2022-02-26 02:00 | 25
2022-02-26 03:00 | 25
2022-02-26 04:00 | 24
2022-02-26 05:00 | 24
2022-02-26 06:00 | 24
2022-02-26 07:00 | 24
2022-02-26 08:00 | 25
2022-02-26 09:00 | 27
2022-02-26 10:00 | 28
2022-02-26 11:00 | 31
2022-02-26 12:00 | 33
2022-02-26 13:00 | 34
2022-02-26 14:00 | 36
2022-02-26 15:00 | 35
2022-02-26 16:00 | 37
2022-02-26 17:00 | 36
2022-02-26 18:00 | 35
2022-02-26 19:00 | 35
2022-02-26 20:00 | 34
2022-02-26 21:00 | 34
2022-02-26 22:00 | 33
2022-02-26 23:00 | 32
2022-02-27 | 31
2022-02-27 01:00 | 30
2022-02-27 02:00 | 30
2022-02-27 03:00 | 30
2022-02-27 04:00 | 29
2022-02-27 05:00 | 29
2022-02-27 06:00 | 29
2022-02-27 07:00 | 29
2022-02-27 08:00 | 31
2022-02-27 09:00 | 34
2022-02-27 10:00 | 36
2022-02-27 11:00 | 39
2022-02-27 12:00 | 42
2022-02-27 13:00 | 45
2022-02-27 14:00 | 46
2022-02-27 15:00 | 47
2022-02-27 16:00 | 48
2022-02-27 17:00 | 47
2022-02-27 18:00 | 47
2022-02-27 19:00 | 46
2022-02-27 20:00 | 45
2022-02-27 21:00 | 42
2022-02-27 22:00 | 40
2022-02-27 23:00 | 37
2022-02-28 | 34
2022-02-28 01:00 | 33
2022-02-28 02:00 | 32
2022-02-28 03:00 | 31
2022-02-28 04:00 | 30
2022-02-28 05:00 | 29
2022-02-28 06:00 | 28
2022-02-28 07:00 | 28
2022-02-28 08:00 | 28
2022-02-28 09:00 | 30
2022-02-28 10:00 | 30
2022-02-28 11:00 | 31
2022-02-28 12:00 | 33
2022-02-28 13:00 | 34
2022-02-28 14:00 | 36
2022-02-28 15:00 | 37
2022-02-28 16:00 | 36
2022-02-28 17:00 | 35
2022-02-28 18:00 | 33
2022-02-28 19:00 | 31
2022-02-28 20:00 | 30
2022-02-28 21:00 | 28
2022-02-28 22:00 | 29
2022-02-28 23:00 | 28
2022-03-01 | 28
2022-03-01 01:00 | 29
2022-03-01 02:00 | 30
2022-03-01 03:00 | 29
2022-03-01 04:00 | 28
2022-03-01 05:00 | 30
2022-03-01 06:00 | 35
2022-03-01 07:00 | 36
2022-03-01 08:00 | 38
2022-03-01 09:00 | 39
2022-03-01 10:00 | 40
2022-03-01 11:00 | 40
2022-03-01 12:00 | 41
2022-03-01 13:00 | 43
2022-03-01 14:00 | 43
2022-03-01 15:00 | 44
2022-03-01 16:00 | 43
2022-03-01 17:00 | 44
2022-03-01 18:00 | 41
2022-03-01 19:00 | 42
2022-03-01 20:00 | 43
2022-03-01 21:00 | 41
2022-03-01 22:00 | 40
2022-03-01 23:00 | 41
2022-03-02 | 42
2022-03-02 01:00 | 42
2022-03-02 02:00 | 39
2022-03-02 03:00 | 43
2022-03-02 04:00 | 43
2022-03-02 05:00 | 42
2022-03-02 06:00 | 43
2022-03-02 07:00 | 41
2022-03-02 08:00 | 42
2022-03-02 09:00 | 44
2022-03-02 10:00 | 45
2022-03-02 11:00 | 47
2022-03-02 12:00 | 48
2022-03-02 13:00 | 49
2022-03-02 14:00 | 50
2022-03-02 15:00 | 52
2022-03-02 16:00 | 52
2022-03-02 17:00 | 48
2022-03-02 18:00 | 42
2022-03-02 19:00 | 41
2022-03-02 20:00 | 42
2022-03-02 21:00 | 41
2022-03-02 22:00 | 41
2022-03-02 23:00 | 41
2022-03-03 | 41
2022-03-03 01:00 | 41
2022-03-03 02:00 | 42
2022-03-03 03:00 | 42
2022-03-03 04:00 | 43
2022-03-03 05:00 | 44
2022-03-03 06:00 | 41
2022-03-03 07:00 | 39
2022-03-03 08:00 | 39
2022-03-03 09:00 | 42
2022-03-03 10:00 | 44
2022-03-03 11:00 | 42
2022-03-03 12:00 | 42
2022-03-03 13:00 | 43
2022-03-03 14:00 | 45
2022-03-03 15:00 | 43
2022-03-03 16:00 | 42
2022-03-03 17:00 | 38
2022-03-03 18:00 | 35
2022-03-03 19:00 | 34
2022-03-03 20:00 | 32
2022-03-03 21:00 | 29
2022-03-03 22:00 | 28
2022-03-03 23:00 | 26
2022-03-04 | 25
2022-03-04 01:00 | 24
2022-03-04 02:00 | 22
2022-03-04 03:00 | 22
2022-03-04 04:00 | 21
2022-03-04 05:00 | 20
2022-03-04 06:00 | 20
2022-03-04 07:00 | 21
2022-03-04 08:00 | 25
2022-03-04 09:00 | 26
2022-03-04 10:00 | 26
2022-03-04 11:00 | 28
2022-03-04 12:00 | 30
2022-03-04 13:00 | 31
2022-03-04 14:00 | 32
2022-03-04 15:00 | 32
2022-03-04 16:00 | 33
2022-03-04 17:00 | 33
2022-03-04 18:00 | 32
2022-03-04 19:00 | 35
2022-03-04 20:00 | 35
2022-03-04 21:00 | 34
2022-03-04 22:00 | 33
2022-03-04 23:00 | 34
2022-03-05 | 30
2022-03-05 01:00 | 31
2022-03-05 02:00 | 32
2022-03-05 03:00 | 32
2022-03-05 04:00 | 28
2022-03-05 05:00 | 28
2022-03-05 06:00 | 28
2022-03-05 07:00 | 30
2022-03-05 08:00 | 33
2022-03-05 09:00 | 36
2022-03-05 10:00 | 38
2022-03-05 11:00 | 40
2022-03-05 12:00 | 41
2022-03-05 13:00 | 42
2022-03-05 14:00 | 43
2022-03-05 15:00 | 42
2022-03-05 16:00 | 41
2022-03-05 17:00 | 40
2022-03-05 18:00 | 40
2022-03-05 19:00 | 39
2022-03-05 20:00 | 40
2022-03-05 21:00 | 42
2022-03-05 22:00 | 43
2022-03-05 23:00 | 43
2022-03-06 | 44
2022-03-06 01:00 | 46
2022-03-06 02:00 | 46
2022-03-06 03:00 | 45
2022-03-06 04:00 | 45
2022-03-06 05:00 | 45
2022-03-06 06:00 | 44
2022-03-06 07:00 | 44
2022-03-06 08:00 | 45
2022-03-06 09:00 | 47
2022-03-06 10:00 | 48
2022-03-06 11:00 | 47
2022-03-06 12:00 | 50
2022-03-06 13:00 | 52
2022-03-06 14:00 | 55
2022-03-06 15:00 | 61
2022-03-06 16:00 | 58
2022-03-06 17:00 | 52
2022-03-06 18:00 | 50
2022-03-06 19:00 | 50
2022-03-06 20:00 | 50
2022-03-06 21:00 | 50
2022-03-06 22:00 | 51
2022-03-06 23:00 | 50
2022-03-07 | 53
2022-03-07 01:00 | 56
2022-03-07 02:00 | 54
2022-03-07 03:00 | 52
2022-03-07 04:00 | 49
2022-03-07 05:00 | 53
2022-03-07 06:00 | 50
2022-03-07 07:00 | 51
2022-03-07 08:00 | 52
2022-03-07 09:00 | 58
2022-03-07 10:00 | 56
2022-03-07 11:00 | 53
2022-03-07 12:00 | 59
2022-03-07 13:00 | 57
2022-03-07 14:00 | 54
2022-03-07 15:00 | 55
2022-03-07 16:00 | 54
2022-03-07 17:00 | 53
2022-03-07 18:00 | 52
2022-03-07 19:00 | 52
2022-03-07 20:00 | 53
2022-03-07 21:00 | 53
2022-03-07 22:00 | 59
2022-03-07 23:00 | 60
2022-03-08 | 55
2022-03-08 01:00 | 47
2022-03-08 02:00 | 45
2022-03-08 03:00 | 45
2022-03-08 04:00 | 43
2022-03-08 05:00 | 41
2022-03-08 06:00 | 41
2022-03-08 07:00 | 40
2022-03-08 08:00 | 41
2022-03-08 09:00 | 42
2022-03-08 10:00 | 45
2022-03-08 11:00 | 45
2022-03-08 12:00 | 46
2022-03-08 13:00 | 46
2022-03-08 14:00 | 46
2022-03-08 15:00 | 46
2022-03-08 16:00 | 46
2022-03-08 17:00 | 45
2022-03-08 18:00 | 43
2022-03-08 19:00 | 43
2022-03-08 20:00 | 40
2022-03-08 21:00 | 39
2022-03-08 22:00 | 39
2022-03-08 23:00 | 39
2022-03-09 | 38
2022-03-09 01:00 | 39
2022-03-09 02:00 | 38
2022-03-09 03:00 | 39
2022-03-09 04:00 | 39
2022-03-09 05:00 | 40
2022-03-09 06:00 | 36
2022-03-09 07:00 | 35
2022-03-09 08:00 | 36
2022-03-09 09:00 | 37
2022-03-09 10:00 | 37
2022-03-09 11:00 | 35
2022-03-09 12:00 | 33
2022-03-09 13:00 | 34
2022-03-09 14:00 | 34
2022-03-09 15:00 | 34
2022-03-09 16:00 | 35
2022-03-09 17:00 | 35
2022-03-09 18:00 | 35
2022-03-09 19:00 | 35
2022-03-09 20:00 | 36
2022-03-09 21:00 | 36
2022-03-09 22:00 | 36
2022-03-09 23:00 | 36
2022-03-10 | 36
2022-03-10 01:00 | 35
2022-03-10 02:00 | 34
2022-03-10 03:00 | 34
2022-03-10 04:00 | 33
2022-03-10 05:00 | 33
2022-03-10 06:00 | 32
2022-03-10 07:00 | 32
2022-03-10 08:00 | 33
2022-03-10 09:00 | 37
2022-03-10 10:00 | 41
2022-03-10 11:00 | 45
2022-03-10 12:00 | 48
2022-03-10 13:00 | 49
2022-03-10 14:00 | 50
2022-03-10 15:00 | 45
2022-03-10 16:00 | 44
2022-03-10 17:00 | 43
2022-03-10 18:00 | 41
2022-03-10 19:00 | 40
2022-03-10 20:00 | 40
2022-03-10 21:00 | 39
2022-03-10 22:00 | 36
2022-03-10 23:00 | 38
2022-03-11 | 39
2022-03-11 01:00 | 36
2022-03-11 02:00 | 35
2022-03-11 03:00 | 35
2022-03-11 04:00 | 34
2022-03-11 05:00 | 32
2022-03-11 06:00 | 33
2022-03-11 07:00 | 36
2022-03-11 08:00 | 41
2022-03-11 09:00 | 44
2022-03-11 10:00 | 46
2022-03-11 11:00 | 49
2022-03-11 12:00 | 49
2022-03-11 13:00 | 48
2022-03-11 14:00 | 48
2022-03-11 15:00 | 48
2022-03-11 16:00 | 46
2022-03-11 17:00 | 45
2022-03-11 18:00 | 43
2022-03-11 19:00 | 42
2022-03-11 20:00 | 43
2022-03-11 21:00 | 44
2022-03-11 22:00 | 45
2022-03-11 23:00 | 45
2022-03-12 | 45
2022-03-12 01:00 | 46
2022-03-12 02:00 | 44
2022-03-12 03:00 | 45
2022-03-12 04:00 | 45
2022-03-12 05:00 | 45
2022-03-12 06:00 | 45
2022-03-12 07:00 | 45
2022-03-12 08:00 | 45
2022-03-12 09:00 | 46
2022-03-12 10:00 | 45
2022-03-12 11:00 | 36
2022-03-12 12:00 | 35
2022-03-12 13:00 | 33
2022-03-12 14:00 | 32
2022-03-12 15:00 | 32
2022-03-12 16:00 | 31
2022-03-12 17:00 | 27
2022-03-12 18:00 | 24
2022-03-12 19:00 | 26
2022-03-12 20:00 | 27
2022-03-12 21:00 | 26
2022-03-12 22:00 | 26
2022-03-12 23:00 | 25
2022-03-13 | 24
2022-03-13 01:00 | 23
2022-03-13 03:00 | 23
2022-03-13 04:00 | 23
2022-03-13 05:00 | 23
2022-03-13 06:00 | 23
2022-03-13 07:00 | 23
2022-03-13 08:00 | 24
2022-03-13 09:00 | 26
2022-03-13 10:00 | 28
2022-03-13 11:00 | 30
2022-03-13 12:00 | 32
2022-03-13 13:00 | 32
2022-03-13 14:00 | 33
2022-03-13 15:00 | 34
2022-03-13 16:00 | 35
2022-03-13 17:00 | 34
2022-03-13 18:00 | 34
2022-03-13 19:00 | 32
2022-03-13 20:00 | 28
2022-03-13 21:00 | 30
2022-03-13 22:00 | 31
2022-03-13 23:00 | 31
2022-03-14 | 32
2022-03-14 01:00 | 34
2022-03-14 02:00 | 36
2022-03-14 03:00 | 36
2022-03-14 04:00 | 37
2022-03-14 05:00 | 37
2022-03-14 06:00 | 37
2022-03-14 07:00 | 37
2022-03-14 08:00 | 37
2022-03-14 09:00 | 41
2022-03-14 10:00 | 45
2022-03-14 11:00 | 47
2022-03-14 12:00 | 51
2022-03-14 13:00 | 53
2022-03-14 14:00 | 54
2022-03-14 15:00 | 52
2022-03-14 16:00 | 50
2022-03-14 17:00 | 48
2022-03-14 18:00 | 47
2022-03-14 19:00 | 45
2022-03-14 20:00 | 45
2022-03-14 21:00 | 45
2022-03-14 22:00 | 47
2022-03-14 23:00 | 46
2022-03-15 | 45
2022-03-15 01:00 | 44
2022-03-15 02:00 | 44
2022-03-15 03:00 | 43
2022-03-15 04:00 | 42
2022-03-15 05:00 | 40
2022-03-15 06:00 | 40
2022-03-15 07:00 | 40
2022-03-15 08:00 | 42
2022-03-15 09:00 | 46
2022-03-15 10:00 | 49
2022-03-15 11:00 | 50
2022-03-15 12:00 | 52
2022-03-15 13:00 | 55
2022-03-15 14:00 | 56
2022-03-15 15:00 | 55
2022-03-15 16:00 | 54
2022-03-15 17:00 | 53
2022-03-15 18:00 | 51
2022-03-15 19:00 | 48
2022-03-15 20:00 | 48
2022-03-15 21:00 | 48
2022-03-15 22:00 | 51
2022-03-15 23:00 | 58
2022-03-16 | 51
2022-03-16 01:00 | 50
2022-03-16 02:00 | 50
2022-03-16 03:00 | 47
2022-03-16 04:00 | 44
2022-03-16 05:00 | 44
2022-03-16 06:00 | 45
2022-03-16 07:00 | 44
2022-03-16 08:00 | 47
2022-03-16 09:00 | 56
2022-03-16 10:00 | 58
2022-03-16 11:00 | 60
2022-03-16 12:00 | 62
2022-03-16 13:00 | 60
2022-03-16 14:00 | 58
2022-03-16 15:00 | 55
2022-03-16 16:00 | 54
2022-03-16 17:00 | 54
2022-03-16 18:00 | 51
2022-03-16 19:00 | 48
2022-03-16 20:00 | 48
2022-03-16 21:00 | 47
2022-03-16 22:00 | 46
2022-03-16 23:00 | 46
2022-03-17 | 46
2022-03-17 01:00 | 45
2022-03-17 02:00 | 45
2022-03-17 03:00 | 47
2022-03-17 04:00 | 47
2022-03-17 05:00 | 49
2022-03-17 06:00 | 50
2022-03-17 07:00 | 47
2022-03-17 08:00 | 47
2022-03-17 09:00 | 47
2022-03-17 10:00 | 48
2022-03-17 11:00 | 51
2022-03-17 12:00 | 52
2022-03-17 13:00 | 52
2022-03-17 14:00 | 53
2022-03-17 15:00 | 54
2022-03-17 16:00 | 55
2022-03-17 17:00 | 54
2022-03-17 18:00 | 53
2022-03-17 19:00 | 53
2022-03-17 20:00 | 53
2022-03-17 21:00 | 53
2022-03-17 22:00 | 53
2022-03-17 23:00 | 52
2022-03-18 | 52
2022-03-18 01:00 | 52
2022-03-18 02:00 | 52
2022-03-18 03:00 | 53
2022-03-18 04:00 | 53
2022-03-18 05:00 | 53
2022-03-18 06:00 | 52
2022-03-18 07:00 | 51
2022-03-18 08:00 | 51
2022-03-18 09:00 | 51
2022-03-18 10:00 | 51
2022-03-18 11:00 | 55
2022-03-18 12:00 | 60
2022-03-18 13:00 | 62
2022-03-18 14:00 | 61
2022-03-18 15:00 | 59
2022-03-18 16:00 | 57
2022-03-18 17:00 | 56
2022-03-18 18:00 | 52
2022-03-18 19:00 | 50
2022-03-18 20:00 | 49
2022-03-18 21:00 | 49
2022-03-18 22:00 | 49
2022-03-18 23:00 | 49
2022-03-19 | 47
2022-03-19 01:00 | 47
2022-03-19 02:00 | 46
2022-03-19 03:00 | 47
2022-03-19 04:00 | 48
2022-03-19 05:00 | 49
2022-03-19 06:00 | 50
2022-03-19 07:00 | 50
2022-03-19 08:00 | 50
2022-03-19 09:00 | 52
2022-03-19 10:00 | 53
2022-03-19 11:00 | 54
2022-03-19 12:00 | 56
2022-03-19 13:00 | 58
2022-03-19 14:00 | 57
2022-03-19 15:00 | 58
2022-03-19 16:00 | 58
2022-03-19 17:00 | 58
2022-03-19 18:00 | 55
2022-03-19 19:00 | 55
2022-03-19 20:00 | 53
2022-03-19 21:00 | 53
2022-03-19 22:00 | 52
2022-03-19 23:00 | 52
2022-03-20 | 56
2022-03-20 01:00 | 57
2022-03-20 02:00 | 55
2022-03-20 03:00 | 53
2022-03-20 04:00 | 56
2022-03-20 05:00 | 56
2022-03-20 06:00 | 54
2022-03-20 07:00 | 53
2022-03-20 08:00 | 53
2022-03-20 09:00 | 56
2022-03-20 10:00 | 58
2022-03-20 11:00 | 59
2022-03-20 12:00 | 59
2022-03-20 13:00 | 58
2022-03-20 14:00 | 57
2022-03-20 15:00 | 58
2022-03-20 16:00 | 58
2022-03-20 17:00 | 55
2022-03-20 18:00 | 55
2022-03-20 19:00 | 54
2022-03-20 20:00 | 53
2022-03-20 21:00 | 50
2022-03-20 22:00 | 48
2022-03-20 23:00 | 47
2022-03-21 | 46
2022-03-21 01:00 | 47
2022-03-21 02:00 | 47
2022-03-21 03:00 | 46
2022-03-21 04:00 | 45
2022-03-21 05:00 | 45
2022-03-21 06:00 | 45
2022-03-21 07:00 | 45
2022-03-21 08:00 | 46
2022-03-21 09:00 | 48
2022-03-21 10:00 | 51
2022-03-21 11:00 | 53
2022-03-21 12:00 | 55
2022-03-21 13:00 | 58
2022-03-21 14:00 | 60
2022-03-21 15:00 | 62
2022-03-21 16:00 | 62
2022-03-21 17:00 | 63
2022-03-21 18:00 | 62
2022-03-21 19:00 | 60
2022-03-21 20:00 | 58
2022-03-21 21:00 | 57
2022-03-21 22:00 | 54
2022-03-21 23:00 | 54
2022-03-22 | 54
2022-03-22 01:00 | 53
2022-03-22 02:00 | 52
2022-03-22 03:00 | 51
2022-03-22 04:00 | 51
2022-03-22 05:00 | 50
2022-03-22 06:00 | 49
2022-03-22 07:00 | 47
2022-03-22 08:00 | 46
2022-03-22 09:00 | 47
2022-03-22 10:00 | 48
2022-03-22 11:00 | 50
2022-03-22 12:00 | 52
2022-03-22 13:00 | 54
2022-03-22 14:00 | 56
2022-03-22 15:00 | 59
2022-03-22 16:00 | 58
2022-03-22 17:00 | 57
2022-03-22 18:00 | 57
2022-03-22 19:00 | 55
2022-03-22 20:00 | 54
2022-03-22 21:00 | 52
2022-03-22 22:00 | 50
2022-03-22 23:00 | 49
2022-03-23 | 47
2022-03-23 01:00 | 46
2022-03-23 02:00 | 44
2022-03-23 03:00 | 42
2022-03-23 04:00 | 42
2022-03-23 05:00 | 41
2022-03-23 06:00 | 40
2022-03-23 07:00 | 40
2022-03-23 08:00 | 40
2022-03-23 09:00 | 42
2022-03-23 10:00 | 43
2022-03-23 11:00 | 43
2022-03-23 12:00 | 43
2022-03-23 13:00 | 45
2022-03-23 14:00 | 45
2022-03-23 15:00 | 43
2022-03-23 16:00 | 42
2022-03-23 17:00 | 41
2022-03-23 18:00 | 42
2022-03-23 19:00 | 42
2022-03-23 20:00 | 41
2022-03-23 21:00 | 41
2022-03-23 22:00 | 42
2022-03-23 23:00 | 42
2022-03-24 | 40
2022-03-24 01:00 | 41
2022-03-24 02:00 | 41
2022-03-24 03:00 | 42
2022-03-24 04:00 | 43
2022-03-24 05:00 | 44
2022-03-24 06:00 | 44
2022-03-24 07:00 | 44
2022-03-24 08:00 | 45
2022-03-24 09:00 | 45
2022-03-24 10:00 | 46
2022-03-24 11:00 | 47
2022-03-24 12:00 | 46
2022-03-24 13:00 | 45
2022-03-24 14:00 | 45
2022-03-24 15:00 | 45
2022-03-24 16:00 | 46
2022-03-24 17:00 | 46
2022-03-24 18:00 | 46
2022-03-24 19:00 | 46
2022-03-24 20:00 | 46
2022-03-24 21:00 | 45
2022-03-24 22:00 | 45
2022-03-24 23:00 | 45
2022-03-25 | 44
2022-03-25 01:00 | 44
2022-03-25 02:00 | 44
2022-03-25 03:00 | 45
2022-03-25 04:00 | 45
2022-03-25 05:00 | 45
2022-03-25 06:00 | 45
2022-03-25 07:00 | 46
2022-03-25 08:00 | 47
2022-03-25 09:00 | 49
2022-03-25 10:00 | 49
2022-03-25 11:00 | 49
2022-03-25 12:00 | 51
2022-03-25 13:00 | 55
2022-03-25 14:00 | 55
2022-03-25 15:00 | 54
2022-03-25 16:00 | 57
2022-03-25 17:00 | 56
2022-03-25 18:00 | 56
2022-03-25 19:00 | 53
2022-03-25 20:00 | 53
2022-03-25 21:00 | 51
2022-03-25 22:00 | 51
2022-03-25 23:00 | 51
2022-03-26 | 52
2022-03-26 01:00 | 51
2022-03-26 02:00 | 50
2022-03-26 03:00 | 50
2022-03-26 04:00 | 49
2022-03-26 05:00 | 49
2022-03-26 06:00 | 49
2022-03-26 07:00 | 47
2022-03-26 08:00 | 48
2022-03-26 09:00 | 49
2022-03-26 10:00 | 52
2022-03-26 11:00 | 53
2022-03-26 12:00 | 52
2022-03-26 13:00 | 51
2022-03-26 14:00 | 53
2022-03-26 15:00 | 47
2022-03-26 16:00 | 48
2022-03-26 17:00 | 53
2022-03-26 18:00 | 50
2022-03-26 19:00 | 50
2022-03-26 20:00 | 48
2022-03-26 21:00 | 47
2022-03-26 22:00 | 47
2022-03-26 23:00 | 45
2022-03-27 | 44
2022-03-27 01:00 | 42
2022-03-27 02:00 | 41
2022-03-27 03:00 | 41
2022-03-27 04:00 | 40
2022-03-27 05:00 | 41
2022-03-27 06:00 | 39
2022-03-27 07:00 | 40
2022-03-27 08:00 | 42
2022-03-27 09:00 | 43
2022-03-27 10:00 | 44
2022-03-27 11:00 | 46
2022-03-27 12:00 | 45
2022-03-27 13:00 | 45
2022-03-27 14:00 | 46
2022-03-27 15:00 | 45
2022-03-27 16:00 | 43
2022-03-27 17:00 | 42
2022-03-27 18:00 | 39
2022-03-27 19:00 | 38
2022-03-27 20:00 | 37
2022-03-27 21:00 | 37
2022-03-27 22:00 | 35
2022-03-27 23:00 | 33
2022-03-28 | 32
2022-03-28 01:00 | 29
2022-03-28 02:00 | 27
2022-03-28 03:00 | 26
2022-03-28 04:00 | 25
2022-03-28 05:00 | 24
2022-03-28 06:00 | 23
2022-03-28 07:00 | 23
2022-03-28 08:00 | 25
2022-03-28 09:00 | 26
2022-03-28 10:00 | 28
2022-03-28 11:00 | 31
2022-03-28 12:00 | 32
2022-03-28 13:00 | 32
2022-03-28 14:00 | 33
2022-03-28 15:00 | 32
2022-03-28 16:00 | 32
2022-03-28 17:00 | 31
2022-03-28 18:00 | 30
2022-03-28 19:00 | 28
2022-03-28 20:00 | 27
2022-03-28 21:00 | 26
2022-03-28 22:00 | 25
2022-03-28 23:00 | 24
2022-03-29 | 24
2022-03-29 01:00 | 24
2022-03-29 02:00 | 24
2022-03-29 03:00 | 25
2022-03-29 04:00 | 25
2022-03-29 05:00 | 25
2022-03-29 06:00 | 25
2022-03-29 07:00 | 25
2022-03-29 08:00 | 27
2022-03-29 09:00 | 29
2022-03-29 10:00 | 31
2022-03-29 11:00 | 34
2022-03-29 12:00 | 36
2022-03-29 13:00 | 36
2022-03-29 14:00 | 37
2022-03-29 15:00 | 35
2022-03-29 16:00 | 37
2022-03-29 17:00 | 38
2022-03-29 18:00 | 38
2022-03-29 19:00 | 36
2022-03-29 20:00 | 35
2022-03-29 21:00 | 34
2022-03-29 22:00 | 34
2022-03-29 23:00 | 34
2022-03-30 | 32
2022-03-30 01:00 | 32
2022-03-30 02:00 | 31
2022-03-30 03:00 | 30
2022-03-30 04:00 | 29
2022-03-30 05:00 | 28
2022-03-30 06:00 | 29
2022-03-30 07:00 | 29
2022-03-30 08:00 | 32
2022-03-30 09:00 | 35
2022-03-30 10:00 | 37
2022-03-30 11:00 | 39
2022-03-30 12:00 | 40
2022-03-30 13:00 | 40
2022-03-30 14:00 | 42
2022-03-30 15:00 | 41
2022-03-30 16:00 | 42
2022-03-30 17:00 | 41
2022-03-30 18:00 | 41
2022-03-30 19:00 | 40
2022-03-30 20:00 | 41
2022-03-30 21:00 | 41
2022-03-30 22:00 | 42
2022-03-30 23:00 | 42
2022-03-31 | 43
2022-03-31 01:00 | 44
2022-03-31 02:00 | 45
2022-03-31 03:00 | 46
2022-03-31 04:00 | 46
2022-03-31 05:00 | 47
2022-03-31 06:00 | 47
2022-03-31 07:00 | 47
2022-03-31 08:00 | 48
2022-03-31 09:00 | 52
2022-03-31 10:00 | 56
2022-03-31 11:00 | 54
2022-03-31 12:00 | 55
2022-03-31 13:00 | 54
2022-03-31 14:00 | 55
2022-03-31 15:00 | 54
2022-03-31 16:00 | 54
2022-03-31 17:00 | 53
2022-03-31 18:00 | 53
2022-03-31 19:00 | 52
2022-03-31 20:00 | 53
2022-03-31 21:00 | 54
2022-03-31 22:00 | 56
2022-03-31 23:00 | 55
2022-04-01 | 54
2022-04-01 01:00 | 52
2022-04-01 02:00 | 51
2022-04-01 03:00 | 49
2022-04-01 04:00 | 56
2022-04-01 05:00 | 59
2022-04-01 06:00 | 57
2022-04-01 07:00 | 54
2022-04-01 08:00 | 53
2022-04-01 09:00 | 52
2022-04-01 10:00 | 53
2022-04-01 11:00 | 54
2022-04-01 12:00 | 56
2022-04-01 13:00 | 56
2022-04-01 14:00 | 56
2022-04-01 15:00 | 55
2022-04-01 16:00 | 54
2022-04-01 17:00 | 51
2022-04-01 18:00 | 50
2022-04-01 19:00 | 48
2022-04-01 20:00 | 46
2022-04-01 21:00 | 46
2022-04-01 22:00 | 45
2022-04-01 23:00 | 45
2022-04-02 | 44
2022-04-02 01:00 | 43
2022-04-02 02:00 | 43
2022-04-02 03:00 | 42
2022-04-02 04:00 | 41
2022-04-02 05:00 | 40
2022-04-02 06:00 | 40
2022-04-02 07:00 | 39
2022-04-02 08:00 | 39
2022-04-02 09:00 | 42
2022-04-02 10:00 | 42
2022-04-02 11:00 | 44
2022-04-02 12:00 | 46
2022-04-02 13:00 | 48
2022-04-02 14:00 | 50
2022-04-02 15:00 | 51
2022-04-02 16:00 | 52
2022-04-02 17:00 | 51
2022-04-02 18:00 | 51
2022-04-02 19:00 | 45
2022-04-02 20:00 | 43
2022-04-02 21:00 | 43
2022-04-02 22:00 | 42
2022-04-02 23:00 | 43
2022-04-03 | 43
2022-04-03 01:00 | 43
2022-04-03 02:00 | 41
2022-04-03 03:00 | 39
2022-04-03 04:00 | 41
2022-04-03 05:00 | 41
2022-04-03 06:00 | 41
2022-04-03 07:00 | 40
2022-04-03 08:00 | 43
2022-04-03 09:00 | 45
2022-04-03 10:00 | 45
2022-04-03 11:00 | 46
2022-04-03 12:00 | 44
2022-04-03 13:00 | 44
2022-04-03 14:00 | 44
2022-04-03 15:00 | 45
2022-04-03 16:00 | 45
2022-04-03 17:00 | 46
2022-04-03 18:00 | 45
2022-04-03 19:00 | 45
2022-04-03 20:00 | 46
2022-04-03 21:00 | 45
2022-04-03 22:00 | 44
2022-04-03 23:00 | 42
2022-04-04 | 41
2022-04-04 01:00 | 40
2022-04-04 02:00 | 40
2022-04-04 03:00 | 40
2022-04-04 04:00 | 40
2022-04-04 05:00 | 40
2022-04-04 06:00 | 39
2022-04-04 07:00 | 40
2022-04-04 08:00 | 43
2022-04-04 09:00 | 45
2022-04-04 10:00 | 47
2022-04-04 11:00 | 50
2022-04-04 12:00 | 51
2022-04-04 13:00 | 52
2022-04-04 14:00 | 53
2022-04-04 15:00 | 54
2022-04-04 16:00 | 54
2022-04-04 17:00 | 53
2022-04-04 18:00 | 52
2022-04-04 19:00 | 51
2022-04-04 20:00 | 51
2022-04-04 21:00 | 50
2022-04-04 22:00 | 50
2022-04-04 23:00 | 48
2022-04-05 | 46
2022-04-05 01:00 | 46
2022-04-05 02:00 | 43
2022-04-05 03:00 | 39
2022-04-05 04:00 | 41
2022-04-05 05:00 | 40
2022-04-05 06:00 | 43
2022-04-05 07:00 | 42
2022-04-05 08:00 | 45
2022-04-05 09:00 | 46
2022-04-05 10:00 | 50
2022-04-05 11:00 | 51
2022-04-05 12:00 | 52
2022-04-05 13:00 | 52
2022-04-05 14:00 | 51
2022-04-05 15:00 | 51
2022-04-05 16:00 | 51
2022-04-05 17:00 | 50
2022-04-05 18:00 | 48
2022-04-05 19:00 | 47
2022-04-05 20:00 | 47
2022-04-05 21:00 | 47
2022-04-05 22:00 | 47
2022-04-05 23:00 | 47
2022-04-06 | 47
2022-04-06 01:00 | 47
2022-04-06 02:00 | 47
2022-04-06 03:00 | 47
2022-04-06 04:00 | 47
2022-04-06 05:00 | 48
2022-04-06 06:00 | 49
2022-04-06 07:00 | 50
2022-04-06 08:00 | 48
2022-04-06 09:00 | 48
2022-04-06 10:00 | 47
2022-04-06 11:00 | 49
2022-04-06 12:00 | 50
2022-04-06 13:00 | 52
2022-04-06 14:00 | 51
2022-04-06 15:00 | 51
2022-04-06 16:00 | 53
2022-04-06 17:00 | 53
2022-04-06 18:00 | 52
2022-04-06 19:00 | 51
2022-04-06 20:00 | 51
2022-04-06 21:00 | 50
2022-04-06 22:00 | 50
2022-04-06 23:00 | 50
2022-04-07 | 49
2022-04-07 01:00 | 49
2022-04-07 02:00 | 48
2022-04-07 03:00 | 47
2022-04-07 04:00 | 47
2022-04-07 05:00 | 47
2022-04-07 06:00 | 46
2022-04-07 07:00 | 45
2022-04-07 08:00 | 46
2022-04-07 09:00 | 46
2022-04-07 10:00 | 46
2022-04-07 11:00 | 46
2022-04-07 12:00 | 47
2022-04-07 13:00 | 48
2022-04-07 14:00 | 48
2022-04-07 15:00 | 48
2022-04-07 16:00 | 49
2022-04-07 17:00 | 48
2022-04-07 18:00 | 49
2022-04-07 19:00 | 49
2022-04-07 20:00 | 49
2022-04-07 21:00 | 49
2022-04-07 22:00 | 51
2022-04-07 23:00 | 51
2022-04-08 | 51
2022-04-08 01:00 | 51
2022-04-08 02:00 | 50
2022-04-08 03:00 | 48
2022-04-08 04:00 | 50
2022-04-08 05:00 | 50
2022-04-08 06:00 | 50
2022-04-08 07:00 | 50
2022-04-08 08:00 | 50
2022-04-08 09:00 | 52
2022-04-08 10:00 | 54
2022-04-08 11:00 | 57
2022-04-08 12:00 | 59
2022-04-08 13:00 | 59
2022-04-08 14:00 | 61
2022-04-08 15:00 | 61
2022-04-08 16:00 | 63
2022-04-08 17:00 | 58
2022-04-08 18:00 | 55
2022-04-08 19:00 | 53
2022-04-08 20:00 | 49
2022-04-08 21:00 | 48
2022-04-08 22:00 | 50
2022-04-08 23:00 | 49
2022-04-09 | 49
2022-04-09 01:00 | 49
2022-04-09 02:00 | 50
2022-04-09 03:00 | 48
2022-04-09 04:00 | 50
2022-04-09 05:00 | 50
2022-04-09 06:00 | 50
2022-04-09 07:00 | 48
2022-04-09 08:00 | 49
2022-04-09 09:00 | 50
2022-04-09 10:00 | 49
2022-04-09 11:00 | 51
2022-04-09 12:00 | 54
2022-04-09 13:00 | 55
2022-04-09 14:00 | 53
2022-04-09 15:00 | 54
2022-04-09 16:00 | 56
2022-04-09 17:00 | 55
2022-04-09 18:00 | 55
2022-04-09 19:00 | 53
2022-04-09 20:00 | 52
2022-04-09 21:00 | 51
2022-04-09 22:00 | 48
2022-04-09 23:00 | 49
2022-04-10 | 49
2022-04-10 01:00 | 49
2022-04-10 02:00 | 49
2022-04-10 03:00 | 48
2022-04-10 04:00 | 47
2022-04-10 05:00 | 46
2022-04-10 06:00 | 45
2022-04-10 07:00 | 45
2022-04-10 08:00 | 44
2022-04-10 09:00 | 46
2022-04-10 10:00 | 48
2022-04-10 11:00 | 49
2022-04-10 12:00 | 48
2022-04-10 13:00 | 48
2022-04-10 14:00 | 51
2022-04-10 15:00 | 49
2022-04-10 16:00 | 50
2022-04-10 17:00 | 52
2022-04-10 18:00 | 49
2022-04-10 19:00 | 47
2022-04-10 20:00 | 47
2022-04-10 21:00 | 46
2022-04-10 22:00 | 46
2022-04-10 23:00 | 45
2022-04-11 | 44
2022-04-11 01:00 | 43
2022-04-11 02:00 | 42
2022-04-11 03:00 | 42
2022-04-11 04:00 | 41.7
2022-04-11 05:00 | 41
2022-04-11 06:00 | 40
2022-04-11 07:00 | 41
2022-04-11 08:00 | 44
2022-04-11 09:00 | 46
2022-04-11 10:00 | 48
2022-04-11 11:00 | 50
2022-04-11 12:00 | 51
2022-04-11 13:00 | 52
2022-04-11 14:00 | 54
2022-04-11 15:00 | 53
2022-04-11 16:00 | 53
2022-04-11 17:00 | 49
2022-04-11 18:00 | 49
2022-04-11 19:00 | 48
2022-04-11 20:00 | 47
2022-04-11 21:00 | 48
2022-04-11 22:00 | 48
2022-04-11 23:00 | 50
2022-04-12 | 48
2022-04-12 01:00 | 48
2022-04-12 02:00 | 48
2022-04-12 03:00 | 48
2022-04-12 04:00 | 48
2022-04-12 05:00 | 47
2022-04-12 06:00 | 48
2022-04-12 07:00 | 48
2022-04-12 08:00 | 49
2022-04-12 09:00 | 52
2022-04-12 10:00 | 52
2022-04-12 11:00 | 52
2022-04-12 12:00 | 59
2022-04-12 13:00 | 63
2022-04-12 14:00 | 66
2022-04-12 15:00 | 68
2022-04-12 16:00 | 70
2022-04-12 17:00 | 66
2022-04-12 18:00 | 68
2022-04-12 19:00 | 61
2022-04-12 20:00 | 55
2022-04-12 21:00 | 54
2022-04-12 22:00 | 54
2022-04-12 23:00 | 51
2022-04-13 | 51
2022-04-13 01:00 | 49
2022-04-13 02:00 | 48
2022-04-13 03:00 | 47
2022-04-13 04:00 | 48
2022-04-13 05:00 | 48
2022-04-13 06:00 | 50
2022-04-13 07:00 | 51
2022-04-13 08:00 | 53
2022-04-13 09:00 | 60
2022-04-13 10:00 | 60
2022-04-13 11:00 | 62
2022-04-13 12:00 | 63
2022-04-13 13:00 | 64
2022-04-13 14:00 | 59
2022-04-13 15:00 | 59
2022-04-13 16:00 | 59
2022-04-13 17:00 | 59
2022-04-13 18:00 | 58
2022-04-13 19:00 | 58
2022-04-13 20:00 | 57
2022-04-13 21:00 | 57
2022-04-13 22:00 | 56
2022-04-13 23:00 | 56
2022-04-14 | 57
2022-04-14 01:00 | 55
2022-04-14 02:00 | 54
2022-04-14 03:00 | 53
2022-04-14 04:00 | 53
2022-04-14 05:00 | 53
2022-04-14 06:00 | 54
2022-04-14 07:00 | 54
2022-04-14 08:00 | 58
2022-04-14 09:00 | 62
2022-04-14 10:00 | 62
2022-04-14 11:00 | 65
2022-04-14 12:00 | 67
2022-04-14 13:00 | 67
2022-04-14 14:00 | 67
2022-04-14 15:00 | 68
2022-04-14 16:00 | 66
2022-04-14 17:00 | 66
2022-04-14 18:00 | 62
2022-04-14 19:00 | 68
2022-04-14 20:00 | 63
2022-04-14 21:00 | 62
2022-04-14 22:00 | 63
2022-04-14 23:00 | 62
2022-04-15 | 61
2022-04-15 01:00 | 60
2022-04-15 02:00 | 57
2022-04-15 03:00 | 54
2022-04-15 04:00 | 54
2022-04-15 05:00 | 53
2022-04-15 06:00 | 49
2022-04-15 07:00 | 47
2022-04-15 08:00 | 55
2022-04-15 09:00 | 58
2022-04-15 10:00 | 62
2022-04-15 11:00 | 63
2022-04-15 12:00 | 65
2022-04-15 13:00 | 64
2022-04-15 14:00 | 66
2022-04-15 15:00 | 64
2022-04-15 16:00 | 61
2022-04-15 17:00 | 59
2022-04-15 18:00 | 58
2022-04-15 19:00 | 55
2022-04-15 20:00 | 53
2022-04-15 21:00 | 54
2022-04-15 22:00 | 54
2022-04-15 23:00 | 52
2022-04-16 | 51
2022-04-16 01:00 | 50
2022-04-16 02:00 | 51
2022-04-16 03:00 | 50
2022-04-16 04:00 | 50
2022-04-16 05:00 | 50
2022-04-16 06:00 | 51
2022-04-16 07:00 | 51
2022-04-16 08:00 | 53
2022-04-16 09:00 | 55
2022-04-16 10:00 | 57
2022-04-16 11:00 | 56
2022-04-16 12:00 | 57
2022-04-16 13:00 | 61
2022-04-16 14:00 | 59
2022-04-16 15:00 | 59
2022-04-16 16:00 | 57
2022-04-16 17:00 | 57
2022-04-16 18:00 | 55
2022-04-16 19:00 | 54
2022-04-16 20:00 | 56
2022-04-16 21:00 | 53
2022-04-16 22:00 | 50
2022-04-16 23:00 | 46
2022-04-17 | 45
2022-04-17 01:00 | 45
2022-04-17 02:00 | 45
2022-04-17 03:00 | 45
2022-04-17 04:00 | 45
2022-04-17 05:00 | 44
2022-04-17 06:00 | 43
2022-04-17 07:00 | 43
2022-04-17 08:00 | 44
2022-04-17 09:00 | 46
2022-04-17 10:00 | 47
2022-04-17 11:00 | 48
2022-04-17 12:00 | 49
2022-04-17 13:00 | 49
2022-04-17 14:00 | 51
2022-04-17 15:00 | 48
2022-04-17 16:00 | 49
2022-04-17 17:00 | 49
2022-04-17 18:00 | 48
2022-04-17 19:00 | 48
2022-04-17 20:00 | 46
2022-04-17 21:00 | 45
2022-04-17 22:00 | 45
2022-04-17 23:00 | 43
2022-04-18 | 41
2022-04-18 01:00 | 40
2022-04-18 02:00 | 41
2022-04-18 03:00 | 39
2022-04-18 04:00 | 38
2022-04-18 05:00 | 38
2022-04-18 06:00 | 38
2022-04-18 07:00 | 40
2022-04-18 08:00 | 44
2022-04-18 09:00 | 47
2022-04-18 10:00 | 50
2022-04-18 11:00 | 50
2022-04-18 12:00 | 50
2022-04-18 13:00 | 50
2022-04-18 14:00 | 48
2022-04-18 15:00 | 48
2022-04-18 16:00 | 47
2022-04-18 17:00 | 47
2022-04-18 18:00 | 46
2022-04-18 19:00 | 46
2022-04-18 20:00 | 46
2022-04-18 21:00 | 46
2022-04-18 22:00 | 44
2022-04-18 23:00 | 42
2022-04-19 | 44
2022-04-19 01:00 | 45
2022-04-19 02:00 | 46
2022-04-19 03:00 | 48
2022-04-19 04:00 | 49
2022-04-19 05:00 | 47
2022-04-19 06:00 | 44
2022-04-19 07:00 | 41
2022-04-19 08:00 | 43
2022-04-19 09:00 | 43
2022-04-19 10:00 | 45
2022-04-19 11:00 | 45
2022-04-19 12:00 | 46
2022-04-19 13:00 | 48
2022-04-19 14:00 | 49
2022-04-19 15:00 | 50
2022-04-19 16:00 | 50
2022-04-19 17:00 | 51
2022-04-19 18:00 | 50
2022-04-19 19:00 | 48
2022-04-19 20:00 | 44
2022-04-19 21:00 | 45
2022-04-19 22:00 | 45
2022-04-19 23:00 | 44
2022-04-20 | 44
2022-04-20 01:00 | 43
2022-04-20 02:00 | 43
2022-04-20 03:00 | 42
2022-04-20 04:00 | 42
2022-04-20 05:00 | 42
2022-04-20 06:00 | 41
2022-04-20 07:00 | 43
2022-04-20 08:00 | 45
2022-04-20 09:00 | 48
2022-04-20 10:00 | 50
2022-04-20 11:00 | 51
2022-04-20 12:00 | 54
2022-04-20 13:00 | 55
2022-04-20 14:00 | 56
2022-04-20 15:00 | 57
2022-04-20 16:00 | 59
2022-04-20 17:00 | 58
2022-04-20 18:00 | 51
2022-04-20 19:00 | 49
2022-04-20 20:00 | 48
2022-04-20 21:00 | 47
2022-04-20 22:00 | 47
2022-04-20 23:00 | 46
2022-04-21 | 43
2022-04-21 01:00 | 42
2022-04-21 02:00 | 41
2022-04-21 03:00 | 40
2022-04-21 04:00 | 40
2022-04-21 05:00 | 41
2022-04-21 06:00 | 43
2022-04-21 07:00 | 45
2022-04-21 08:00 | 48
2022-04-21 09:00 | 51
2022-04-21 10:00 | 52
2022-04-21 11:00 | 53
2022-04-21 12:00 | 55
2022-04-21 13:00 | 54
2022-04-21 14:00 | 55
2022-04-21 15:00 | 53
2022-04-21 16:00 | 51
2022-04-21 17:00 | 51
2022-04-21 18:00 | 50
2022-04-21 19:00 | 50
2022-04-21 20:00 | 51
2022-04-21 21:00 | 51
2022-04-21 22:00 | 51
2022-04-21 23:00 | 51
2022-04-22 | 48
2022-04-22 01:00 | 47
2022-04-22 02:00 | 46
2022-04-22 03:00 | 47
2022-04-22 04:00 | 46
2022-04-22 05:00 | 46
2022-04-22 06:00 | 48
2022-04-22 07:00 | 51
2022-04-22 08:00 | 57
2022-04-22 09:00 | 61
2022-04-22 10:00 | 63
2022-04-22 11:00 | 65
2022-04-22 12:00 | 66
2022-04-22 13:00 | 68
2022-04-22 14:00 | 69
2022-04-22 15:00 | 69
2022-04-22 16:00 | 69
2022-04-22 17:00 | 69
2022-04-22 18:00 | 68
2022-04-22 19:00 | 66
2022-04-22 20:00 | 63
2022-04-22 21:00 | 62
2022-04-22 22:00 | 61
2022-04-22 23:00 | 58
2022-04-23 | 55
2022-04-23 01:00 | 52
2022-04-23 02:00 | 52
2022-04-23 03:00 | 50
2022-04-23 04:00 | 50
2022-04-23 05:00 | 50
2022-04-23 06:00 | 50
2022-04-23 07:00 | 51
2022-04-23 08:00 | 51
2022-04-23 09:00 | 53
2022-04-23 10:00 | 57
2022-04-23 11:00 | 59
2022-04-23 12:00 | 58
2022-04-23 13:00 | 59
2022-04-23 14:00 | 58
2022-04-23 15:00 | 57
2022-04-23 16:00 | 57
2022-04-23 17:00 | 56
2022-04-23 18:00 | 54
2022-04-23 19:00 | 52
2022-04-23 20:00 | 52
2022-04-23 21:00 | 52
2022-04-23 22:00 | 52
2022-04-23 23:00 | 52
2022-04-24 | 52
2022-04-24 01:00 | 51
2022-04-24 02:00 | 51
2022-04-24 03:00 | 50
2022-04-24 04:00 | 50
2022-04-24 05:00 | 50
2022-04-24 06:00 | 48
2022-04-24 07:00 | 50
2022-04-24 08:00 | 55
2022-04-24 09:00 | 59
2022-04-24 10:00 | 56
2022-04-24 11:00 | 56
2022-04-24 12:00 | 56
2022-04-24 13:00 | 53
2022-04-24 14:00 | 54
2022-04-24 15:00 | 54
2022-04-24 16:00 | 53
2022-04-24 17:00 | 52
2022-04-24 18:00 | 50
2022-04-24 19:00 | 49
2022-04-24 20:00 | 47
2022-04-24 21:00 | 46
2022-04-24 22:00 | 46
2022-04-24 23:00 | 46
2022-04-25 | 45
2022-04-25 01:00 | 45
2022-04-25 02:00 | 45
2022-04-25 03:00 | 45
2022-04-25 04:00 | 46
2022-04-25 05:00 | 45
2022-04-25 06:00 | 44
2022-04-25 07:00 | 46
2022-04-25 08:00 | 49
2022-04-25 09:00 | 52
2022-04-25 10:00 | 54
2022-04-25 11:00 | 55
2022-04-25 12:00 | 54
2022-04-25 13:00 | 54
2022-04-25 14:00 | 54
2022-04-25 15:00 | 54
2022-04-25 16:00 | 53
2022-04-25 17:00 | 54
2022-04-25 18:00 | 53
2022-04-25 19:00 | 51
2022-04-25 20:00 | 51
2022-04-25 21:00 | 50
2022-04-25 22:00 | 51
2022-04-25 23:00 | 50
2022-04-26 | 51
2022-04-26 01:00 | 51
2022-04-26 02:00 | 51
2022-04-26 03:00 | 51
2022-04-26 04:00 | 51
2022-04-26 05:00 | 52
2022-04-26 06:00 | 52
2022-04-26 07:00 | 51
2022-04-26 08:00 | 52
2022-04-26 09:00 | 53
2022-04-26 10:00 | 54
2022-04-26 11:00 | 56
2022-04-26 12:00 | 58
2022-04-26 13:00 | 59
2022-04-26 14:00 | 59
2022-04-26 15:00 | 58
2022-04-26 16:00 | 57
2022-04-26 17:00 | 57
2022-04-26 18:00 | 58
2022-04-26 19:00 | 56
2022-04-26 20:00 | 55
2022-04-26 21:00 | 56
2022-04-26 22:00 | 56
2022-04-26 23:00 | 55
2022-04-27 | 54
2022-04-27 01:00 | 54
2022-04-27 02:00 | 57
2022-04-27 03:00 | 52
2022-04-27 04:00 | 50
2022-04-27 05:00 | 49
2022-04-27 06:00 | 49
2022-04-27 07:00 | 49
2022-04-27 08:00 | 50
2022-04-27 09:00 | 52
2022-04-27 10:00 | 54
2022-04-27 11:00 | 55
2022-04-27 12:00 | 54
2022-04-27 13:00 | 55
2022-04-27 14:00 | 54
2022-04-27 15:00 | 56
2022-04-27 16:00 | 56
2022-04-27 17:00 | 54
2022-04-27 18:00 | 52
2022-04-27 19:00 | 50
2022-04-27 20:00 | 48
2022-04-27 21:00 | 46
2022-04-27 22:00 | 44
2022-04-27 23:00 | 43
2022-04-28 | 42
2022-04-28 01:00 | 41
2022-04-28 02:00 | 41
2022-04-28 03:00 | 41
2022-04-28 04:00 | 41
2022-04-28 05:00 | 41
2022-04-28 06:00 | 40
2022-04-28 07:00 | 41
2022-04-28 08:00 | 43
2022-04-28 09:00 | 44
2022-04-28 10:00 | 47
2022-04-28 11:00 | 50
2022-04-28 12:00 | 52
2022-04-28 13:00 | 54
2022-04-28 14:00 | 57
2022-04-28 15:00 | 57
2022-04-28 16:00 | 57
2022-04-28 17:00 | 57
2022-04-28 18:00 | 56
2022-04-28 19:00 | 54
2022-04-28 20:00 | 52
2022-04-28 21:00 | 50
2022-04-28 22:00 | 48
2022-04-28 23:00 | 47
2022-04-29 | 46
2022-04-29 01:00 | 45
2022-04-29 02:00 | 44
2022-04-29 03:00 | 44
2022-04-29 04:00 | 43
2022-04-29 05:00 | 42
2022-04-29 06:00 | 42
2022-04-29 07:00 | 43
2022-04-29 08:00 | 45
2022-04-29 09:00 | 47
2022-04-29 10:00 | 50
2022-04-29 11:00 | 52
2022-04-29 12:00 | 56
2022-04-29 13:00 | 59
2022-04-29 14:00 | 60
2022-04-29 15:00 | 62
2022-04-29 16:00 | 63
2022-04-29 17:00 | 63
2022-04-29 18:00 | 62
2022-04-29 19:00 | 60
2022-04-29 20:00 | 58
2022-04-29 21:00 | 56
2022-04-29 22:00 | 55
2022-04-29 23:00 | 53
2022-04-30 | 51
2022-04-30 01:00 | 50
2022-04-30 02:00 | 49
2022-04-30 03:00 | 47
2022-04-30 04:00 | 46
2022-04-30 05:00 | 45
2022-04-30 06:00 | 44
2022-04-30 07:00 | 46
2022-04-30 08:00 | 50
2022-04-30 09:00 | 53
2022-04-30 10:00 | 55
2022-04-30 11:00 | 58
2022-04-30 12:00 | 60
2022-04-30 13:00 | 62
2022-04-30 14:00 | 61
2022-04-30 15:00 | 64
2022-04-30 16:00 | 66
2022-04-30 17:00 | 59
2022-04-30 18:00 | 55
2022-04-30 19:00 | 53
2022-04-30 20:00 | 51
2022-04-30 21:00 | 51
2022-04-30 22:00 | 50
2022-04-30 23:00 | 47
2022-05-01 | 46
2022-05-01 01:00 | 45
2022-05-01 02:00 | 46
2022-05-01 03:00 | 44
2022-05-01 04:00 | 47
2022-05-01 05:00 | 45
2022-05-01 06:00 | 42
2022-05-01 07:00 | 45
2022-05-01 08:00 | 51
2022-05-01 09:00 | 57
2022-05-01 10:00 | 61
2022-05-01 11:00 | 60
2022-05-01 12:00 | 59
2022-05-01 13:00 | 61
2022-05-01 14:00 | 62
2022-05-01 15:00 | 62
2022-05-01 16:00 | 60
2022-05-01 17:00 | 58
2022-05-01 18:00 | 57
2022-05-01 19:00 | 55
2022-05-01 20:00 | 55
2022-05-01 21:00 | 54
2022-05-01 22:00 | 54
2022-05-01 23:00 | 53
2022-05-02 | 52
2022-05-02 01:00 | 53
2022-05-02 02:00 | 53
2022-05-02 03:00 | 53
2022-05-02 04:00 | 54
2022-05-02 05:00 | 52
2022-05-02 06:00 | 52
2022-05-02 07:00 | 52
2022-05-02 08:00 | 55
2022-05-02 09:00 | 54
2022-05-02 10:00 | 54
2022-05-02 11:00 | 55
2022-05-02 12:00 | 54
2022-05-02 13:00 | 53
2022-05-02 14:00 | 54
2022-05-02 15:00 | 55
2022-05-02 16:00 | 55
2022-05-02 17:00 | 55
2022-05-02 18:00 | 54
2022-05-02 19:00 | 52
2022-05-02 20:00 | 52
2022-05-02 21:00 | 52
2022-05-02 22:00 | 51
2022-05-02 23:00 | 51
2022-05-03 | 50
2022-05-03 01:00 | 52
2022-05-03 02:00 | 51
2022-05-03 03:00 | 51
2022-05-03 04:00 | 52
2022-05-03 05:00 | 51
2022-05-03 06:00 | 50
2022-05-03 07:00 | 52
2022-05-03 08:00 | 54
2022-05-03 09:00 | 55
2022-05-03 10:00 | 57
2022-05-03 11:00 | 59
2022-05-03 12:00 | 60
2022-05-03 13:00 | 61
2022-05-03 14:00 | 61
2022-05-03 15:00 | 59
2022-05-03 16:00 | 57
2022-05-03 17:00 | 56
2022-05-03 18:00 | 54
2022-05-03 19:00 | 53
2022-05-03 20:00 | 51
2022-05-03 21:00 | 51
2022-05-03 22:00 | 51
2022-05-03 23:00 | 50
2022-05-04 | 49
2022-05-04 01:00 | 49
2022-05-04 02:00 | 49
2022-05-04 03:00 | 49
2022-05-04 04:00 | 49
2022-05-04 05:00 | 49
2022-05-04 06:00 | 50
2022-05-04 07:00 | 50
2022-05-04 08:00 | 51
2022-05-04 09:00 | 52
2022-05-04 10:00 | 52
2022-05-04 11:00 | 53
2022-05-04 12:00 | 54
2022-05-04 13:00 | 58
2022-05-04 14:00 | 59
2022-05-04 15:00 | 61
2022-05-04 16:00 | 59
2022-05-04 17:00 | 63
2022-05-04 18:00 | 63
2022-05-04 19:00 | 65
2022-05-04 20:00 | 57
2022-05-04 21:00 | 55
2022-05-04 22:00 | 56
2022-05-04 23:00 | 55
2022-05-05 | 60
2022-05-05 01:00 | 60
2022-05-05 02:00 | 59
2022-05-05 03:00 | 59
2022-05-05 04:00 | 58
2022-05-05 05:00 | 58
2022-05-05 06:00 | 56
2022-05-05 07:00 | 57
2022-05-05 08:00 | 59
2022-05-05 09:00 | 62
2022-05-05 10:00 | 64
2022-05-05 11:00 | 65
2022-05-05 12:00 | 67
2022-05-05 13:00 | 68
2022-05-05 14:00 | 65
2022-05-05 15:00 | 65
2022-05-05 16:00 | 66
2022-05-05 17:00 | 63
2022-05-05 18:00 | 61
2022-05-05 19:00 | 59
2022-05-05 20:00 | 57
2022-05-05 21:00 | 56
2022-05-05 22:00 | 55
2022-05-05 23:00 | 54
2022-05-06 | 54
2022-05-06 01:00 | 54
2022-05-06 02:00 | 55
2022-05-06 03:00 | 55
2022-05-06 04:00 | 55
2022-05-06 05:00 | 56
2022-05-06 06:00 | 56
2022-05-06 07:00 | 54
2022-05-06 08:00 | 55
2022-05-06 09:00 | 56
2022-05-06 10:00 | 58
2022-05-06 11:00 | 56
2022-05-06 12:00 | 56
2022-05-06 13:00 | 56
2022-05-06 14:00 | 56
2022-05-06 15:00 | 55
2022-05-06 16:00 | 53
2022-05-06 17:00 | 52
2022-05-06 18:00 | 51
2022-05-06 19:00 | 50
2022-05-06 20:00 | 49
2022-05-06 21:00 | 49
2022-05-06 22:00 | 49
2022-05-06 23:00 | 49
2022-05-07 | 49
2022-05-07 01:00 | 49
2022-05-07 02:00 | 50
2022-05-07 03:00 | 50
2022-05-07 04:00 | 50
2022-05-07 05:00 | 51
2022-05-07 06:00 | 50
2022-05-07 07:00 | 50
2022-05-07 08:00 | 50
2022-05-07 09:00 | 50
2022-05-07 10:00 | 50
2022-05-07 11:00 | 50
2022-05-07 12:00 | 49
2022-05-07 13:00 | 48
2022-05-07 14:00 | 47
2022-05-07 15:00 | 47
2022-05-07 16:00 | 45
2022-05-07 17:00 | 46
2022-05-07 18:00 | 46
2022-05-07 19:00 | 46
2022-05-07 20:00 | 47
2022-05-07 21:00 | 47
2022-05-07 22:00 | 47
2022-05-07 23:00 | 46
2022-05-08 | 45
2022-05-08 01:00 | 44
2022-05-08 02:00 | 45
2022-05-08 03:00 | 46
2022-05-08 04:00 | 47
2022-05-08 05:00 | 47
2022-05-08 06:00 | 47
2022-05-08 07:00 | 47
2022-05-08 08:00 | 48
2022-05-08 09:00 | 49
2022-05-08 10:00 | 51
2022-05-08 11:00 | 51
2022-05-08 12:00 | 53
2022-05-08 13:00 | 54
2022-05-08 14:00 | 57
2022-05-08 15:00 | 58
2022-05-08 16:00 | 58
2022-05-08 17:00 | 57
2022-05-08 18:00 | 57
2022-05-08 19:00 | 55
2022-05-08 20:00 | 55
2022-05-08 21:00 | 53
2022-05-08 22:00 | 52
2022-05-08 23:00 | 51
2022-05-09 | 51
2022-05-09 01:00 | 49
2022-05-09 02:00 | 48
2022-05-09 03:00 | 46
2022-05-09 04:00 | 46
2022-05-09 05:00 | 45
2022-05-09 06:00 | 45
2022-05-09 07:00 | 47
2022-05-09 08:00 | 50
2022-05-09 09:00 | 53
2022-05-09 10:00 | 56
2022-05-09 11:00 | 59
2022-05-09 12:00 | 62
2022-05-09 13:00 | 64
2022-05-09 14:00 | 66
2022-05-09 15:00 | 68
2022-05-09 16:00 | 69
2022-05-09 17:00 | 70
2022-05-09 18:00 | 68
2022-05-09 19:00 | 65
2022-05-09 20:00 | 62
2022-05-09 21:00 | 60
2022-05-09 22:00 | 59
2022-05-09 23:00 | 55
2022-05-10 | 54
2022-05-10 01:00 | 53
2022-05-10 02:00 | 52
2022-05-10 03:00 | 51
2022-05-10 04:00 | 51
2022-05-10 05:00 | 51
2022-05-10 06:00 | 51
2022-05-10 07:00 | 52
2022-05-10 08:00 | 55
2022-05-10 09:00 | 58
2022-05-10 10:00 | 61
2022-05-10 11:00 | 64
2022-05-10 12:00 | 66
2022-05-10 13:00 | 69
2022-05-10 14:00 | 71
2022-05-10 15:00 | 73
2022-05-10 16:00 | 71
2022-05-10 17:00 | 64
2022-05-10 18:00 | 66
2022-05-10 19:00 | 67
2022-05-10 20:00 | 64
2022-05-10 21:00 | 63
2022-05-10 22:00 | 60
2022-05-10 23:00 | 58
2022-05-11 | 57
2022-05-11 01:00 | 55
2022-05-11 02:00 | 54
2022-05-11 03:00 | 54
2022-05-11 04:00 | 53
2022-05-11 05:00 | 53
2022-05-11 06:00 | 54
2022-05-11 07:00 | 55
2022-05-11 08:00 | 57
2022-05-11 09:00 | 58
2022-05-11 10:00 | 61
2022-05-11 11:00 | 65
2022-05-11 12:00 | 68
2022-05-11 13:00 | 68
2022-05-11 14:00 | 71
2022-05-11 15:00 | 72
2022-05-11 16:00 | 68
2022-05-11 17:00 | 62
2022-05-11 18:00 | 62
2022-05-11 19:00 | 60
2022-05-11 20:00 | 57
2022-05-11 21:00 | 55
2022-05-11 22:00 | 55
2022-05-11 23:00 | 56
2022-05-12 | 58
2022-05-12 01:00 | 55
2022-05-12 02:00 | 54
2022-05-12 03:00 | 56
2022-05-12 04:00 | 56
2022-05-12 05:00 | 58
2022-05-12 06:00 | 61
2022-05-12 07:00 | 57
2022-05-12 08:00 | 57
2022-05-12 09:00 | 61
2022-05-12 10:00 | 64
2022-05-12 11:00 | 62
2022-05-12 12:00 | 66
2022-05-12 13:00 | 70
2022-05-12 14:00 | 69
2022-05-12 15:00 | 68
2022-05-12 16:00 | 68
2022-05-12 17:00 | 68
2022-05-12 18:00 | 65
2022-05-12 19:00 | 61
2022-05-12 20:00 | 60
2022-05-12 21:00 | 59
2022-05-12 22:00 | 60
2022-05-12 23:00 | 59
2022-05-13 | 56
2022-05-13 01:00 | 57
2022-05-13 02:00 | 58
2022-05-13 03:00 | 59
2022-05-13 04:00 | 60
2022-05-13 05:00 | 61
2022-05-13 06:00 | 59
2022-05-13 07:00 | 59
2022-05-13 08:00 | 60
2022-05-13 09:00 | 61
2022-05-13 10:00 | 62
2022-05-13 11:00 | 66
2022-05-13 12:00 | 68
2022-05-13 13:00 | 73
2022-05-13 14:00 | 74
2022-05-13 15:00 | 68
2022-05-13 16:00 | 68
2022-05-13 17:00 | 66
2022-05-13 18:00 | 64
2022-05-13 19:00 | 61
2022-05-13 20:00 | 59
2022-05-13 21:00 | 58
2022-05-13 22:00 | 58
2022-05-13 23:00 | 58
2022-05-14 | 58
2022-05-14 01:00 | 58
2022-05-14 02:00 | 59
2022-05-14 03:00 | 59
2022-05-14 04:00 | 59
2022-05-14 05:00 | 58
2022-05-14 06:00 | 59
2022-05-14 07:00 | 60
2022-05-14 08:00 | 60
2022-05-14 09:00 | 62
2022-05-14 10:00 | 65
2022-05-14 11:00 | 68
2022-05-14 12:00 | 69
2022-05-14 13:00 | 67
2022-05-14 14:00 | 68
2022-05-14 15:00 | 66
2022-05-14 16:00 | 61
2022-05-14 17:00 | 64
2022-05-14 18:00 | 63
2022-05-14 19:00 | 62
2022-05-14 20:00 | 59
2022-05-14 21:00 | 58
2022-05-14 22:00 | 59
2022-05-14 23:00 | 61
2022-05-15 | 60
2022-05-15 01:00 | 58
2022-05-15 02:00 | 57
2022-05-15 03:00 | 57
2022-05-15 04:00 | 56
2022-05-15 05:00 | 56
2022-05-15 06:00 | 55
2022-05-15 07:00 | 57
2022-05-15 08:00 | 58
2022-05-15 09:00 | 60
2022-05-15 10:00 | 61
2022-05-15 11:00 | 64
2022-05-15 12:00 | 70
2022-05-15 13:00 | 71
2022-05-15 14:00 | 70
2022-05-15 15:00 | 68
2022-05-15 16:00 | 68
2022-05-15 17:00 | 67
2022-05-15 18:00 | 65
2022-05-15 19:00 | 64
2022-05-15 20:00 | 62
2022-05-15 21:00 | 60
2022-05-15 22:00 | 59
2022-05-15 23:00 | 60
2022-05-16 | 60
2022-05-16 01:00 | 60
2022-05-16 02:00 | 61
2022-05-16 03:00 | 63
2022-05-16 04:00 | 60
2022-05-16 05:00 | 59
2022-05-16 06:00 | 60
2022-05-16 07:00 | 63
2022-05-16 08:00 | 63
2022-05-16 09:00 | 61
2022-05-16 10:00 | 67
2022-05-16 11:00 | 66
2022-05-16 12:00 | 69
2022-05-16 13:00 | 68
2022-05-16 14:00 | 67
2022-05-16 15:00 | 64
2022-05-16 16:00 | 63
2022-05-16 17:00 | 64
2022-05-16 18:00 | 62
2022-05-16 19:00 | 61
2022-05-16 20:00 | 62
2022-05-16 21:00 | 66
2022-05-16 22:00 | 64
2022-05-16 23:00 | 63
2022-05-17 | 64
2022-05-17 01:00 | 62
2022-05-17 02:00 | 60
2022-05-17 03:00 | 60
2022-05-17 04:00 | 59
2022-05-17 05:00 | 58
2022-05-17 06:00 | 57
2022-05-17 07:00 | 60
2022-05-17 08:00 | 62
2022-05-17 09:00 | 63
2022-05-17 10:00 | 67
2022-05-17 11:00 | 69
2022-05-17 12:00 | 71
2022-05-17 13:00 | 77
2022-05-17 14:00 | 77
2022-05-17 15:00 | 78
2022-05-17 16:00 | 77
2022-05-17 17:00 | 76
2022-05-17 18:00 | 77
2022-05-17 19:00 | 75
2022-05-17 20:00 | 72
2022-05-17 21:00 | 69
2022-05-17 22:00 | 66
2022-05-17 23:00 | 63
2022-05-18 | 62
2022-05-18 01:00 | 60
2022-05-18 02:00 | 59
2022-05-18 03:00 | 59
2022-05-18 04:00 | 58
2022-05-18 05:00 | 57
2022-05-18 06:00 | 56
2022-05-18 07:00 | 57
2022-05-18 08:00 | 60
2022-05-18 09:00 | 63
2022-05-18 10:00 | 63
2022-05-18 11:00 | 65
2022-05-18 12:00 | 66
2022-05-18 13:00 | 68
2022-05-18 14:00 | 69
2022-05-18 15:00 | 68
2022-05-18 16:00 | 70
2022-05-18 17:00 | 66
2022-05-18 18:00 | 61
2022-05-18 19:00 | 61
2022-05-18 20:00 | 59
2022-05-18 21:00 | 58
2022-05-18 22:00 | 58
2022-05-18 23:00 | 58
2022-05-19 | 59
2022-05-19 01:00 | 58
2022-05-19 02:00 | 58
2022-05-19 03:00 | 57
2022-05-19 04:00 | 56
2022-05-19 05:00 | 54
2022-05-19 06:00 | 54
2022-05-19 07:00 | 54
2022-05-19 08:00 | 54
2022-05-19 09:00 | 54
2022-05-19 10:00 | 55
2022-05-19 11:00 | 55
2022-05-19 12:00 | 56
2022-05-19 13:00 | 56
2022-05-19 14:00 | 58
2022-05-19 15:00 | 59
2022-05-19 16:00 | 60
2022-05-19 17:00 | 61
2022-05-19 18:00 | 62
2022-05-19 19:00 | 60
2022-05-19 20:00 | 57
2022-05-19 21:00 | 56
2022-05-19 22:00 | 56
2022-05-19 23:00 | 55
2022-05-20 | 54
2022-05-20 01:00 | 55
2022-05-20 02:00 | 54
2022-05-20 03:00 | 53
2022-05-20 04:00 | 54
2022-05-20 05:00 | 54
2022-05-20 06:00 | 53
2022-05-20 07:00 | 56
2022-05-20 08:00 | 59
2022-05-20 09:00 | 61
2022-05-20 10:00 | 63
2022-05-20 11:00 | 67
2022-05-20 12:00 | 65
2022-05-20 13:00 | 59
2022-05-20 14:00 | 61
2022-05-20 15:00 | 66
2022-05-20 16:00 | 63
2022-05-20 17:00 | 63
2022-05-20 18:00 | 62
2022-05-20 19:00 | 63
2022-05-20 20:00 | 63
2022-05-20 21:00 | 64
2022-05-20 22:00 | 63
2022-05-20 23:00 | 63
2022-05-21 | 61
2022-05-21 01:00 | 61
2022-05-21 02:00 | 59
2022-05-21 03:00 | 59
2022-05-21 04:00 | 60
2022-05-21 05:00 | 60
2022-05-21 06:00 | 60
2022-05-21 07:00 | 62
2022-05-21 08:00 | 63
2022-05-21 09:00 | 65
2022-05-21 10:00 | 72
2022-05-21 11:00 | 77
2022-05-21 12:00 | 82
2022-05-21 13:00 | 86
2022-05-21 14:00 | 77
2022-05-21 15:00 | 73
2022-05-21 16:00 | 74
2022-05-21 17:00 | 77
2022-05-21 18:00 | 77
2022-05-21 19:00 | 78
2022-05-21 20:00 | 76
2022-05-21 21:00 | 75
2022-05-21 22:00 | 71
2022-05-21 23:00 | 71
2022-05-22 | 74
2022-05-22 01:00 | 69
2022-05-22 02:00 | 69
2022-05-22 03:00 | 67
2022-05-22 04:00 | 65
2022-05-22 05:00 | 65
2022-05-22 06:00 | 66
2022-05-22 07:00 | 67
2022-05-22 08:00 | 69
2022-05-22 09:00 | 70
2022-05-22 10:00 | 78
2022-05-22 11:00 | 82
2022-05-22 12:00 | 80
2022-05-22 13:00 | 78
2022-05-22 14:00 | 82
2022-05-22 15:00 | 79
2022-05-22 16:00 | 76
2022-05-22 17:00 | 74
2022-05-22 18:00 | 73
2022-05-22 19:00 | 71
2022-05-22 20:00 | 69
2022-05-22 21:00 | 70
2022-05-22 22:00 | 73
2022-05-22 23:00 | 77
2022-05-23 | 74
2022-05-23 01:00 | 73
2022-05-23 02:00 | 72
2022-05-23 03:00 | 69
2022-05-23 04:00 | 67
2022-05-23 05:00 | 65
2022-05-23 06:00 | 64
2022-05-23 07:00 | 63
2022-05-23 08:00 | 65
2022-05-23 09:00 | 65
2022-05-23 10:00 | 66
2022-05-23 11:00 | 68
2022-05-23 12:00 | 70
2022-05-23 13:00 | 71
2022-05-23 14:00 | 73
2022-05-23 15:00 | 73
2022-05-23 16:00 | 74
2022-05-23 17:00 | 74
2022-05-23 18:00 | 72
2022-05-23 19:00 | 71
2022-05-23 20:00 | 70
2022-05-23 21:00 | 64
2022-05-23 22:00 | 63
2022-05-23 23:00 | 63
2022-05-24 | 61
2022-05-24 01:00 | 61
2022-05-24 02:00 | 61
2022-05-24 03:00 | 60
2022-05-24 04:00 | 59
2022-05-24 05:00 | 58
2022-05-24 06:00 | 59
2022-05-24 07:00 | 60
2022-05-24 08:00 | 60
2022-05-24 09:00 | 62
2022-05-24 10:00 | 63
2022-05-24 11:00 | 63
2022-05-24 12:00 | 62
2022-05-24 13:00 | 63
2022-05-24 14:00 | 65
2022-05-24 15:00 | 67
2022-05-24 16:00 | 65
2022-05-24 17:00 | 66
2022-05-24 18:00 | 62
2022-05-24 19:00 | 59
2022-05-24 20:00 | 58
2022-05-24 21:00 | 58
2022-05-24 22:00 | 57
2022-05-24 23:00 | 55
2022-05-25 | 54
2022-05-25 01:00 | 54
2022-05-25 02:00 | 54
2022-05-25 03:00 | 54
2022-05-25 04:00 | 52
2022-05-25 05:00 | 52
2022-05-25 06:00 | 52
2022-05-25 07:00 | 55
2022-05-25 08:00 | 58
2022-05-25 09:00 | 60
2022-05-25 10:00 | 62
2022-05-25 11:00 | 64
2022-05-25 12:00 | 65
2022-05-25 13:00 | 64
2022-05-25 14:00 | 64
2022-05-25 15:00 | 63
2022-05-25 16:00 | 63
2022-05-25 17:00 | 61
2022-05-25 18:00 | 59
2022-05-25 19:00 | 59
2022-05-25 20:00 | 56
2022-05-25 21:00 | 55
2022-05-25 22:00 | 55
2022-05-25 23:00 | 54
2022-05-26 | 54
2022-05-26 01:00 | 53
2022-05-26 02:00 | 52
2022-05-26 03:00 | 53
2022-05-26 04:00 | 54
2022-05-26 05:00 | 53
2022-05-26 06:00 | 53
2022-05-26 07:00 | 56
2022-05-26 08:00 | 59
2022-05-26 09:00 | 61
2022-05-26 10:00 | 63
2022-05-26 11:00 | 64
2022-05-26 12:00 | 65
2022-05-26 13:00 | 66
2022-05-26 14:00 | 66
2022-05-26 15:00 | 64
2022-05-26 16:00 | 66
2022-05-26 17:00 | 65
2022-05-26 18:00 | 64
2022-05-26 19:00 | 63
2022-05-26 20:00 | 63
2022-05-26 21:00 | 62
2022-05-26 22:00 | 62
2022-05-26 23:00 | 63
2022-05-27 | 62
2022-05-27 01:00 | 62
2022-05-27 02:00 | 63
2022-05-27 03:00 | 62
2022-05-27 04:00 | 62
2022-05-27 05:00 | 62
2022-05-27 06:00 | 62
2022-05-27 07:00 | 62
2022-05-27 08:00 | 62
2022-05-27 09:00 | 64
2022-05-27 10:00 | 66
2022-05-27 11:00 | 69
2022-05-27 12:00 | 70
2022-05-27 13:00 | 71
2022-05-27 14:00 | 72
2022-05-27 15:00 | 70
2022-05-27 16:00 | 71
2022-05-27 17:00 | 66
2022-05-27 18:00 | 66
2022-05-27 19:00 | 66
2022-05-27 20:00 | 64
2022-05-27 21:00 | 64
2022-05-27 22:00 | 64
2022-05-27 23:00 | 63
2022-05-28 | 63
2022-05-28 01:00 | 63
2022-05-28 02:00 | 64
2022-05-28 03:00 | 63
2022-05-28 04:00 | 63
2022-05-28 05:00 | 64
2022-05-28 06:00 | 66
2022-05-28 07:00 | 65
2022-05-28 08:00 | 65
2022-05-28 09:00 | 66
2022-05-28 10:00 | 67
2022-05-28 11:00 | 69
2022-05-28 12:00 | 73
2022-05-28 13:00 | 70
2022-05-28 14:00 | 69
2022-05-28 15:00 | 72
2022-05-28 16:00 | 74
2022-05-28 17:00 | 72
2022-05-28 18:00 | 72
2022-05-28 19:00 | 74
2022-05-28 20:00 | 73
2022-05-28 21:00 | 72
2022-05-28 22:00 | 71
2022-05-28 23:00 | 70
2022-05-29 | 67
2022-05-29 01:00 | 66
2022-05-29 02:00 | 64
2022-05-29 03:00 | 63
2022-05-29 04:00 | 62
2022-05-29 05:00 | 62
2022-05-29 06:00 | 61
2022-05-29 07:00 | 64
2022-05-29 08:00 | 67
2022-05-29 09:00 | 70
2022-05-29 10:00 | 72
2022-05-29 11:00 | 71
2022-05-29 12:00 | 72
2022-05-29 13:00 | 73
2022-05-29 14:00 | 73
2022-05-29 15:00 | 74
2022-05-29 16:00 | 74
2022-05-29 17:00 | 71
2022-05-29 18:00 | 69
2022-05-29 19:00 | 66
2022-05-29 20:00 | 65
2022-05-29 21:00 | 63
2022-05-29 22:00 | 63
2022-05-29 23:00 | 63
2022-05-30 | 62
2022-05-30 01:00 | 63
2022-05-30 02:00 | 62
2022-05-30 03:00 | 62
2022-05-30 04:00 | 61
2022-05-30 05:00 | 61
2022-05-30 06:00 | 62
2022-05-30 07:00 | 65
2022-05-30 08:00 | 67
2022-05-30 09:00 | 70
2022-05-30 10:00 | 73
2022-05-30 11:00 | 75
2022-05-30 12:00 | 77
2022-05-30 13:00 | 79
2022-05-30 14:00 | 79
2022-05-30 15:00 | 78
2022-05-30 16:00 | 78
2022-05-30 17:00 | 77
2022-05-30 18:00 | 74
2022-05-30 19:00 | 72
2022-05-30 20:00 | 71
2022-05-30 21:00 | 70
2022-05-30 22:00 | 70
2022-05-30 23:00 | 71
2022-05-31 | 70
2022-05-31 01:00 | 70
2022-05-31 02:00 | 72
2022-05-31 03:00 | 71
2022-05-31 04:00 | 73
2022-05-31 05:00 | 72
2022-05-31 06:00 | 73
2022-05-31 07:00 | 75
2022-05-31 08:00 | 80
2022-05-31 09:00 | 85
2022-05-31 10:00 | 88
2022-05-31 11:00 | 90
2022-05-31 12:00 | 91
2022-05-31 13:00 | 92
2022-05-31 14:00 | 93
2022-05-31 15:00 | 91
2022-05-31 16:00 | 87
2022-05-31 17:00 | 83
2022-05-31 18:00 | 82
2022-05-31 19:00 | 80
2022-05-31 20:00 | 75
2022-05-31 21:00 | 74
2022-05-31 22:00 | 75
2022-05-31 23:00 | 67
2022-06-01 | 65
2022-06-01 01:00 | 63
2022-06-01 02:00 | 62
2022-06-01 03:00 | 63
2022-06-01 04:00 | 62
2022-06-01 05:00 | 60
2022-06-01 06:00 | 60
2022-06-01 07:00 | 60
2022-06-01 08:00 | 61
2022-06-01 09:00 | 62
2022-06-01 10:00 | 63
2022-06-01 11:00 | 64
2022-06-01 12:00 | 67
2022-06-01 13:00 | 65
2022-06-01 14:00 | 65
2022-06-01 15:00 | 64
2022-06-01 16:00 | 63
2022-06-01 17:00 | 62
2022-06-01 18:00 | 60
2022-06-01 19:00 | 60
2022-06-01 20:00 | 60
2022-06-01 21:00 | 59
2022-06-01 22:00 | 59
2022-06-01 23:00 | 60
2022-06-02 | 60
2022-06-02 01:00 | 60
2022-06-02 02:00 | 61
2022-06-02 03:00 | 63
2022-06-02 04:00 | 63
2022-06-02 05:00 | 63
2022-06-02 06:00 | 64
2022-06-02 07:00 | 66
2022-06-02 08:00 | 67
2022-06-02 09:00 | 69
2022-06-02 10:00 | 70
2022-06-02 11:00 | 71
2022-06-02 12:00 | 73
2022-06-02 13:00 | 72
2022-06-02 14:00 | 72
2022-06-02 15:00 | 74
2022-06-02 16:00 | 75
2022-06-02 17:00 | 71
2022-06-02 18:00 | 71
2022-06-02 19:00 | 69
2022-06-02 20:00 | 68
2022-06-02 21:00 | 66
2022-06-02 22:00 | 65
2022-06-02 23:00 | 65
2022-06-03 | 66
2022-06-03 01:00 | 66
2022-06-03 02:00 | 65
2022-06-03 03:00 | 66
2022-06-03 04:00 | 66
2022-06-03 05:00 | 66
2022-06-03 06:00 | 65
2022-06-03 07:00 | 65
2022-06-03 08:00 | 64
2022-06-03 09:00 | 64
2022-06-03 10:00 | 67
2022-06-03 11:00 | 66
2022-06-03 12:00 | 66
2022-06-03 13:00 | 68
2022-06-03 14:00 | 68
2022-06-03 15:00 | 68
2022-06-03 16:00 | 68
2022-06-03 17:00 | 67
2022-06-03 18:00 | 68
2022-06-03 19:00 | 67
2022-06-03 20:00 | 65
2022-06-03 21:00 | 64
2022-06-03 22:00 | 63
2022-06-03 23:00 | 63
2022-06-04 | 63
2022-06-04 01:00 | 61
2022-06-04 02:00 | 62
2022-06-04 03:00 | 62
2022-06-04 04:00 | 59
2022-06-04 05:00 | 59
2022-06-04 06:00 | 60
2022-06-04 07:00 | 64
2022-06-04 08:00 | 69
2022-06-04 09:00 | 71
2022-06-04 10:00 | 74
2022-06-04 11:00 | 72
2022-06-04 12:00 | 71
2022-06-04 13:00 | 72
2022-06-04 14:00 | 71
2022-06-04 15:00 | 71
2022-06-04 16:00 | 72
2022-06-04 17:00 | 71
2022-06-04 18:00 | 69
2022-06-04 19:00 | 68
2022-06-04 20:00 | 66
2022-06-04 21:00 | 64
2022-06-04 22:00 | 64
2022-06-04 23:00 | 64
2022-06-05 | 63
2022-06-05 01:00 | 64
2022-06-05 02:00 | 63
2022-06-05 03:00 | 62
2022-06-05 04:00 | 58
2022-06-05 05:00 | 56
2022-06-05 06:00 | 57
2022-06-05 07:00 | 61
2022-06-05 08:00 | 64
2022-06-05 09:00 | 66
2022-06-05 10:00 | 68
2022-06-05 11:00 | 71
2022-06-05 12:00 | 72
2022-06-05 13:00 | 74
2022-06-05 14:00 | 70
2022-06-05 15:00 | 71
2022-06-05 16:00 | 71
2022-06-05 17:00 | 71
2022-06-05 18:00 | 70
2022-06-05 19:00 | 68
2022-06-05 20:00 | 66
2022-06-05 21:00 | 62
2022-06-05 22:00 | 61
2022-06-05 23:00 | 62
2022-06-06 | 62
2022-06-06 01:00 | 63
2022-06-06 02:00 | 63
2022-06-06 03:00 | 63
2022-06-06 04:00 | 62
2022-06-06 05:00 | 62
2022-06-06 06:00 | 61
2022-06-06 07:00 | 66
2022-06-06 08:00 | 69
2022-06-06 09:00 | 72
2022-06-06 10:00 | 74
2022-06-06 11:00 | 75
2022-06-06 12:00 | 77
2022-06-06 13:00 | 74
2022-06-06 14:00 | 75
2022-06-06 15:00 | 76
2022-06-06 16:00 | 75
2022-06-06 17:00 | 74
2022-06-06 18:00 | 72
2022-06-06 19:00 | 70
2022-06-06 20:00 | 68
2022-06-06 21:00 | 67
2022-06-06 22:00 | 67
2022-06-06 23:00 | 67
2022-06-07 | 65
2022-06-07 01:00 | 63
2022-06-07 02:00 | 64
2022-06-07 03:00 | 61
2022-06-07 04:00 | 60
2022-06-07 05:00 | 59
2022-06-07 06:00 | 60
2022-06-07 07:00 | 66
2022-06-07 08:00 | 68
2022-06-07 09:00 | 70
2022-06-07 10:00 | 70
2022-06-07 11:00 | 72
2022-06-07 12:00 | 72
2022-06-07 13:00 | 74
2022-06-07 14:00 | 74
2022-06-07 15:00 | 75
2022-06-07 16:00 | 71
2022-06-07 17:00 | 71
2022-06-07 18:00 | 71
2022-06-07 19:00 | 70
2022-06-07 20:00 | 69
2022-06-07 21:00 | 69
2022-06-07 22:00 | 68
2022-06-07 23:00 | 67
2022-06-08 | 67
2022-06-08 01:00 | 67
2022-06-08 02:00 | 67
2022-06-08 03:00 | 67
2022-06-08 04:00 | 67
2022-06-08 05:00 | 67
2022-06-08 06:00 | 67
2022-06-08 07:00 | 68
2022-06-08 08:00 | 71
2022-06-08 09:00 | 74
2022-06-08 10:00 | 78
2022-06-08 11:00 | 80
2022-06-08 12:00 | 82
2022-06-08 13:00 | 83
2022-06-08 14:00 | 83
2022-06-08 15:00 | 83
2022-06-08 16:00 | 83
2022-06-08 17:00 | 78
2022-06-08 18:00 | 78
2022-06-08 19:00 | 76
2022-06-08 20:00 | 73
2022-06-08 21:00 | 70
2022-06-08 22:00 | 70
2022-06-08 23:00 | 70
2022-06-09 | 69
2022-06-09 01:00 | 69
2022-06-09 02:00 | 69
2022-06-09 03:00 | 69
2022-06-09 04:00 | 69
2022-06-09 05:00 | 69
2022-06-09 06:00 | 69
2022-06-09 07:00 | 68
2022-06-09 08:00 | 69
2022-06-09 09:00 | 70
2022-06-09 10:00 | 75
2022-06-09 11:00 | 79
2022-06-09 12:00 | 81
2022-06-09 13:00 | 82
2022-06-09 14:00 | 83
2022-06-09 15:00 | 83
2022-06-09 16:00 | 82
2022-06-09 17:00 | 81
2022-06-09 18:00 | 80
2022-06-09 19:00 | 80
2022-06-09 20:00 | 76
2022-06-09 21:00 | 74
2022-06-09 22:00 | 72
2022-06-09 23:00 | 69
2022-06-10 | 69
2022-06-10 01:00 | 66
2022-06-10 02:00 | 65
2022-06-10 03:00 | 64
2022-06-10 04:00 | 65
2022-06-10 05:00 | 64
2022-06-10 06:00 | 64
2022-06-10 07:00 | 66
2022-06-10 08:00 | 68
2022-06-10 09:00 | 71
2022-06-10 10:00 | 72
2022-06-10 11:00 | 74
2022-06-10 12:00 | 75
2022-06-10 13:00 | 78
2022-06-10 14:00 | 79
2022-06-10 15:00 | 80
2022-06-10 16:00 | 79
2022-06-10 17:00 | 77
2022-06-10 18:00 | 72
2022-06-10 19:00 | 71
2022-06-10 20:00 | 70
2022-06-10 21:00 | 75
2022-06-10 22:00 | 73
2022-06-10 23:00 | 73
2022-06-11 | 72
2022-06-11 01:00 | 69
2022-06-11 02:00 | 67
2022-06-11 03:00 | 67
2022-06-11 04:00 | 68
2022-06-11 05:00 | 65
2022-06-11 06:00 | 66
2022-06-11 07:00 | 68
2022-06-11 08:00 | 69
2022-06-11 09:00 | 72
2022-06-11 10:00 | 76
2022-06-11 11:00 | 76
2022-06-11 12:00 | 79
2022-06-11 13:00 | 72
2022-06-11 14:00 | 72
2022-06-11 15:00 | 71
2022-06-11 16:00 | 71
2022-06-11 17:00 | 72
2022-06-11 18:00 | 70
2022-06-11 19:00 | 70
2022-06-11 20:00 | 70
2022-06-11 21:00 | 69
2022-06-11 22:00 | 68
2022-06-11 23:00 | 67
2022-06-12 | 66
2022-06-12 01:00 | 66
2022-06-12 02:00 | 65
2022-06-12 03:00 | 64
2022-06-12 04:00 | 64
2022-06-12 05:00 | 65
2022-06-12 06:00 | 65
2022-06-12 07:00 | 66
2022-06-12 08:00 | 66
2022-06-12 09:00 | 64
2022-06-12 10:00 | 64
2022-06-12 11:00 | 65
2022-06-12 12:00 | 65
2022-06-12 13:00 | 66
2022-06-12 14:00 | 67
2022-06-12 15:00 | 70
2022-06-12 16:00 | 69
2022-06-12 17:00 | 72
2022-06-12 18:00 | 71
2022-06-12 19:00 | 70
2022-06-12 20:00 | 69
2022-06-12 21:00 | 68
2022-06-12 22:00 | 68
2022-06-12 23:00 | 68
2022-06-13 | 68
2022-06-13 01:00 | 68
2022-06-13 02:00 | 67
2022-06-13 03:00 | 68
2022-06-13 04:00 | 67
2022-06-13 05:00 | 66
2022-06-13 06:00 | 67
2022-06-13 07:00 | 68
2022-06-13 08:00 | 69
2022-06-13 09:00 | 72
2022-06-13 10:00 | 76
2022-06-13 11:00 | 77
2022-06-13 12:00 | 77
2022-06-13 13:00 | 79
2022-06-13 14:00 | 75
2022-06-13 15:00 | 77
2022-06-13 16:00 | 79
2022-06-13 17:00 | 79
2022-06-13 18:00 | 78
2022-06-13 19:00 | 76
2022-06-13 20:00 | 76
2022-06-13 21:00 | 74
2022-06-13 22:00 | 76
2022-06-13 23:00 | 77
2022-06-14 | 75
2022-06-14 01:00 | 73
2022-06-14 02:00 | 73
2022-06-14 03:00 | 70
2022-06-14 04:00 | 69
2022-06-14 05:00 | 68
2022-06-14 06:00 | 68
2022-06-14 07:00 | 67
2022-06-14 08:00 | 68
2022-06-14 09:00 | 69
2022-06-14 10:00 | 70
2022-06-14 11:00 | 73
2022-06-14 12:00 | 77
2022-06-14 13:00 | 78
2022-06-14 14:00 | 76
2022-06-14 15:00 | 75
2022-06-14 16:00 | 76
2022-06-14 17:00 | 77
2022-06-14 18:00 | 77
2022-06-14 19:00 | 77
2022-06-14 20:00 | 79
2022-06-14 21:00 | 76
2022-06-14 22:00 | 68
2022-06-14 23:00 | 69
2022-06-15 | 67
2022-06-15 01:00 | 72
2022-06-15 02:00 | 70
2022-06-15 03:00 | 69
2022-06-15 04:00 | 68
2022-06-15 05:00 | 67
2022-06-15 06:00 | 67
2022-06-15 07:00 | 71
2022-06-15 08:00 | 75
2022-06-15 09:00 | 76
2022-06-15 10:00 | 79
2022-06-15 11:00 | 77
2022-06-15 12:00 | 76
2022-06-15 13:00 | 74
2022-06-15 14:00 | 74
2022-06-15 15:00 | 75
2022-06-15 16:00 | 73
2022-06-15 17:00 | 72
2022-06-15 18:00 | 71
2022-06-15 19:00 | 70
2022-06-15 20:00 | 68
2022-06-15 21:00 | 67
2022-06-15 22:00 | 67
2022-06-15 23:00 | 67
2022-06-16 | 67
2022-06-16 01:00 | 67
2022-06-16 02:00 | 67
2022-06-16 03:00 | 68
2022-06-16 04:00 | 67
2022-06-16 05:00 | 67
2022-06-16 06:00 | 68
2022-06-16 07:00 | 68
2022-06-16 08:00 | 66
2022-06-16 09:00 | 65
2022-06-16 10:00 | 66
2022-06-16 11:00 | 68
2022-06-16 12:00 | 69
2022-06-16 13:00 | 71
2022-06-16 14:00 | 69
2022-06-16 15:00 | 70
2022-06-16 16:00 | 70
2022-06-16 17:00 | 70
2022-06-16 18:00 | 69
2022-06-16 19:00 | 69
2022-06-16 20:00 | 69
2022-06-16 21:00 | 69
2022-06-16 22:00 | 69
2022-06-16 23:00 | 69
2022-06-17 | 69
2022-06-17 01:00 | 69
2022-06-17 02:00 | 69
2022-06-17 03:00 | 69
2022-06-17 04:00 | 68
2022-06-17 05:00 | 69
2022-06-17 06:00 | 69
2022-06-17 07:00 | 71
2022-06-17 08:00 | 71
2022-06-17 09:00 | 73
2022-06-17 10:00 | 76
2022-06-17 11:00 | 80
2022-06-17 12:00 | 80
2022-06-17 13:00 | 83
2022-06-17 14:00 | 91
2022-06-17 15:00 | 93
2022-06-17 16:00 | 92
2022-06-17 17:00 | 91
2022-06-17 18:00 | 90
2022-06-17 19:00 | 89
2022-06-17 20:00 | 86
2022-06-17 21:00 | 84
2022-06-17 22:00 | 82
2022-06-17 23:00 | 80
2022-06-18 | 80
2022-06-18 01:00 | 78
2022-06-18 02:00 | 77
2022-06-18 03:00 | 76
2022-06-18 04:00 | 74
2022-06-18 05:00 | 73
2022-06-18 06:00 | 70
2022-06-18 07:00 | 69
2022-06-18 08:00 | 70
2022-06-18 09:00 | 70
2022-06-18 10:00 | 70
2022-06-18 11:00 | 70
2022-06-18 12:00 | 69
2022-06-18 13:00 | 71
2022-06-18 14:00 | 71
2022-06-18 15:00 | 69
2022-06-18 16:00 | 70
2022-06-18 17:00 | 68
2022-06-18 18:00 | 64
2022-06-18 19:00 | 63
2022-06-18 20:00 | 63
2022-06-18 21:00 | 63
2022-06-18 22:00 | 62
2022-06-18 23:00 | 61
2022-06-19 | 60
2022-06-19 01:00 | 59
2022-06-19 02:00 | 58
2022-06-19 03:00 | 59
2022-06-19 04:00 | 58
2022-06-19 05:00 | 57
2022-06-19 06:00 | 55
2022-06-19 07:00 | 57
2022-06-19 08:00 | 59
2022-06-19 09:00 | 62
2022-06-19 10:00 | 64
2022-06-19 11:00 | 66
2022-06-19 12:00 | 68
2022-06-19 13:00 | 71
2022-06-19 14:00 | 73
2022-06-19 15:00 | 74
2022-06-19 16:00 | 75
2022-06-19 17:00 | 75
2022-06-19 18:00 | 74
2022-06-19 19:00 | 73
2022-06-19 20:00 | 71
2022-06-19 21:00 | 69
2022-06-19 22:00 | 68
2022-06-19 23:00 | 66
2022-06-20 | 64
2022-06-20 01:00 | 63
2022-06-20 02:00 | 62
2022-06-20 03:00 | 62
2022-06-20 04:00 | 61
2022-06-20 05:00 | 59
2022-06-20 06:00 | 60
2022-06-20 07:00 | 63
2022-06-20 08:00 | 66
2022-06-20 09:00 | 70
2022-06-20 10:00 | 72
2022-06-20 11:00 | 73
2022-06-20 12:00 | 75
2022-06-20 13:00 | 77
2022-06-20 14:00 | 79
2022-06-20 15:00 | 80
2022-06-20 16:00 | 81
2022-06-20 17:00 | 81
2022-06-20 18:00 | 79
2022-06-20 19:00 | 71
2022-06-20 20:00 | 69
2022-06-20 21:00 | 66
2022-06-20 22:00 | 65
2022-06-20 23:00 | 65
2022-06-21 | 64
2022-06-21 01:00 | 65
2022-06-21 02:00 | 65
2022-06-21 03:00 | 63
2022-06-21 04:00 | 63
2022-06-21 05:00 | 64
2022-06-21 06:00 | 65
2022-06-21 07:00 | 67
2022-06-21 08:00 | 70
2022-06-21 09:00 | 74
2022-06-21 10:00 | 76
2022-06-21 11:00 | 76
2022-06-21 12:00 | 74
2022-06-21 13:00 | 77
2022-06-21 14:00 | 76
2022-06-21 15:00 | 77
2022-06-21 16:00 | 75
2022-06-21 17:00 | 73
2022-06-21 18:00 | 72
2022-06-21 19:00 | 71
2022-06-21 20:00 | 69
2022-06-21 21:00 | 68
2022-06-21 22:00 | 68
2022-06-21 23:00 | 67
2022-06-22 | 67
2022-06-22 01:00 | 67
2022-06-22 02:00 | 66
2022-06-22 03:00 | 66
2022-06-22 04:00 | 67
2022-06-22 05:00 | 66
2022-06-22 06:00 | 65
2022-06-22 07:00 | 65
2022-06-22 08:00 | 63
2022-06-22 09:00 | 63
2022-06-22 10:00 | 64
2022-06-22 11:00 | 64
2022-06-22 12:00 | 64
2022-06-22 13:00 | 64
2022-06-22 14:00 | 64
2022-06-22 15:00 | 63
2022-06-22 16:00 | 64
2022-06-22 17:00 | 63
2022-06-22 18:00 | 62
2022-06-22 19:00 | 63
2022-06-22 20:00 | 63
2022-06-22 21:00 | 64
2022-06-22 22:00 | 63
2022-06-22 23:00 | 64
2022-06-23 | 63
2022-06-23 01:00 | 61
2022-06-23 02:00 | 61
2022-06-23 03:00 | 60
2022-06-23 04:00 | 62
2022-06-23 05:00 | 62
2022-06-23 06:00 | 62
2022-06-23 07:00 | 65
2022-06-23 08:00 | 67
2022-06-23 09:00 | 68
2022-06-23 10:00 | 71
2022-06-23 11:00 | 72
2022-06-23 12:00 | 73
2022-06-23 13:00 | 73
2022-06-23 14:00 | 73
2022-06-23 15:00 | 72
2022-06-23 16:00 | 73
2022-06-23 17:00 | 72
2022-06-23 18:00 | 73
2022-06-23 19:00 | 70
2022-06-23 20:00 | 68
2022-06-23 21:00 | 68
2022-06-23 22:00 | 67
2022-06-23 23:00 | 67
2022-06-24 | 65
2022-06-24 01:00 | 64
2022-06-24 02:00 | 64
2022-06-24 03:00 | 63
2022-06-24 04:00 | 62
2022-06-24 05:00 | 61
2022-06-24 06:00 | 61
2022-06-24 07:00 | 65
2022-06-24 08:00 | 66
2022-06-24 09:00 | 69
2022-06-24 10:00 | 71
2022-06-24 11:00 | 72
2022-06-24 12:00 | 72
2022-06-24 13:00 | 74
2022-06-24 14:00 | 75
2022-06-24 15:00 | 75
2022-06-24 16:00 | 74
2022-06-24 17:00 | 73
2022-06-24 18:00 | 72
2022-06-24 19:00 | 70
2022-06-24 20:00 | 69
2022-06-24 21:00 | 69
2022-06-24 22:00 | 69
2022-06-24 23:00 | 69
2022-06-25 | 68
2022-06-25 01:00 | 68
2022-06-25 02:00 | 68
2022-06-25 03:00 | 67
2022-06-25 04:00 | 67
2022-06-25 05:00 | 67
2022-06-25 06:00 | 68
2022-06-25 07:00 | 74
2022-06-25 08:00 | 77
2022-06-25 09:00 | 81
2022-06-25 10:00 | 84
2022-06-25 11:00 | 86
2022-06-25 12:00 | 86
2022-06-25 13:00 | 86
2022-06-25 14:00 | 86
2022-06-25 15:00 | 87
2022-06-25 16:00 | 84
2022-06-25 17:00 | 82
2022-06-25 18:00 | 80
2022-06-25 19:00 | 79
2022-06-25 20:00 | 77
2022-06-25 21:00 | 75
2022-06-25 22:00 | 74
2022-06-25 23:00 | 72
2022-06-26 | 70
2022-06-26 01:00 | 70
2022-06-26 02:00 | 69
2022-06-26 03:00 | 69
2022-06-26 04:00 | 68
2022-06-26 05:00 | 68
2022-06-26 06:00 | 69
2022-06-26 07:00 | 71
2022-06-26 08:00 | 74
2022-06-26 09:00 | 77
2022-06-26 10:00 | 79
2022-06-26 11:00 | 82
2022-06-26 12:00 | 82
2022-06-26 13:00 | 82
2022-06-26 14:00 | 83
2022-06-26 15:00 | 82
2022-06-26 16:00 | 80
2022-06-26 17:00 | 80
2022-06-26 18:00 | 78
2022-06-26 19:00 | 75
2022-06-26 20:00 | 74
2022-06-26 21:00 | 73
2022-06-26 22:00 | 72
2022-06-26 23:00 | 72
2022-06-27 | 71
2022-06-27 01:00 | 71
2022-06-27 02:00 | 70
2022-06-27 03:00 | 71
2022-06-27 04:00 | 70
2022-06-27 05:00 | 70
2022-06-27 06:00 | 70
2022-06-27 07:00 | 71
2022-06-27 08:00 | 72
2022-06-27 09:00 | 73
2022-06-27 10:00 | 75
2022-06-27 11:00 | 73
2022-06-27 12:00 | 71
2022-06-27 13:00 | 76
2022-06-27 14:00 | 75
2022-06-27 15:00 | 75
2022-06-27 16:00 | 73
2022-06-27 17:00 | 73
2022-06-27 18:00 | 72
2022-06-27 19:00 | 72
2022-06-27 20:00 | 72
2022-06-27 21:00 | 73
2022-06-27 22:00 | 72
2022-06-27 23:00 | 74
2022-06-28 | 71
2022-06-28 01:00 | 69
2022-06-28 02:00 | 67
2022-06-28 03:00 | 66
2022-06-28 04:00 | 66
2022-06-28 05:00 | 65
2022-06-28 06:00 | 65
2022-06-28 07:00 | 66
2022-06-28 08:00 | 70
2022-06-28 09:00 | 70
2022-06-28 10:00 | 73
2022-06-28 11:00 | 75
2022-06-28 12:00 | 77
2022-06-28 13:00 | 76
2022-06-28 14:00 | 76
2022-06-28 15:00 | 76
2022-06-28 16:00 | 77
2022-06-28 17:00 | 79
2022-06-28 18:00 | 74
2022-06-28 19:00 | 73
2022-06-28 20:00 | 70
2022-06-28 21:00 | 69
2022-06-28 22:00 | 69
2022-06-28 23:00 | 68
2022-06-29 | 67
2022-06-29 01:00 | 66
2022-06-29 02:00 | 65
2022-06-29 03:00 | 65
2022-06-29 04:00 | 65
2022-06-29 05:00 | 65
2022-06-29 06:00 | 64
2022-06-29 07:00 | 67
2022-06-29 08:00 | 70
2022-06-29 09:00 | 72
2022-06-29 10:00 | 75
2022-06-29 11:00 | 79
2022-06-29 12:00 | 80
2022-06-29 13:00 | 81
2022-06-29 14:00 | 81
2022-06-29 15:00 | 81
2022-06-29 16:00 | 80
2022-06-29 17:00 | 79
2022-06-29 18:00 | 75
2022-06-29 19:00 | 75
2022-06-29 20:00 | 73
2022-06-29 21:00 | 71
2022-06-29 22:00 | 71
2022-06-29 23:00 | 70
2022-06-30 | 68
2022-06-30 01:00 | 70
2022-06-30 02:00 | 70
2022-06-30 03:00 | 68
2022-06-30 04:00 | 70
2022-06-30 05:00 | 69
2022-06-30 06:00 | 70
2022-06-30 07:00 | 72
2022-06-30 08:00 | 75
2022-06-30 09:00 | 77
2022-06-30 10:00 | 80
2022-06-30 11:00 | 82
2022-06-30 12:00 | 79
2022-06-30 13:00 | 81
2022-06-30 14:00 | 82
2022-06-30 15:00 | 81
2022-06-30 16:00 | 82
2022-06-30 17:00 | 80
2022-06-30 18:00 | 79
2022-06-30 19:00 | 77
2022-06-30 20:00 | 74
2022-06-30 21:00 | 73
2022-06-30 22:00 | 73
2022-06-30 23:00 | 72
2022-07-01 | 70
2022-07-01 01:00 | 73
2022-07-01 02:00 | 73
2022-07-01 03:00 | 73
2022-07-01 04:00 | 73
2022-07-01 05:00 | 71
2022-07-01 06:00 | 71
2022-07-01 07:00 | 73
2022-07-01 08:00 | 74
2022-07-01 09:00 | 77
2022-07-01 10:00 | 78
2022-07-01 11:00 | 80
2022-07-01 12:00 | 81
2022-07-01 13:00 | 83
2022-07-01 14:00 | 84
2022-07-01 15:00 | 84
2022-07-01 16:00 | 83
2022-07-01 17:00 | 81
2022-07-01 18:00 | 79
2022-07-01 19:00 | 79
2022-07-01 20:00 | 77
2022-07-01 21:00 | 76
2022-07-01 22:00 | 75
2022-07-01 23:00 | 75
2022-07-02 | 77
2022-07-02 01:00 | 74
2022-07-02 02:00 | 73
2022-07-02 03:00 | 73
2022-07-02 04:00 | 74
2022-07-02 05:00 | 73
2022-07-02 06:00 | 74
2022-07-02 07:00 | 76
2022-07-02 08:00 | 76
2022-07-02 09:00 | 79
2022-07-02 10:00 | 79
2022-07-02 11:00 | 83
2022-07-02 12:00 | 84
2022-07-02 13:00 | 82
2022-07-02 14:00 | 85
2022-07-02 15:00 | 84
2022-07-02 16:00 | 83
2022-07-02 17:00 | 83
2022-07-02 18:00 | 81
2022-07-02 19:00 | 79
2022-07-02 20:00 | 79
2022-07-02 21:00 | 78
2022-07-02 22:00 | 73
2022-07-02 23:00 | 75
2022-07-03 | 77
2022-07-03 01:00 | 79
2022-07-03 02:00 | 79
2022-07-03 03:00 | 79
2022-07-03 04:00 | 78
2022-07-03 05:00 | 77
2022-07-03 06:00 | 76
2022-07-03 07:00 | 76
2022-07-03 08:00 | 77
2022-07-03 09:00 | 77
2022-07-03 10:00 | 78
2022-07-03 11:00 | 79
2022-07-03 12:00 | 83
2022-07-03 13:00 | 86
2022-07-03 14:00 | 86
2022-07-03 15:00 | 84
2022-07-03 16:00 | 82
2022-07-03 17:00 | 82
2022-07-03 18:00 | 80
2022-07-03 19:00 | 79
2022-07-03 20:00 | 75
2022-07-03 21:00 | 72
2022-07-03 22:00 | 71
2022-07-03 23:00 | 77
2022-07-04 | 76
2022-07-04 01:00 | 74
2022-07-04 02:00 | 71
2022-07-04 03:00 | 70
2022-07-04 04:00 | 68
2022-07-04 05:00 | 66
2022-07-04 06:00 | 66
2022-07-04 07:00 | 70
2022-07-04 08:00 | 73
2022-07-04 09:00 | 77
2022-07-04 10:00 | 79
2022-07-04 11:00 | 82
2022-07-04 12:00 | 84
2022-07-04 13:00 | 82
2022-07-04 14:00 | 83
2022-07-04 15:00 | 81
2022-07-04 16:00 | 81
2022-07-04 17:00 | 79
2022-07-04 18:00 | 78
2022-07-04 19:00 | 76
2022-07-04 20:00 | 75
2022-07-04 21:00 | 73
2022-07-04 22:00 | 74
2022-07-04 23:00 | 72
2022-07-05 | 72
2022-07-05 01:00 | 71
2022-07-05 02:00 | 71
2022-07-05 03:00 | 69
2022-07-05 04:00 | 69
2022-07-05 05:00 | 69
2022-07-05 06:00 | 70
2022-07-05 07:00 | 72
2022-07-05 08:00 | 73
2022-07-05 09:00 | 76
2022-07-05 10:00 | 77
2022-07-05 11:00 | 81
2022-07-05 12:00 | 82
2022-07-05 13:00 | 81
2022-07-05 14:00 | 81
2022-07-05 15:00 | 77
2022-07-05 16:00 | 76
2022-07-05 17:00 | 75
2022-07-05 18:00 | 75
2022-07-05 19:00 | 74
2022-07-05 20:00 | 73
2022-07-05 21:00 | 71
2022-07-05 22:00 | 72
2022-07-05 23:00 | 71
2022-07-06 | 72
2022-07-06 01:00 | 72
2022-07-06 02:00 | 72
2022-07-06 03:00 | 72
2022-07-06 04:00 | 71
2022-07-06 05:00 | 72
2022-07-06 06:00 | 73
2022-07-06 07:00 | 76
2022-07-06 08:00 | 79
2022-07-06 09:00 | 83
2022-07-06 10:00 | 87
2022-07-06 11:00 | 86
2022-07-06 12:00 | 86
2022-07-06 13:00 | 86
2022-07-06 14:00 | 86
2022-07-06 15:00 | 86
2022-07-06 16:00 | 87
2022-07-06 17:00 | 87
2022-07-06 18:00 | 87
2022-07-06 19:00 | 84
2022-07-06 20:00 | 83
2022-07-06 21:00 | 81
2022-07-06 22:00 | 79
2022-07-06 23:00 | 79
2022-07-07 | 78
2022-07-07 01:00 | 77
2022-07-07 02:00 | 76
2022-07-07 03:00 | 75
2022-07-07 04:00 | 73
2022-07-07 05:00 | 73
2022-07-07 06:00 | 73
2022-07-07 07:00 | 74
2022-07-07 08:00 | 74
2022-07-07 09:00 | 76
2022-07-07 10:00 | 77
2022-07-07 11:00 | 78
2022-07-07 12:00 | 79
2022-07-07 13:00 | 81
2022-07-07 14:00 | 81
2022-07-07 15:00 | 79
2022-07-07 16:00 | 80
2022-07-07 17:00 | 78
2022-07-07 18:00 | 78
2022-07-07 19:00 | 74
2022-07-07 20:00 | 73
2022-07-07 21:00 | 71
2022-07-07 22:00 | 70
2022-07-07 23:00 | 70
2022-07-08 | 69
2022-07-08 01:00 | 69
2022-07-08 02:00 | 68
2022-07-08 03:00 | 67
2022-07-08 04:00 | 67
2022-07-08 05:00 | 66
2022-07-08 06:00 | 67
2022-07-08 07:00 | 70
2022-07-08 08:00 | 71
2022-07-08 09:00 | 74
2022-07-08 10:00 | 74
2022-07-08 11:00 | 77
2022-07-08 12:00 | 77
2022-07-08 13:00 | 78
2022-07-08 14:00 | 80
2022-07-08 15:00 | 79
2022-07-08 16:00 | 77
2022-07-08 17:00 | 75
2022-07-08 18:00 | 73
2022-07-08 19:00 | 72
2022-07-08 20:00 | 70
2022-07-08 21:00 | 71
2022-07-08 22:00 | 72
2022-07-08 23:00 | 73
2022-07-09 | 72
2022-07-09 01:00 | 72
2022-07-09 02:00 | 73
2022-07-09 03:00 | 73
2022-07-09 04:00 | 73
2022-07-09 05:00 | 72
2022-07-09 06:00 | 72
2022-07-09 07:00 | 72
2022-07-09 08:00 | 74
2022-07-09 09:00 | 78
2022-07-09 10:00 | 80
2022-07-09 11:00 | 82
2022-07-09 12:00 | 84
2022-07-09 13:00 | 84
2022-07-09 14:00 | 85
2022-07-09 15:00 | 82
2022-07-09 16:00 | 81
2022-07-09 17:00 | 80
2022-07-09 18:00 | 79
2022-07-09 19:00 | 77
2022-07-09 20:00 | 74
2022-07-09 21:00 | 72
2022-07-09 22:00 | 71
2022-07-09 23:00 | 71
2022-07-10 | 70
2022-07-10 01:00 | 70
2022-07-10 02:00 | 68
2022-07-10 03:00 | 66
2022-07-10 04:00 | 66
2022-07-10 05:00 | 66
2022-07-10 06:00 | 67
2022-07-10 07:00 | 68
2022-07-10 08:00 | 70
2022-07-10 09:00 | 73
2022-07-10 10:00 | 76
2022-07-10 11:00 | 78
2022-07-10 12:00 | 81
2022-07-10 13:00 | 79
2022-07-10 14:00 | 79
2022-07-10 15:00 | 79
2022-07-10 16:00 | 79
2022-07-10 17:00 | 78
2022-07-10 18:00 | 77
2022-07-10 19:00 | 75
2022-07-10 20:00 | 73
2022-07-10 21:00 | 71
2022-07-10 22:00 | 70
2022-07-10 23:00 | 69
2022-07-11 | 68
2022-07-11 01:00 | 68
2022-07-11 02:00 | 67
2022-07-11 03:00 | 67
2022-07-11 04:00 | 66
2022-07-11 05:00 | 66
2022-07-11 06:00 | 65
2022-07-11 07:00 | 69
2022-07-11 08:00 | 72
2022-07-11 09:00 | 75
2022-07-11 10:00 | 77
2022-07-11 11:00 | 79
2022-07-11 12:00 | 79
2022-07-11 13:00 | 80
2022-07-11 14:00 | 80
2022-07-11 15:00 | 81
2022-07-11 16:00 | 80
2022-07-11 17:00 | 78
2022-07-11 18:00 | 76
2022-07-11 19:00 | 75
2022-07-11 20:00 | 73
2022-07-11 21:00 | 72
2022-07-11 22:00 | 72
2022-07-11 23:00 | 72
2022-07-12 | 71
2022-07-12 01:00 | 70
2022-07-12 02:00 | 69
2022-07-12 03:00 | 69
2022-07-12 04:00 | 69
2022-07-12 05:00 | 69
2022-07-12 06:00 | 70
2022-07-12 07:00 | 71
2022-07-12 08:00 | 73
2022-07-12 09:00 | 75
2022-07-12 10:00 | 77
2022-07-12 11:00 | 80
2022-07-12 12:00 | 82
2022-07-12 13:00 | 82
2022-07-12 14:00 | 83
2022-07-12 15:00 | 82
2022-07-12 16:00 | 82
2022-07-12 17:00 | 81
2022-07-12 18:00 | 79
2022-07-12 19:00 | 77
2022-07-12 20:00 | 77
2022-07-12 21:00 | 79
2022-07-12 22:00 | 78
2022-07-12 23:00 | 81
2022-07-13 | 79
2022-07-13 01:00 | 78
2022-07-13 02:00 | 76
2022-07-13 03:00 | 76
2022-07-13 04:00 | 78
2022-07-13 05:00 | 76
2022-07-13 06:00 | 75
2022-07-13 07:00 | 78
2022-07-13 08:00 | 80
2022-07-13 09:00 | 82
2022-07-13 10:00 | 86
2022-07-13 11:00 | 85
2022-07-13 12:00 | 88
2022-07-13 13:00 | 88
2022-07-13 14:00 | 89
2022-07-13 15:00 | 91
2022-07-13 16:00 | 88
2022-07-13 17:00 | 84
2022-07-13 18:00 | 84
2022-07-13 19:00 | 80
2022-07-13 20:00 | 77
2022-07-13 21:00 | 76
2022-07-13 22:00 | 75
2022-07-13 23:00 | 75
2022-07-14 | 73
2022-07-14 01:00 | 73
2022-07-14 02:00 | 72
2022-07-14 03:00 | 72
2022-07-14 04:00 | 74
2022-07-14 05:00 | 73
2022-07-14 06:00 | 72
2022-07-14 07:00 | 73
2022-07-14 08:00 | 74
2022-07-14 09:00 | 79
2022-07-14 10:00 | 82
2022-07-14 11:00 | 85
2022-07-14 12:00 | 86
2022-07-14 13:00 | 85
2022-07-14 14:00 | 87
2022-07-14 15:00 | 91
2022-07-14 16:00 | 87
2022-07-14 17:00 | 88
2022-07-14 18:00 | 81
2022-07-14 19:00 | 80
2022-07-14 20:00 | 80
2022-07-14 21:00 | 80
2022-07-14 22:00 | 79
2022-07-14 23:00 | 80
2022-07-15 | 79
2022-07-15 01:00 | 78
2022-07-15 02:00 | 76
2022-07-15 03:00 | 76
2022-07-15 04:00 | 75
2022-07-15 05:00 | 74
2022-07-15 06:00 | 73
2022-07-15 07:00 | 73
2022-07-15 08:00 | 75
2022-07-15 09:00 | 78
2022-07-15 10:00 | 79
2022-07-15 11:00 | 82
2022-07-15 12:00 | 82
2022-07-15 13:00 | 82
2022-07-15 14:00 | 82
2022-07-15 15:00 | 83
2022-07-15 16:00 | 82
2022-07-15 17:00 | 79
2022-07-15 18:00 | 79
2022-07-15 19:00 | 78
2022-07-15 20:00 | 75
2022-07-15 21:00 | 73
2022-07-15 22:00 | 73
2022-07-15 23:00 | 73
2022-07-16 | 73
2022-07-16 01:00 | 73
2022-07-16 02:00 | 73
2022-07-16 03:00 | 72
2022-07-16 04:00 | 72
2022-07-16 05:00 | 72
2022-07-16 06:00 | 73
2022-07-16 07:00 | 73
2022-07-16 08:00 | 75
2022-07-16 09:00 | 76
2022-07-16 10:00 | 79
2022-07-16 11:00 | 80
2022-07-16 12:00 | 80
2022-07-16 13:00 | 84
2022-07-16 14:00 | 82
2022-07-16 15:00 | 84
2022-07-16 16:00 | 76
2022-07-16 17:00 | 80
2022-07-16 18:00 | 79
2022-07-16 19:00 | 78
2022-07-16 20:00 | 77
2022-07-16 21:00 | 76
2022-07-16 22:00 | 75
2022-07-16 23:00 | 76
2022-07-17 | 75
2022-07-17 01:00 | 75
2022-07-17 02:00 | 76
2022-07-17 03:00 | 75
2022-07-17 04:00 | 76
2022-07-17 05:00 | 74
2022-07-17 06:00 | 72
2022-07-17 07:00 | 73
2022-07-17 08:00 | 75
2022-07-17 09:00 | 79
2022-07-17 10:00 | 80
2022-07-17 11:00 | 81
2022-07-17 12:00 | 81
2022-07-17 13:00 | 82
2022-07-17 14:00 | 83
2022-07-17 15:00 | 82
2022-07-17 16:00 | 82
2022-07-17 17:00 | 81
2022-07-17 18:00 | 80
2022-07-17 19:00 | 80
2022-07-17 20:00 | 78
2022-07-17 21:00 | 77
2022-07-17 22:00 | 76
2022-07-17 23:00 | 77
2022-07-18 | 77
2022-07-18 01:00 | 77
2022-07-18 02:00 | 76
2022-07-18 03:00 | 75
2022-07-18 04:00 | 75
2022-07-18 05:00 | 75
2022-07-18 06:00 | 75
2022-07-18 07:00 | 76
2022-07-18 08:00 | 77
2022-07-18 09:00 | 77
2022-07-18 10:00 | 80
2022-07-18 11:00 | 80
2022-07-18 12:00 | 83
2022-07-18 13:00 | 80
2022-07-18 14:00 | 79
2022-07-18 15:00 | 79
2022-07-18 16:00 | 79
2022-07-18 17:00 | 80
2022-07-18 18:00 | 78
2022-07-18 19:00 | 77
2022-07-18 20:00 | 76
2022-07-18 21:00 | 76
2022-07-18 22:00 | 76
2022-07-18 23:00 | 77
2022-07-19 | 79
2022-07-19 01:00 | 78
2022-07-19 02:00 | 77
2022-07-19 03:00 | 76
2022-07-19 04:00 | 76
2022-07-19 05:00 | 76
2022-07-19 06:00 | 75
2022-07-19 07:00 | 75
2022-07-19 08:00 | 78
2022-07-19 09:00 | 79
2022-07-19 10:00 | 83
2022-07-19 11:00 | 85
2022-07-19 12:00 | 88
2022-07-19 13:00 | 90
2022-07-19 14:00 | 91
2022-07-19 15:00 | 91
2022-07-19 16:00 | 93
2022-07-19 17:00 | 93
2022-07-19 18:00 | 93
2022-07-19 19:00 | 92
2022-07-19 20:00 | 90
2022-07-19 21:00 | 88
2022-07-19 22:00 | 85
2022-07-19 23:00 | 84
2022-07-20 | 83
2022-07-20 01:00 | 81
2022-07-20 02:00 | 80
2022-07-20 03:00 | 78
2022-07-20 04:00 | 78
2022-07-20 05:00 | 77
2022-07-20 06:00 | 79
2022-07-20 07:00 | 79
2022-07-20 08:00 | 83
2022-07-20 09:00 | 87
2022-07-20 10:00 | 90
2022-07-20 11:00 | 91
2022-07-20 12:00 | 93
2022-07-20 13:00 | 93
2022-07-20 14:00 | 92
2022-07-20 15:00 | 92
2022-07-20 16:00 | 90
2022-07-20 17:00 | 88
2022-07-20 18:00 | 87
2022-07-20 19:00 | 84
2022-07-20 20:00 | 81
2022-07-20 21:00 | 80
2022-07-20 22:00 | 82
2022-07-20 23:00 | 81
2022-07-21 | 80
2022-07-21 01:00 | 79
2022-07-21 02:00 | 77
2022-07-21 03:00 | 76
2022-07-21 04:00 | 78
2022-07-21 05:00 | 77
2022-07-21 06:00 | 79
2022-07-21 07:00 | 79
2022-07-21 08:00 | 83
2022-07-21 09:00 | 87
2022-07-21 10:00 | 90
2022-07-21 11:00 | 91
2022-07-21 12:00 | 93
2022-07-21 13:00 | 93
2022-07-21 14:00 | 92
2022-07-21 15:00 | 92
2022-07-21 16:00 | 89.9
2022-07-21 17:00 | 86.1
2022-07-21 18:00 | 84
2022-07-21 19:00 | 88
2022-07-21 20:00 | 89
2022-07-21 21:00 | 87
2022-07-21 22:00 | 91
2022-07-21 23:00 | 86
2022-07-22 | 85
2022-07-22 01:00 | 82
2022-07-22 02:00 | 81
2022-07-22 03:00 | 79
2022-07-22 04:00 | 81
2022-07-22 05:00 | 80
2022-07-22 06:00 | 80
2022-07-22 07:00 | 83
2022-07-22 08:00 | 86
2022-07-22 09:00 | 88
2022-07-22 10:00 | 91
2022-07-22 11:00 | 92
2022-07-22 12:00 | 92
2022-07-22 13:00 | 93
2022-07-22 14:00 | 95
2022-07-22 15:00 | 93
2022-07-22 16:00 | 92
2022-07-22 17:00 | 90
2022-07-22 18:00 | 85
2022-07-22 19:00 | 83
2022-07-22 20:00 | 85
2022-07-22 21:00 | 83
2022-07-22 22:00 | 83
2022-07-22 23:00 | 80
2022-07-23 | 79
2022-07-23 01:00 | 79
2022-07-23 02:00 | 79
2022-07-23 03:00 | 79
2022-07-23 04:00 | 79
2022-07-23 05:00 | 80
2022-07-23 06:00 | 81
2022-07-23 07:00 | 83
2022-07-23 08:00 | 85
2022-07-23 09:00 | 88
2022-07-23 10:00 | 91
2022-07-23 11:00 | 92
2022-07-23 12:00 | 93
2022-07-23 13:00 | 94
2022-07-23 14:00 | 95
2022-07-23 15:00 | 95
2022-07-23 16:00 | 92
2022-07-23 17:00 | 92
2022-07-23 18:00 | 88
2022-07-23 19:00 | 84
2022-07-23 20:00 | 82
2022-07-23 21:00 | 80
2022-07-23 22:00 | 79
2022-07-23 23:00 | 78
2022-07-24 | 78
2022-07-24 01:00 | 79
2022-07-24 02:00 | 78
2022-07-24 03:00 | 77
2022-07-24 04:00 | 76
2022-07-24 05:00 | 77
2022-07-24 06:00 | 78
2022-07-24 07:00 | 78
2022-07-24 08:00 | 82
2022-07-24 09:00 | 85
2022-07-24 10:00 | 89
2022-07-24 11:00 | 90
2022-07-24 12:00 | 93
2022-07-24 13:00 | 95
2022-07-24 14:00 | 92
2022-07-24 15:00 | 91
2022-07-24 16:00 | 90
2022-07-24 17:00 | 88
2022-07-24 18:00 | 85
2022-07-24 19:00 | 84
2022-07-24 20:00 | 83
2022-07-24 21:00 | 82
2022-07-24 22:00 | 81
2022-07-24 23:00 | 79
2022-07-25 | 80
2022-07-25 01:00 | 80
2022-07-25 02:00 | 79
2022-07-25 03:00 | 78
2022-07-25 04:00 | 78
2022-07-25 05:00 | 77
2022-07-25 06:00 | 78
2022-07-25 07:00 | 78
2022-07-25 08:00 | 80
2022-07-25 09:00 | 81
2022-07-25 10:00 | 82
2022-07-25 11:00 | 83
2022-07-25 12:00 | 83
2022-07-25 13:00 | 82
2022-07-25 14:00 | 80
2022-07-25 15:00 | 83
2022-07-25 16:00 | 75
2022-07-25 17:00 | 80
2022-07-25 18:00 | 83
2022-07-25 19:00 | 83
2022-07-25 20:00 | 82
2022-07-25 21:00 | 80
2022-07-25 22:00 | 78
2022-07-25 23:00 | 78
2022-07-26 | 76
2022-07-26 01:00 | 75
2022-07-26 02:00 | 74
2022-07-26 03:00 | 73
2022-07-26 04:00 | 73
2022-07-26 05:00 | 73
2022-07-26 06:00 | 72
2022-07-26 07:00 | 72
2022-07-26 08:00 | 74
2022-07-26 09:00 | 76
2022-07-26 10:00 | 78
2022-07-26 11:00 | 79
2022-07-26 12:00 | 79
2022-07-26 13:00 | 77
2022-07-26 14:00 | 78
2022-07-26 15:00 | 78
2022-07-26 16:00 | 78
2022-07-26 17:00 | 79
2022-07-26 18:00 | 79
2022-07-26 19:00 | 78
2022-07-26 20:00 | 77
2022-07-26 21:00 | 77
2022-07-26 22:00 | 75
2022-07-26 23:00 | 77
2022-07-27 | 76
2022-07-27 01:00 | 73
2022-07-27 02:00 | 74
2022-07-27 03:00 | 68
2022-07-27 04:00 | 70
2022-07-27 05:00 | 69
2022-07-27 06:00 | 69
2022-07-27 07:00 | 72
2022-07-27 08:00 | 75
2022-07-27 09:00 | 79
2022-07-27 10:00 | 81
2022-07-27 11:00 | 81
2022-07-27 12:00 | 82
2022-07-27 13:00 | 82
2022-07-27 14:00 | 83
2022-07-27 15:00 | 84
2022-07-27 16:00 | 83
2022-07-27 17:00 | 80
2022-07-27 18:00 | 79
2022-07-27 19:00 | 77
2022-07-27 20:00 | 76
2022-07-27 21:00 | 75
2022-07-27 22:00 | 75
2022-07-27 23:00 | 75
2022-07-28 | 74
2022-07-28 01:00 | 75
2022-07-28 02:00 | 75
2022-07-28 03:00 | 74
2022-07-28 04:00 | 75
2022-07-28 05:00 | 74
2022-07-28 06:00 | 74
2022-07-28 07:00 | 74
2022-07-28 08:00 | 74
2022-07-28 09:00 | 77
2022-07-28 10:00 | 79
2022-07-28 11:00 | 80
2022-07-28 12:00 | 81
2022-07-28 13:00 | 83
2022-07-28 14:00 | 84
2022-07-28 15:00 | 83
2022-07-28 16:00 | 82
2022-07-28 17:00 | 82
2022-07-28 18:00 | 80
2022-07-28 19:00 | 78
2022-07-28 20:00 | 77
2022-07-28 21:00 | 81
2022-07-28 22:00 | 81
2022-07-28 23:00 | 82
2022-07-29 | 82
2022-07-29 01:00 | 81
2022-07-29 02:00 | 79
2022-07-29 03:00 | 78
2022-07-29 04:00 | 77
2022-07-29 05:00 | 76
2022-07-29 06:00 | 76
2022-07-29 07:00 | 79
2022-07-29 08:00 | 80
2022-07-29 09:00 | 79
2022-07-29 10:00 | 82
2022-07-29 11:00 | 83
2022-07-29 12:00 | 81
2022-07-29 13:00 | 81
2022-07-29 14:00 | 83
2022-07-29 15:00 | 83
2022-07-29 16:00 | 82
2022-07-29 17:00 | 82
2022-07-29 18:00 | 81
2022-07-29 19:00 | 79
2022-07-29 20:00 | 81
2022-07-29 21:00 | 79
2022-07-29 22:00 | 82
2022-07-29 23:00 | 81
2022-07-30 | 80
2022-07-30 01:00 | 79
2022-07-30 02:00 | 76
2022-07-30 03:00 | 76
2022-07-30 04:00 | 78
2022-07-30 05:00 | 77
2022-07-30 06:00 | 76
2022-07-30 07:00 | 76
2022-07-30 08:00 | 79
2022-07-30 09:00 | 81
2022-07-30 10:00 | 83
2022-07-30 11:00 | 86
2022-07-30 12:00 | 87
2022-07-30 13:00 | 88
2022-07-30 14:00 | 89
2022-07-30 15:00 | 90
2022-07-30 16:00 | 89
2022-07-30 17:00 | 87
2022-07-30 18:00 | 88
2022-07-30 19:00 | 86
2022-07-30 20:00 | 78
2022-07-30 21:00 | 77
2022-07-30 22:00 | 76
2022-07-30 23:00 | 75
2022-07-31 | 78
2022-07-31 01:00 | 75
2022-07-31 02:00 | 75
2022-07-31 03:00 | 72
2022-07-31 04:00 | 71
2022-07-31 05:00 | 71
2022-07-31 06:00 | 70
2022-07-31 07:00 | 73
2022-07-31 08:00 | 77
2022-07-31 09:00 | 80
2022-07-31 10:00 | 81
2022-07-31 11:00 | 83
2022-07-31 12:00 | 81
2022-07-31 13:00 | 84
2022-07-31 14:00 | 84
2022-07-31 15:00 | 83
2022-07-31 16:00 | 83
2022-07-31 17:00 | 81
2022-07-31 18:00 | 80
2022-07-31 19:00 | 78
2022-07-31 20:00 | 77
2022-07-31 21:00 | 77
2022-07-31 22:00 | 76
2022-07-31 23:00 | 77
2022-08-01 | 75
2022-08-01 01:00 | 75
2022-08-01 02:00 | 75
2022-08-01 03:00 | 72
2022-08-01 04:00 | 71
2022-08-01 05:00 | 70
2022-08-01 06:00 | 70
2022-08-01 07:00 | 69
2022-08-01 08:00 | 69
2022-08-01 09:00 | 69
2022-08-01 10:00 | 69
2022-08-01 11:00 | 70
2022-08-01 12:00 | 71
2022-08-01 13:00 | 72
2022-08-01 14:00 | 73
2022-08-01 15:00 | 73
2022-08-01 16:00 | 73
2022-08-01 17:00 | 73
2022-08-01 18:00 | 74
2022-08-01 19:00 | 73
2022-08-01 20:00 | 72
2022-08-01 21:00 | 71
2022-08-01 22:00 | 71
2022-08-01 23:00 | 71
2022-08-02 | 71
2022-08-02 01:00 | 71
2022-08-02 02:00 | 71
2022-08-02 03:00 | 70
2022-08-02 04:00 | 70
2022-08-02 05:00 | 71
2022-08-02 06:00 | 71
2022-08-02 07:00 | 72
2022-08-02 08:00 | 75
2022-08-02 09:00 | 76
2022-08-02 10:00 | 78
2022-08-02 11:00 | 82
2022-08-02 12:00 | 84
2022-08-02 13:00 | 87
2022-08-02 14:00 | 86
2022-08-02 15:00 | 88
2022-08-02 16:00 | 86
2022-08-02 17:00 | 85
2022-08-02 18:00 | 84
2022-08-02 19:00 | 83
2022-08-02 20:00 | 89
2022-08-02 21:00 | 89
2022-08-02 22:00 | 88
2022-08-02 23:00 | 84
2022-08-03 | 83
2022-08-03 01:00 | 80
2022-08-03 02:00 | 78
2022-08-03 03:00 | 77
2022-08-03 04:00 | 76
2022-08-03 05:00 | 75
2022-08-03 06:00 | 74
2022-08-03 07:00 | 75
2022-08-03 08:00 | 77
2022-08-03 09:00 | 80
2022-08-03 10:00 | 83
2022-08-03 11:00 | 84
2022-08-03 12:00 | 84
2022-08-03 13:00 | 84
2022-08-03 14:00 | 87
2022-08-03 15:00 | 88
2022-08-03 16:00 | 88
2022-08-03 17:00 | 85
2022-08-03 18:00 | 84
2022-08-03 19:00 | 81
2022-08-03 20:00 | 79
2022-08-03 21:00 | 78
2022-08-03 22:00 | 78
2022-08-03 23:00 | 77
2022-08-04 | 76
2022-08-04 01:00 | 74
2022-08-04 02:00 | 74
2022-08-04 03:00 | 74
2022-08-04 04:00 | 74
2022-08-04 05:00 | 73
2022-08-04 06:00 | 75
2022-08-04 07:00 | 75
2022-08-04 08:00 | 80
2022-08-04 09:00 | 82
2022-08-04 10:00 | 84
2022-08-04 11:00 | 85
2022-08-04 12:00 | 87
2022-08-04 13:00 | 88
2022-08-04 14:00 | 90
2022-08-04 15:00 | 89
2022-08-04 16:00 | 89
2022-08-04 17:00 | 86
2022-08-04 18:00 | 85
2022-08-04 19:00 | 83
2022-08-04 20:00 | 81
2022-08-04 21:00 | 80
2022-08-04 22:00 | 82
2022-08-04 23:00 | 81
2022-08-05 | 79
2022-08-05 01:00 | 79
2022-08-05 02:00 | 79
2022-08-05 03:00 | 81
2022-08-05 04:00 | 81
2022-08-05 05:00 | 78
2022-08-05 06:00 | 78
2022-08-05 07:00 | 79
2022-08-05 08:00 | 78
2022-08-05 09:00 | 79
2022-08-05 10:00 | 81
2022-08-05 11:00 | 80
2022-08-05 12:00 | 83
2022-08-05 13:00 | 84
2022-08-05 14:00 | 85
2022-08-05 15:00 | 88
2022-08-05 16:00 | 87
2022-08-05 17:00 | 85
2022-08-05 18:00 | 82
2022-08-05 19:00 | 82
2022-08-05 20:00 | 80
2022-08-05 21:00 | 81
2022-08-05 22:00 | 80
2022-08-05 23:00 | 79
2022-08-06 | 77
2022-08-06 01:00 | 76
2022-08-06 02:00 | 77
2022-08-06 03:00 | 76
2022-08-06 04:00 | 75
2022-08-06 05:00 | 74
2022-08-06 06:00 | 75
2022-08-06 07:00 | 76
2022-08-06 08:00 | 79
2022-08-06 09:00 | 81
2022-08-06 10:00 | 83
2022-08-06 11:00 | 82
2022-08-06 12:00 | 83
2022-08-06 13:00 | 86
2022-08-06 14:00 | 87
2022-08-06 15:00 | 87
2022-08-06 16:00 | 88
2022-08-06 17:00 | 86
2022-08-06 18:00 | 84
2022-08-06 19:00 | 81
2022-08-06 20:00 | 80
2022-08-06 21:00 | 79
2022-08-06 22:00 | 79
2022-08-06 23:00 | 80
2022-08-07 | 80
2022-08-07 01:00 | 79
2022-08-07 02:00 | 78
2022-08-07 03:00 | 79
2022-08-07 04:00 | 79
2022-08-07 05:00 | 78
2022-08-07 06:00 | 78
2022-08-07 07:00 | 78
2022-08-07 08:00 | 79
2022-08-07 09:00 | 80
2022-08-07 10:00 | 83
2022-08-07 11:00 | 85
2022-08-07 12:00 | 87
2022-08-07 13:00 | 88
2022-08-07 14:00 | 87
2022-08-07 15:00 | 87
2022-08-07 16:00 | 80
2022-08-07 17:00 | 83
2022-08-07 18:00 | 83
2022-08-07 19:00 | 82
2022-08-07 20:00 | 80
2022-08-07 21:00 | 80
2022-08-07 22:00 | 79
2022-08-07 23:00 | 79
2022-08-08 | 78
2022-08-08 01:00 | 78
2022-08-08 02:00 | 78
2022-08-08 03:00 | 78
2022-08-08 04:00 | 77
2022-08-08 05:00 | 77
2022-08-08 06:00 | 77
2022-08-08 07:00 | 78
2022-08-08 08:00 | 80
2022-08-08 09:00 | 83
2022-08-08 10:00 | 83
2022-08-08 11:00 | 85
2022-08-08 12:00 | 87
2022-08-08 13:00 | 87
2022-08-08 14:00 | 87
2022-08-08 15:00 | 87
2022-08-08 16:00 | 86
2022-08-08 17:00 | 81
2022-08-08 18:00 | 82
2022-08-08 19:00 | 81
2022-08-08 20:00 | 78
2022-08-08 21:00 | 78
2022-08-08 22:00 | 78
2022-08-08 23:00 | 78
2022-08-09 | 79
2022-08-09 01:00 | 78
2022-08-09 02:00 | 78
2022-08-09 03:00 | 79
2022-08-09 04:00 | 79
2022-08-09 05:00 | 77
2022-08-09 06:00 | 75
2022-08-09 07:00 | 79
2022-08-09 08:00 | 80
2022-08-09 09:00 | 85
2022-08-09 10:00 | 88
2022-08-09 11:00 | 92
2022-08-09 12:00 | 93
2022-08-09 13:00 | 93
2022-08-09 14:00 | 88
2022-08-09 15:00 | 89
2022-08-09 16:00 | 90
2022-08-09 17:00 | 89
2022-08-09 18:00 | 88
2022-08-09 19:00 | 89
2022-08-09 20:00 | 87
2022-08-09 21:00 | 85
2022-08-09 22:00 | 83
2022-08-09 23:00 | 83
2022-08-10 | 82
2022-08-10 01:00 | 84
2022-08-10 02:00 | 83
2022-08-10 03:00 | 80
2022-08-10 04:00 | 79
2022-08-10 05:00 | 77
2022-08-10 06:00 | 76
2022-08-10 07:00 | 76
2022-08-10 08:00 | 78
2022-08-10 09:00 | 81
2022-08-10 10:00 | 83
2022-08-10 11:00 | 85
2022-08-10 12:00 | 86
2022-08-10 13:00 | 83
2022-08-10 14:00 | 83
2022-08-10 15:00 | 82
2022-08-10 16:00 | 86
2022-08-10 17:00 | 80
2022-08-10 18:00 | 80
2022-08-10 19:00 | 78
2022-08-10 20:00 | 76
2022-08-10 21:00 | 76
2022-08-10 22:00 | 76
2022-08-10 23:00 | 76
2022-08-11 | 75
2022-08-11 01:00 | 75
2022-08-11 02:00 | 75
2022-08-11 03:00 | 74
2022-08-11 04:00 | 75
2022-08-11 05:00 | 74
2022-08-11 06:00 | 74
2022-08-11 07:00 | 74
2022-08-11 08:00 | 73
2022-08-11 09:00 | 74
2022-08-11 10:00 | 76
2022-08-11 11:00 | 79
2022-08-11 12:00 | 83
2022-08-11 13:00 | 83
2022-08-11 14:00 | 84
2022-08-11 15:00 | 84
2022-08-11 16:00 | 84
2022-08-11 17:00 | 82
2022-08-11 18:00 | 81
2022-08-11 19:00 | 78
2022-08-11 20:00 | 76
2022-08-11 21:00 | 76
2022-08-11 22:00 | 75
2022-08-11 23:00 | 74
2022-08-12 | 75
2022-08-12 01:00 | 77
2022-08-12 02:00 | 77
2022-08-12 03:00 | 75
2022-08-12 04:00 | 74
2022-08-12 05:00 | 73
2022-08-12 06:00 | 72
2022-08-12 07:00 | 72
2022-08-12 08:00 | 73
2022-08-12 09:00 | 76
2022-08-12 10:00 | 76
2022-08-12 11:00 | 78
2022-08-12 12:00 | 80
2022-08-12 13:00 | 83
2022-08-12 14:00 | 84
2022-08-12 15:00 | 84
2022-08-12 16:00 | 85
2022-08-12 17:00 | 84
2022-08-12 18:00 | 83
2022-08-12 19:00 | 77
2022-08-12 20:00 | 75
2022-08-12 21:00 | 75
2022-08-12 22:00 | 75
2022-08-12 23:00 | 75
2022-08-13 | 73
2022-08-13 01:00 | 71
2022-08-13 02:00 | 70
2022-08-13 03:00 | 68
2022-08-13 04:00 | 67
2022-08-13 05:00 | 66
2022-08-13 06:00 | 66
2022-08-13 07:00 | 67
2022-08-13 08:00 | 70
2022-08-13 09:00 | 72
2022-08-13 10:00 | 74
2022-08-13 11:00 | 75
2022-08-13 12:00 | 74
2022-08-13 13:00 | 76
2022-08-13 14:00 | 79
2022-08-13 15:00 | 80
2022-08-13 16:00 | 80
2022-08-13 17:00 | 80
2022-08-13 18:00 | 80
2022-08-13 19:00 | 78
2022-08-13 20:00 | 75
2022-08-13 21:00 | 72
2022-08-13 22:00 | 70
2022-08-13 23:00 | 70
2022-08-14 | 69
2022-08-14 01:00 | 70
2022-08-14 02:00 | 69
2022-08-14 03:00 | 69
2022-08-14 04:00 | 68
2022-08-14 05:00 | 68
2022-08-14 06:00 | 65
2022-08-14 07:00 | 68
2022-08-14 08:00 | 73
2022-08-14 09:00 | 74
2022-08-14 10:00 | 75
2022-08-14 11:00 | 77
2022-08-14 12:00 | 78
2022-08-14 13:00 | 78
2022-08-14 14:00 | 77
2022-08-14 15:00 | 81
2022-08-14 16:00 | 79
2022-08-14 17:00 | 77
2022-08-14 18:00 | 77
2022-08-14 19:00 | 75
2022-08-14 20:00 | 73
2022-08-14 21:00 | 73
2022-08-14 22:00 | 72
2022-08-14 23:00 | 71
2022-08-15 | 71
2022-08-15 01:00 | 70
2022-08-15 02:00 | 69
2022-08-15 03:00 | 68
2022-08-15 04:00 | 70
2022-08-15 05:00 | 69
2022-08-15 06:00 | 67
2022-08-15 07:00 | 67
2022-08-15 08:00 | 74
2022-08-15 09:00 | 75
2022-08-15 10:00 | 78
2022-08-15 11:00 | 79
2022-08-15 12:00 | 81
2022-08-15 13:00 | 78
2022-08-15 14:00 | 78
2022-08-15 15:00 | 81
2022-08-15 16:00 | 80
2022-08-15 17:00 | 79
2022-08-15 18:00 | 77
2022-08-15 19:00 | 75
2022-08-15 20:00 | 72
2022-08-15 21:00 | 71
2022-08-15 22:00 | 71
2022-08-15 23:00 | 69
2022-08-16 | 70
2022-08-16 01:00 | 67
2022-08-16 02:00 | 66
2022-08-16 03:00 | 65
2022-08-16 04:00 | 65
2022-08-16 05:00 | 63
2022-08-16 06:00 | 64
2022-08-16 07:00 | 66
2022-08-16 08:00 | 70
2022-08-16 09:00 | 74
2022-08-16 10:00 | 77
2022-08-16 11:00 | 79
2022-08-16 12:00 | 81
2022-08-16 13:00 | 80
2022-08-16 14:00 | 80
2022-08-16 15:00 | 80
2022-08-16 16:00 | 81
2022-08-16 17:00 | 80
2022-08-16 18:00 | 79
2022-08-16 19:00 | 76
2022-08-16 20:00 | 74
2022-08-16 21:00 | 73
2022-08-16 22:00 | 72
2022-08-16 23:00 | 71
2022-08-17 | 70
2022-08-17 01:00 | 70
2022-08-17 02:00 | 70
2022-08-17 03:00 | 68
2022-08-17 04:00 | 67
2022-08-17 05:00 | 67
2022-08-17 06:00 | 66
2022-08-17 07:00 | 68
2022-08-17 08:00 | 72
2022-08-17 09:00 | 74
2022-08-17 10:00 | 75
2022-08-17 11:00 | 71
2022-08-17 12:00 | 75
2022-08-17 13:00 | 80
2022-08-17 14:00 | 80
2022-08-17 15:00 | 79
2022-08-17 16:00 | 78
2022-08-17 17:00 | 78
2022-08-17 18:00 | 76
2022-08-17 19:00 | 76
2022-08-17 20:00 | 74
2022-08-17 21:00 | 73
2022-08-17 22:00 | 72
2022-08-17 23:00 | 67
2022-08-18 | 67
2022-08-18 01:00 | 67
2022-08-18 02:00 | 66
2022-08-18 03:00 | 65
2022-08-18 04:00 | 67
2022-08-18 05:00 | 67
2022-08-18 06:00 | 66
2022-08-18 07:00 | 67
2022-08-18 08:00 | 71
2022-08-18 09:00 | 74
2022-08-18 10:00 | 78
2022-08-18 11:00 | 80
2022-08-18 12:00 | 82
2022-08-18 13:00 | 84
2022-08-18 14:00 | 85
2022-08-18 15:00 | 84
2022-08-18 16:00 | 81
2022-08-18 17:00 | 77
2022-08-18 18:00 | 77
2022-08-18 19:00 | 76
2022-08-18 20:00 | 75
2022-08-18 21:00 | 75
2022-08-18 22:00 | 73
2022-08-18 23:00 | 72
2022-08-19 | 73
2022-08-19 01:00 | 73
2022-08-19 02:00 | 73
2022-08-19 03:00 | 73
2022-08-19 04:00 | 73
2022-08-19 05:00 | 72
2022-08-19 06:00 | 71
2022-08-19 07:00 | 71
2022-08-19 08:00 | 75
2022-08-19 09:00 | 79
2022-08-19 10:00 | 82
2022-08-19 11:00 | 85
2022-08-19 12:00 | 86
2022-08-19 13:00 | 86
2022-08-19 14:00 | 88
2022-08-19 15:00 | 85
2022-08-19 16:00 | 83
2022-08-19 17:00 | 83
2022-08-19 18:00 | 79
2022-08-19 19:00 | 79
2022-08-19 20:00 | 77
2022-08-19 21:00 | 76
2022-08-19 22:00 | 76
2022-08-19 23:00 | 75
2022-08-20 | 74
2022-08-20 01:00 | 74
2022-08-20 02:00 | 73
2022-08-20 03:00 | 73
2022-08-20 04:00 | 73
2022-08-20 05:00 | 73
2022-08-20 06:00 | 72
2022-08-20 07:00 | 73
2022-08-20 08:00 | 75
2022-08-20 09:00 | 77
2022-08-20 10:00 | 80
2022-08-20 11:00 | 84
2022-08-20 12:00 | 83
2022-08-20 13:00 | 85
2022-08-20 14:00 | 87
2022-08-20 15:00 | 88
2022-08-20 16:00 | 86
2022-08-20 17:00 | 84
2022-08-20 18:00 | 82
2022-08-20 19:00 | 79
2022-08-20 20:00 | 77
2022-08-20 21:00 | 76
2022-08-20 22:00 | 75
2022-08-20 23:00 | 74
2022-08-21 | 73
2022-08-21 01:00 | 72
2022-08-21 02:00 | 71
2022-08-21 03:00 | 71
2022-08-21 04:00 | 72
2022-08-21 05:00 | 71
2022-08-21 06:00 | 72
2022-08-21 07:00 | 72
2022-08-21 08:00 | 74
2022-08-21 09:00 | 75
2022-08-21 10:00 | 78
2022-08-21 11:00 | 79
2022-08-21 12:00 | 79
2022-08-21 13:00 | 79
2022-08-21 14:00 | 80
2022-08-21 15:00 | 80
2022-08-21 16:00 | 81
2022-08-21 17:00 | 78
2022-08-21 18:00 | 78
2022-08-21 19:00 | 76
2022-08-21 20:00 | 75
2022-08-21 21:00 | 75
2022-08-21 22:00 | 74
2022-08-21 23:00 | 74
2022-08-22 | 73
2022-08-22 01:00 | 73
2022-08-22 02:00 | 73
2022-08-22 03:00 | 73
2022-08-22 04:00 | 73
2022-08-22 05:00 | 73
2022-08-22 06:00 | 73
2022-08-22 07:00 | 73
2022-08-22 08:00 | 73
2022-08-22 09:00 | 74
2022-08-22 10:00 | 75
2022-08-22 11:00 | 75
2022-08-22 12:00 | 74
2022-08-22 13:00 | 74
2022-08-22 14:00 | 77
2022-08-22 15:00 | 77
2022-08-22 16:00 | 77
2022-08-22 17:00 | 78
2022-08-22 18:00 | 74
2022-08-22 19:00 | 74
2022-08-22 20:00 | 73
2022-08-22 21:00 | 73
2022-08-22 22:00 | 73
2022-08-22 23:00 | 74
2022-08-23 | 73
2022-08-23 01:00 | 73
2022-08-23 02:00 | 73
2022-08-23 03:00 | 73
2022-08-23 04:00 | 73
2022-08-23 05:00 | 73
2022-08-23 06:00 | 72
2022-08-23 07:00 | 72
2022-08-23 08:00 | 74
2022-08-23 09:00 | 77
2022-08-23 10:00 | 76
2022-08-23 11:00 | 79
2022-08-23 12:00 | 81
2022-08-23 13:00 | 82
2022-08-23 14:00 | 84
2022-08-23 15:00 | 82
2022-08-23 16:00 | 81
2022-08-23 17:00 | 80
2022-08-23 18:00 | 79
2022-08-23 19:00 | 79
2022-08-23 20:00 | 79
2022-08-23 21:00 | 80
2022-08-23 22:00 | 79
2022-08-23 23:00 | 78
2022-08-24 | 77
2022-08-24 01:00 | 75
2022-08-24 02:00 | 76
2022-08-24 03:00 | 74
2022-08-24 04:00 | 73
2022-08-24 05:00 | 73
2022-08-24 06:00 | 72
2022-08-24 07:00 | 73
2022-08-24 08:00 | 76
2022-08-24 09:00 | 80
2022-08-24 10:00 | 82
2022-08-24 11:00 | 84
2022-08-24 12:00 | 87
2022-08-24 13:00 | 88
2022-08-24 14:00 | 88
2022-08-24 15:00 | 87
2022-08-24 16:00 | 87
2022-08-24 17:00 | 84
2022-08-24 18:00 | 81
2022-08-24 19:00 | 80
2022-08-24 20:00 | 78
2022-08-24 21:00 | 77
2022-08-24 22:00 | 76
2022-08-24 23:00 | 77
2022-08-25 | 79
2022-08-25 01:00 | 79
2022-08-25 02:00 | 78
2022-08-25 03:00 | 76
2022-08-25 04:00 | 73
2022-08-25 05:00 | 70
2022-08-25 06:00 | 73
2022-08-25 07:00 | 76
2022-08-25 08:00 | 79
2022-08-25 09:00 | 82
2022-08-25 10:00 | 85
2022-08-25 11:00 | 87
2022-08-25 12:00 | 88
2022-08-25 13:00 | 91
2022-08-25 14:00 | 89
2022-08-25 15:00 | 88
2022-08-25 16:00 | 87
2022-08-25 17:00 | 86
2022-08-25 18:00 | 82
2022-08-25 19:00 | 79
2022-08-25 20:00 | 77
2022-08-25 21:00 | 79
2022-08-25 22:00 | 79
2022-08-25 23:00 | 77
2022-08-26 | 77
2022-08-26 01:00 | 75
2022-08-26 02:00 | 75
2022-08-26 03:00 | 76
2022-08-26 04:00 | 74
2022-08-26 05:00 | 73
2022-08-26 06:00 | 73
2022-08-26 07:00 | 74
2022-08-26 08:00 | 77
2022-08-26 09:00 | 79
2022-08-26 10:00 | 79
2022-08-26 11:00 | 83
2022-08-26 12:00 | 82
2022-08-26 13:00 | 84
2022-08-26 14:00 | 82
2022-08-26 15:00 | 83
2022-08-26 16:00 | 83
2022-08-26 17:00 | 79
2022-08-26 18:00 | 79
2022-08-26 19:00 | 79
2022-08-26 20:00 | 79
2022-08-26 21:00 | 79
2022-08-26 22:00 | 77
2022-08-26 23:00 | 77
2022-08-27 | 77
2022-08-27 01:00 | 76
2022-08-27 02:00 | 77
2022-08-27 03:00 | 75
2022-08-27 04:00 | 75
2022-08-27 05:00 | 76
2022-08-27 06:00 | 76
2022-08-27 07:00 | 76
2022-08-27 08:00 | 77
2022-08-27 09:00 | 80
2022-08-27 10:00 | 82
2022-08-27 11:00 | 85
2022-08-27 12:00 | 85
2022-08-27 13:00 | 90
2022-08-27 14:00 | 87
2022-08-27 15:00 | 85
2022-08-27 16:00 | 85
2022-08-27 17:00 | 84
2022-08-27 18:00 | 80
2022-08-27 19:00 | 79
2022-08-27 20:00 | 77
2022-08-27 21:00 | 76
2022-08-27 22:00 | 75
2022-08-27 23:00 | 75
2022-08-28 | 74
2022-08-28 01:00 | 73
2022-08-28 02:00 | 73
2022-08-28 03:00 | 74
2022-08-28 04:00 | 73
2022-08-28 05:00 | 73
2022-08-28 06:00 | 73
2022-08-28 07:00 | 73
2022-08-28 08:00 | 74
2022-08-28 09:00 | 75
2022-08-28 10:00 | 77
2022-08-28 11:00 | 78
2022-08-28 12:00 | 78
2022-08-28 13:00 | 79
2022-08-28 14:00 | 83
2022-08-28 15:00 | 79
2022-08-28 16:00 | 81
2022-08-28 17:00 | 79
2022-08-28 18:00 | 77
2022-08-28 19:00 | 75
2022-08-28 20:00 | 74
2022-08-28 21:00 | 73
2022-08-28 22:00 | 73
2022-08-28 23:00 | 74
2022-08-29 | 74
2022-08-29 01:00 | 74
2022-08-29 02:00 | 75
2022-08-29 03:00 | 75
2022-08-29 04:00 | 75
2022-08-29 05:00 | 74
2022-08-29 06:00 | 74
2022-08-29 07:00 | 74
2022-08-29 08:00 | 74.9
2022-08-29 09:00 | 77
2022-08-29 10:00 | 80
2022-08-29 11:00 | 82
2022-08-29 12:00 | 82
2022-08-29 13:00 | 83
2022-08-29 14:00 | 83
2022-08-29 15:00 | 84
2022-08-29 16:00 | 82
2022-08-29 17:00 | 81
2022-08-29 18:00 | 80
2022-08-29 19:00 | 78
2022-08-29 20:00 | 77
2022-08-29 21:00 | 77
2022-08-29 22:00 | 76
2022-08-29 23:00 | 76
2022-08-30 | 76
2022-08-30 01:00 | 75
2022-08-30 02:00 | 75
2022-08-30 03:00 | 74
2022-08-30 04:00 | 74
2022-08-30 05:00 | 74
2022-08-30 06:00 | 75
2022-08-30 07:00 | 75
2022-08-30 08:00 | 76
2022-08-30 09:00 | 78
2022-08-30 10:00 | 80
2022-08-30 11:00 | 81
2022-08-30 12:00 | 82
2022-08-30 13:00 | 83
2022-08-30 14:00 | 85
2022-08-30 15:00 | 86
2022-08-30 16:00 | 83
2022-08-30 17:00 | 82
2022-08-30 18:00 | 80
2022-08-30 19:00 | 78
2022-08-30 20:00 | 78
2022-08-30 21:00 | 78
2022-08-30 22:00 | 78
2022-08-30 23:00 | 75
2022-08-31 | 74
2022-08-31 01:00 | 74
2022-08-31 02:00 | 75
2022-08-31 03:00 | 74
2022-08-31 04:00 | 74
2022-08-31 05:00 | 73
2022-08-31 06:00 | 72
2022-08-31 07:00 | 72
2022-08-31 08:00 | 75
2022-08-31 09:00 | 77
2022-08-31 10:00 | 80
2022-08-31 11:00 | 82
2022-08-31 12:00 | 84
2022-08-31 13:00 | 85
2022-08-31 14:00 | 84
2022-08-31 15:00 | 88
2022-08-31 16:00 | 88
2022-08-31 17:00 | 87
2022-08-31 18:00 | 85
2022-08-31 19:00 | 82
2022-08-31 20:00 | 79
2022-08-31 21:00 | 79
2022-08-31 22:00 | 78
2022-08-31 23:00 | 78
2022-09-01 | 77
2022-09-01 01:00 | 76
2022-09-01 02:00 | 75
2022-09-01 03:00 | 73
2022-09-01 04:00 | 72
2022-09-01 05:00 | 71
2022-09-01 06:00 | 70
2022-09-01 07:00 | 72
2022-09-01 08:00 | 74
2022-09-01 09:00 | 77
2022-09-01 10:00 | 79
2022-09-01 11:00 | 82
2022-09-01 12:00 | 83
2022-09-01 13:00 | 84
2022-09-01 14:00 | 87
2022-09-01 15:00 | 88
2022-09-01 16:00 | 89
2022-09-01 17:00 | 88
2022-09-01 18:00 | 87
2022-09-01 19:00 | 84
2022-09-01 20:00 | 81
2022-09-01 21:00 | 78
2022-09-01 22:00 | 77
2022-09-01 23:00 | 74
2022-09-02 | 72
2022-09-02 01:00 | 69
2022-09-02 02:00 | 66
2022-09-02 03:00 | 65
2022-09-02 04:00 | 64
2022-09-02 05:00 | 62
2022-09-02 06:00 | 62
2022-09-02 07:00 | 63
2022-09-02 08:00 | 66
2022-09-02 09:00 | 70
2022-09-02 10:00 | 72
2022-09-02 11:00 | 74
2022-09-02 12:00 | 75
2022-09-02 13:00 | 76
2022-09-02 14:00 | 77
2022-09-02 15:00 | 76
2022-09-02 16:00 | 76
2022-09-02 17:00 | 76
2022-09-02 18:00 | 75
2022-09-02 19:00 | 72
2022-09-02 20:00 | 71
2022-09-02 21:00 | 69
2022-09-02 22:00 | 69
2022-09-02 23:00 | 67
2022-09-03 | 67
2022-09-03 01:00 | 65
2022-09-03 02:00 | 64
2022-09-03 03:00 | 63
2022-09-03 04:00 | 63
2022-09-03 05:00 | 62
2022-09-03 06:00 | 63
2022-09-03 07:00 | 64
2022-09-03 08:00 | 68
2022-09-03 09:00 | 73
2022-09-03 10:00 | 73
2022-09-03 11:00 | 76
2022-09-03 12:00 | 77
2022-09-03 13:00 | 78
2022-09-03 14:00 | 78
2022-09-03 15:00 | 78
2022-09-03 16:00 | 76
2022-09-03 17:00 | 75
2022-09-03 18:00 | 76
2022-09-03 19:00 | 73
2022-09-03 20:00 | 72
2022-09-03 21:00 | 72
2022-09-03 22:00 | 72
2022-09-03 23:00 | 72
2022-09-04 | 72
2022-09-04 01:00 | 72
2022-09-04 02:00 | 73
2022-09-04 03:00 | 72
2022-09-04 04:00 | 72
2022-09-04 05:00 | 72
2022-09-04 06:00 | 72
2022-09-04 07:00 | 72
2022-09-04 08:00 | 75
2022-09-04 09:00 | 76
2022-09-04 10:00 | 78
2022-09-04 11:00 | 81
2022-09-04 12:00 | 80
2022-09-04 13:00 | 85
2022-09-04 14:00 | 84
2022-09-04 15:00 | 84
2022-09-04 16:00 | 82
2022-09-04 17:00 | 79.5
2022-09-04 18:00 | 78
2022-09-04 19:00 | 78
2022-09-04 20:00 | 77
2022-09-04 21:00 | 77
2022-09-04 22:00 | 75
2022-09-04 23:00 | 75
2022-09-05 | 75
2022-09-05 01:00 | 73
2022-09-05 02:00 | 73
2022-09-05 03:00 | 73
2022-09-05 04:00 | 72
2022-09-05 05:00 | 73
2022-09-05 06:00 | 72
2022-09-05 07:00 | 73
2022-09-05 08:00 | 74
2022-09-05 09:00 | 76
2022-09-05 10:00 | 77
2022-09-05 11:00 | 80
2022-09-05 12:00 | 81
2022-09-05 13:00 | 82
2022-09-05 14:00 | 83
2022-09-05 15:00 | 82
2022-09-05 16:00 | 79
2022-09-05 17:00 | 79
2022-09-05 18:00 | 78
2022-09-05 19:00 | 77
2022-09-05 20:00 | 76
2022-09-05 21:00 | 76
2022-09-05 22:00 | 76
2022-09-05 23:00 | 75
2022-09-06 | 75
2022-09-06 01:00 | 75
2022-09-06 02:00 | 74
2022-09-06 03:00 | 75
2022-09-06 04:00 | 75
2022-09-06 05:00 | 74
2022-09-06 06:00 | 75
2022-09-06 07:00 | 74
2022-09-06 08:00 | 74
2022-09-06 09:00 | 74
2022-09-06 10:00 | 73
2022-09-06 11:00 | 73
2022-09-06 12:00 | 73
2022-09-06 13:00 | 71
2022-09-06 14:00 | 70
2022-09-06 15:00 | 71
2022-09-06 16:00 | 70
2022-09-06 17:00 | 68
2022-09-06 18:00 | 69
2022-09-06 19:00 | 69
2022-09-06 20:00 | 70
2022-09-06 21:00 | 69
2022-09-06 22:00 | 67
2022-09-06 23:00 | 67
2022-09-07 | 67
2022-09-07 01:00 | 68
2022-09-07 02:00 | 67
2022-09-07 03:00 | 67
2022-09-07 04:00 | 67
2022-09-07 05:00 | 67
2022-09-07 06:00 | 66
2022-09-07 07:00 | 67
2022-09-07 08:00 | 67
2022-09-07 09:00 | 66
2022-09-07 10:00 | 69
2022-09-07 11:00 | 70
2022-09-07 12:00 | 71
2022-09-07 13:00 | 70
2022-09-07 14:00 | 71
2022-09-07 15:00 | 73
2022-09-07 16:00 | 74
2022-09-07 17:00 | 74
2022-09-07 18:00 | 73
2022-09-07 19:00 | 72
2022-09-07 20:00 | 72
2022-09-07 21:00 | 71
2022-09-07 22:00 | 71
2022-09-07 23:00 | 70
2022-09-08 | 70
2022-09-08 01:00 | 69
2022-09-08 02:00 | 68
2022-09-08 03:00 | 69
2022-09-08 04:00 | 67
2022-09-08 05:00 | 66
2022-09-08 06:00 | 65
2022-09-08 07:00 | 65
2022-09-08 08:00 | 68
2022-09-08 09:00 | 69
2022-09-08 10:00 | 72
2022-09-08 11:00 | 75
2022-09-08 12:00 | 74
2022-09-08 13:00 | 76
2022-09-08 14:00 | 79
2022-09-08 15:00 | 78
2022-09-08 16:00 | 79
2022-09-08 17:00 | 78
2022-09-08 18:00 | 74
2022-09-08 19:00 | 72
2022-09-08 20:00 | 70
2022-09-08 21:00 | 68
2022-09-08 22:00 | 68
2022-09-08 23:00 | 69
2022-09-09 | 68
2022-09-09 01:00 | 67
2022-09-09 02:00 | 63
2022-09-09 03:00 | 63
2022-09-09 04:00 | 63
2022-09-09 05:00 | 62
2022-09-09 06:00 | 60
2022-09-09 07:00 | 62
2022-09-09 08:00 | 65
2022-09-09 09:00 | 68
2022-09-09 10:00 | 71
2022-09-09 11:00 | 75
2022-09-09 12:00 | 77
2022-09-09 13:00 | 76
2022-09-09 14:00 | 76
2022-09-09 15:00 | 77
2022-09-09 16:00 | 76
2022-09-09 17:00 | 75
2022-09-09 18:00 | 73
2022-09-09 19:00 | 71
2022-09-09 20:00 | 69
2022-09-09 21:00 | 69
2022-09-09 22:00 | 68
2022-09-09 23:00 | 67
2022-09-10 | 67
2022-09-10 01:00 | 66
2022-09-10 02:00 | 68
2022-09-10 03:00 | 67
2022-09-10 04:00 | 66
2022-09-10 05:00 | 67
2022-09-10 06:00 | 65
2022-09-10 07:00 | 66
2022-09-10 08:00 | 68
2022-09-10 09:00 | 73
2022-09-10 10:00 | 76
2022-09-10 11:00 | 79
2022-09-10 12:00 | 80
2022-09-10 13:00 | 80
2022-09-10 14:00 | 81
2022-09-10 15:00 | 82
2022-09-10 16:00 | 79
2022-09-10 17:00 | 78
2022-09-10 18:00 | 77
2022-09-10 19:00 | 74
2022-09-10 20:00 | 74
2022-09-10 21:00 | 73
2022-09-10 22:00 | 72
2022-09-10 23:00 | 72
2022-09-11 | 71
2022-09-11 01:00 | 71
2022-09-11 02:00 | 72
2022-09-11 03:00 | 71
2022-09-11 04:00 | 71
2022-09-11 05:00 | 71
2022-09-11 06:00 | 71
2022-09-11 07:00 | 72
2022-09-11 08:00 | 73
2022-09-11 09:00 | 74
2022-09-11 10:00 | 75
2022-09-11 11:00 | 76
2022-09-11 12:00 | 74
2022-09-11 13:00 | 74
2022-09-11 14:00 | 75
2022-09-11 15:00 | 75
2022-09-11 16:00 | 76
2022-09-11 17:00 | 73
2022-09-11 18:00 | 72
2022-09-11 19:00 | 70
2022-09-11 20:00 | 69
2022-09-11 21:00 | 68
2022-09-11 22:00 | 69
2022-09-11 23:00 | 71
2022-09-12 | 71
2022-09-12 01:00 | 72
2022-09-12 02:00 | 72
2022-09-12 03:00 | 73
2022-09-12 04:00 | 72
2022-09-12 05:00 | 71
2022-09-12 06:00 | 70
2022-09-12 07:00 | 69
2022-09-12 08:00 | 69
2022-09-12 09:00 | 68
2022-09-12 10:00 | 69
2022-09-12 11:00 | 73
2022-09-12 12:00 | 74
2022-09-12 13:00 | 74
2022-09-12 14:00 | 78
2022-09-12 15:00 | 77
2022-09-12 16:00 | 77
2022-09-12 17:00 | 78
2022-09-12 18:00 | 77
2022-09-12 19:00 | 75
2022-09-12 20:00 | 73
2022-09-12 21:00 | 73
2022-09-12 22:00 | 74
2022-09-12 23:00 | 73
2022-09-13 | 74
2022-09-13 01:00 | 74
2022-09-13 02:00 | 74
2022-09-13 03:00 | 74
2022-09-13 04:00 | 74
2022-09-13 05:00 | 74
2022-09-13 06:00 | 70
2022-09-13 07:00 | 71
2022-09-13 08:00 | 73
2022-09-13 09:00 | 75
2022-09-13 10:00 | 77
2022-09-13 11:00 | 78
2022-09-13 12:00 | 80
2022-09-13 13:00 | 84
2022-09-13 14:00 | 85
2022-09-13 15:00 | 87
2022-09-13 16:00 | 81
2022-09-13 17:00 | 79
2022-09-13 18:00 | 78
2022-09-13 19:00 | 81
2022-09-13 20:00 | 79
2022-09-13 21:00 | 77
2022-09-13 22:00 | 76
2022-09-13 23:00 | 75
2022-09-14 | 73
2022-09-14 01:00 | 71
2022-09-14 02:00 | 70
2022-09-14 03:00 | 69
2022-09-14 04:00 | 67.2
2022-09-14 05:00 | 66
2022-09-14 06:00 | 66
2022-09-14 07:00 | 65
2022-09-14 08:00 | 67
2022-09-14 09:00 | 69
2022-09-14 10:00 | 72
2022-09-14 11:00 | 73
2022-09-14 12:00 | 77
2022-09-14 13:00 | 78
2022-09-14 14:00 | 81
2022-09-14 15:00 | 82
2022-09-14 16:00 | 83
2022-09-14 17:00 | 82
2022-09-14 18:00 | 80
2022-09-14 19:00 | 78
2022-09-14 20:00 | 77
2022-09-14 21:00 | 76
2022-09-14 22:00 | 74
2022-09-14 23:00 | 73
2022-09-15 | 74
2022-09-15 01:00 | 73
2022-09-15 02:00 | 73
2022-09-15 03:00 | 72
2022-09-15 04:00 | 71
2022-09-15 05:00 | 69
2022-09-15 06:00 | 68
2022-09-15 07:00 | 66
2022-09-15 08:00 | 66
2022-09-15 09:00 | 67
2022-09-15 10:00 | 69
2022-09-15 11:00 | 70
2022-09-15 12:00 | 71
2022-09-15 13:00 | 72
2022-09-15 14:00 | 73
2022-09-15 15:00 | 75
2022-09-15 16:00 | 76
2022-09-15 17:00 | 75
2022-09-15 18:00 | 74
2022-09-15 19:00 | 72
2022-09-15 20:00 | 70
2022-09-15 21:00 | 68
2022-09-15 22:00 | 68
2022-09-15 23:00 | 67
2022-09-16 | 63
2022-09-16 01:00 | 62
2022-09-16 02:00 | 61
2022-09-16 03:00 | 60
2022-09-16 04:00 | 56
2022-09-16 05:00 | 56
2022-09-16 06:00 | 58
2022-09-16 07:00 | 56
2022-09-16 08:00 | 60
2022-09-16 09:00 | 64
2022-09-16 10:00 | 67
2022-09-16 11:00 | 69
2022-09-16 12:00 | 71
2022-09-16 13:00 | 71
2022-09-16 14:00 | 72
2022-09-16 15:00 | 75
2022-09-16 16:00 | 77
2022-09-16 17:00 | 78
2022-09-16 18:00 | 76
2022-09-16 19:00 | 72
2022-09-16 20:00 | 69
2022-09-16 21:00 | 68
2022-09-16 22:00 | 68
2022-09-16 23:00 | 66
2022-09-17 | 66
2022-09-17 01:00 | 67
2022-09-17 02:00 | 67
2022-09-17 03:00 | 67
2022-09-17 04:00 | 66
2022-09-17 05:00 | 66
2022-09-17 06:00 | 65
2022-09-17 07:00 | 65
2022-09-17 08:00 | 66
2022-09-17 09:00 | 68
2022-09-17 10:00 | 69
2022-09-17 11:00 | 72
2022-09-17 12:00 | 72
2022-09-17 13:00 | 73
2022-09-17 14:00 | 73
2022-09-17 15:00 | 73
2022-09-17 16:00 | 73
2022-09-17 17:00 | 72
2022-09-17 18:00 | 71
2022-09-17 19:00 | 70
2022-09-17 20:00 | 69
2022-09-17 21:00 | 69
2022-09-17 22:00 | 70
2022-09-17 23:00 | 71
2022-09-18 | 71
2022-09-18 01:00 | 70
2022-09-18 02:00 | 69
2022-09-18 03:00 | 69
2022-09-18 04:00 | 68
2022-09-18 05:00 | 68
2022-09-18 06:00 | 67
2022-09-18 07:00 | 68
2022-09-18 08:00 | 69
2022-09-18 09:00 | 71
2022-09-18 10:00 | 73
2022-09-18 11:00 | 76
2022-09-18 12:00 | 78
2022-09-18 13:00 | 80
2022-09-18 14:00 | 81
2022-09-18 15:00 | 84
2022-09-18 16:00 | 82
2022-09-18 17:00 | 79
2022-09-18 18:00 | 78
2022-09-18 19:00 | 78
2022-09-18 20:00 | 77
2022-09-18 21:00 | 76
2022-09-18 22:00 | 75
2022-09-18 23:00 | 74
2022-09-19 | 73
2022-09-19 01:00 | 73
2022-09-19 02:00 | 72
2022-09-19 03:00 | 72
2022-09-19 04:00 | 72
2022-09-19 05:00 | 71
2022-09-19 06:00 | 69
2022-09-19 07:00 | 71
2022-09-19 08:00 | 71
2022-09-19 09:00 | 73
2022-09-19 10:00 | 76
2022-09-19 11:00 | 79
2022-09-19 12:00 | 83
2022-09-19 13:00 | 83
2022-09-19 14:00 | 80
2022-09-19 15:00 | 80
2022-09-19 16:00 | 81
2022-09-19 17:00 | 80
2022-09-19 18:00 | 75
2022-09-19 19:00 | 73
2022-09-19 20:00 | 73
2022-09-19 21:00 | 73
2022-09-19 22:00 | 72
2022-09-19 23:00 | 73
2022-09-20 | 72
2022-09-20 01:00 | 71
2022-09-20 02:00 | 71
2022-09-20 03:00 | 71
2022-09-20 04:00 | 69
2022-09-20 05:00 | 70
2022-09-20 06:00 | 70
2022-09-20 07:00 | 69
2022-09-20 08:00 | 71
2022-09-20 09:00 | 74
2022-09-20 10:00 | 75
2022-09-20 11:00 | 78
2022-09-20 12:00 | 77
2022-09-20 13:00 | 79
2022-09-20 14:00 | 79
2022-09-20 15:00 | 83
2022-09-20 16:00 | 82
2022-09-20 17:00 | 78
2022-09-20 18:00 | 78
2022-09-20 19:00 | 76
2022-09-20 20:00 | 75
2022-09-20 21:00 | 74
2022-09-20 22:00 | 73
2022-09-20 23:00 | 72
2022-09-21 | 71
2022-09-21 01:00 | 69
2022-09-21 02:00 | 68
2022-09-21 03:00 | 67
2022-09-21 04:00 | 66
2022-09-21 05:00 | 64
2022-09-21 06:00 | 63
2022-09-21 07:00 | 63
2022-09-21 08:00 | 68
2022-09-21 09:00 | 70
2022-09-21 10:00 | 72
2022-09-21 11:00 | 74
2022-09-21 12:00 | 75
2022-09-21 13:00 | 75
2022-09-21 14:00 | 76
2022-09-21 15:00 | 78
2022-09-21 16:00 | 75
2022-09-21 17:00 | 74
2022-09-21 18:00 | 73
2022-09-21 19:00 | 72
2022-09-21 20:00 | 72
2022-09-21 21:00 | 72
2022-09-21 22:00 | 73
2022-09-21 23:00 | 73
2022-09-22 | 71
2022-09-22 01:00 | 70
2022-09-22 02:00 | 70
2022-09-22 03:00 | 70
2022-09-22 04:00 | 70
2022-09-22 05:00 | 72
2022-09-22 06:00 | 71
2022-09-22 07:00 | 72
2022-09-22 08:00 | 72
2022-09-22 09:00 | 72
2022-09-22 10:00 | 75
2022-09-22 11:00 | 78
2022-09-22 12:00 | 78
2022-09-22 13:00 | 69
2022-09-22 14:00 | 66
2022-09-22 15:00 | 62
2022-09-22 16:00 | 64
2022-09-22 17:00 | 69
2022-09-22 18:00 | 70
2022-09-22 19:00 | 70
2022-09-22 20:00 | 67
2022-09-22 21:00 | 64
2022-09-22 22:00 | 62
2022-09-22 23:00 | 61
2022-09-23 | 59
2022-09-23 01:00 | 58
2022-09-23 02:00 | 57
2022-09-23 03:00 | 56
2022-09-23 04:00 | 55
2022-09-23 05:00 | 54
2022-09-23 06:00 | 53
2022-09-23 07:00 | 52
2022-09-23 08:00 | 53
2022-09-23 09:00 | 55
2022-09-23 10:00 | 57
2022-09-23 11:00 | 60
2022-09-23 12:00 | 61
2022-09-23 13:00 | 63
2022-09-23 14:00 | 64
2022-09-23 15:00 | 65
2022-09-23 16:00 | 66
2022-09-23 17:00 | 64
2022-09-23 18:00 | 62
2022-09-23 19:00 | 59
2022-09-23 20:00 | 57
2022-09-23 21:00 | 56
2022-09-23 22:00 | 54
2022-09-23 23:00 | 53
2022-09-24 | 51
2022-09-24 01:00 | 51
2022-09-24 02:00 | 50
2022-09-24 03:00 | 50
2022-09-24 04:00 | 50
2022-09-24 05:00 | 50
2022-09-24 06:00 | 49
2022-09-24 07:00 | 50
2022-09-24 08:00 | 54
2022-09-24 09:00 | 55
2022-09-24 10:00 | 59
2022-09-24 11:00 | 62
2022-09-24 12:00 | 64
2022-09-24 13:00 | 67
2022-09-24 14:00 | 69
2022-09-24 15:00 | 71
2022-09-24 16:00 | 71
2022-09-24 17:00 | 71
2022-09-24 18:00 | 69
2022-09-24 19:00 | 66
2022-09-24 20:00 | 66
2022-09-24 21:00 | 65
2022-09-24 22:00 | 65
2022-09-24 23:00 | 63
2022-09-25 | 62
2022-09-25 01:00 | 62
2022-09-25 02:00 | 62
2022-09-25 03:00 | 62
2022-09-25 04:00 | 61
2022-09-25 05:00 | 62
2022-09-25 06:00 | 62
2022-09-25 07:00 | 62
2022-09-25 08:00 | 63
2022-09-25 09:00 | 66
2022-09-25 10:00 | 68
2022-09-25 11:00 | 70
2022-09-25 12:00 | 72
2022-09-25 13:00 | 70
2022-09-25 14:00 | 73
2022-09-25 15:00 | 76
2022-09-25 16:00 | 72
2022-09-25 17:00 | 68
2022-09-25 18:00 | 67
2022-09-25 19:00 | 66
2022-09-25 20:00 | 66
2022-09-25 21:00 | 67
2022-09-25 22:00 | 64
2022-09-25 23:00 | 63
2022-09-26 | 62
2022-09-26 01:00 | 62
2022-09-26 02:00 | 61
2022-09-26 03:00 | 60
2022-09-26 04:00 | 60
2022-09-26 05:00 | 59
2022-09-26 06:00 | 59
2022-09-26 07:00 | 60
2022-09-26 08:00 | 62
2022-09-26 09:00 | 63
2022-09-26 10:00 | 65
2022-09-26 11:00 | 69
2022-09-26 12:00 | 70
2022-09-26 13:00 | 73
2022-09-26 14:00 | 73
2022-09-26 15:00 | 74
2022-09-26 16:00 | 73
2022-09-26 17:00 | 72
2022-09-26 18:00 | 69
2022-09-26 19:00 | 68
2022-09-26 20:00 | 68
2022-09-26 21:00 | 68
2022-09-26 22:00 | 67
2022-09-26 23:00 | 68
2022-09-27 | 67
2022-09-27 01:00 | 67
2022-09-27 02:00 | 66
2022-09-27 03:00 | 64
2022-09-27 04:00 | 63
2022-09-27 05:00 | 63
2022-09-27 06:00 | 63
2022-09-27 07:00 | 62
2022-09-27 08:00 | 62
2022-09-27 09:00 | 65
2022-09-27 10:00 | 66
2022-09-27 11:00 | 67
2022-09-27 12:00 | 68
2022-09-27 13:00 | 69
2022-09-27 14:00 | 71
2022-09-27 15:00 | 72
2022-09-27 16:00 | 69
2022-09-27 17:00 | 70
2022-09-27 18:00 | 69
2022-09-27 19:00 | 67
2022-09-27 20:00 | 65
2022-09-27 21:00 | 66
2022-09-27 22:00 | 64
2022-09-27 23:00 | 63
2022-09-28 | 63
2022-09-28 01:00 | 61
2022-09-28 02:00 | 59
2022-09-28 03:00 | 58
2022-09-28 04:00 | 57
2022-09-28 05:00 | 56
2022-09-28 06:00 | 55
2022-09-28 07:00 | 54
2022-09-28 08:00 | 56
2022-09-28 09:00 | 60
2022-09-28 10:00 | 62
2022-09-28 11:00 | 65
2022-09-28 12:00 | 68
2022-09-28 13:00 | 69
2022-09-28 14:00 | 72
2022-09-28 15:00 | 70
2022-09-28 16:00 | 72
2022-09-28 17:00 | 69
2022-09-28 18:00 | 68
2022-09-28 19:00 | 68
2022-09-28 20:00 | 66
2022-09-28 21:00 | 69
2022-09-28 22:00 | 67
2022-09-28 23:00 | 64
2022-09-29 | 63
2022-09-29 01:00 | 61
2022-09-29 02:00 | 60
2022-09-29 03:00 | 58
2022-09-29 04:00 | 57
2022-09-29 05:00 | 56
2022-09-29 06:00 | 56
2022-09-29 07:00 | 56
2022-09-29 08:00 | 57
2022-09-29 09:00 | 59
2022-09-29 10:00 | 62
2022-09-29 11:00 | 65
2022-09-29 12:00 | 65
2022-09-29 13:00 | 66
2022-09-29 14:00 | 67
2022-09-29 15:00 | 67
2022-09-29 16:00 | 67
2022-09-29 17:00 | 67
2022-09-29 18:00 | 64
2022-09-29 19:00 | 63
2022-09-29 20:00 | 61
2022-09-29 21:00 | 60
2022-09-29 22:00 | 60
2022-09-29 23:00 | 58
2022-09-30 | 58
2022-09-30 01:00 | 57
2022-09-30 02:00 | 56
2022-09-30 03:00 | 55
2022-09-30 04:00 | 55
2022-09-30 05:00 | 55
2022-09-30 06:00 | 54
2022-09-30 07:00 | 54
2022-09-30 08:00 | 54
2022-09-30 09:00 | 55
2022-09-30 10:00 | 57
2022-09-30 11:00 | 59
2022-09-30 12:00 | 62
2022-09-30 13:00 | 63
2022-09-30 14:00 | 63
2022-09-30 15:00 | 64
2022-09-30 16:00 | 63
2022-09-30 17:00 | 62
2022-09-30 18:00 | 62
2022-09-30 19:00 | 61
2022-09-30 20:00 | 60
2022-09-30 21:00 | 60
2022-09-30 22:00 | 60
2022-09-30 23:00 | 61
2022-10-01 | 59
2022-10-01 01:00 | 59
2022-10-01 02:00 | 59
2022-10-01 03:00 | 58
2022-10-01 04:00 | 59
2022-10-01 05:00 | 57
2022-10-01 06:00 | 55
2022-10-01 07:00 | 54
2022-10-01 08:00 | 53
2022-10-01 09:00 | 54
2022-10-01 10:00 | 55
2022-10-01 11:00 | 55
2022-10-01 12:00 | 56
2022-10-01 13:00 | 60
2022-10-01 14:00 | 60
2022-10-01 15:00 | 60
2022-10-01 16:00 | 60
2022-10-01 17:00 | 60
2022-10-01 18:00 | 59
2022-10-01 19:00 | 58
2022-10-01 20:00 | 57
2022-10-01 21:00 | 57
2022-10-01 22:00 | 57
2022-10-01 23:00 | 58
2022-10-02 | 59
2022-10-02 01:00 | 59
2022-10-02 02:00 | 59
2022-10-02 03:00 | 59
2022-10-02 04:00 | 59
2022-10-02 05:00 | 59
2022-10-02 06:00 | 59
2022-10-02 07:00 | 60
2022-10-02 08:00 | 60
2022-10-02 09:00 | 59
2022-10-02 10:00 | 57
2022-10-02 11:00 | 58
2022-10-02 12:00 | 57
2022-10-02 13:00 | 56
2022-10-02 14:00 | 56
2022-10-02 15:00 | 55.5
2022-10-02 16:00 | 55
2022-10-02 17:00 | 55
2022-10-02 18:00 | 54
2022-10-02 19:00 | 53
2022-10-02 20:00 | 54
2022-10-02 21:00 | 52
2022-10-02 22:00 | 51
2022-10-02 23:00 | 51
2022-10-03 | 50
2022-10-03 01:00 | 51
2022-10-03 02:00 | 50
2022-10-03 03:00 | 50
2022-10-03 04:00 | 50
2022-10-03 05:00 | 51
2022-10-03 06:00 | 51
2022-10-03 07:00 | 51
2022-10-03 08:00 | 51
2022-10-03 09:00 | 51
2022-10-03 10:00 | 50
2022-10-03 11:00 | 51
2022-10-03 12:00 | 51
2022-10-03 13:00 | 50
2022-10-03 14:00 | 50
2022-10-03 15:00 | 50
2022-10-03 16:00 | 50
2022-10-03 17:00 | 50
2022-10-03 18:00 | 50
2022-10-03 19:00 | 50
2022-10-03 20:00 | 49
2022-10-03 21:00 | 50
2022-10-03 22:00 | 49
2022-10-03 23:00 | 49
2022-10-04 | 49
2022-10-04 01:00 | 49
2022-10-04 02:00 | 47
2022-10-04 03:00 | 47
2022-10-04 04:00 | 47
2022-10-04 05:00 | 47
2022-10-04 06:00 | 48
2022-10-04 07:00 | 48
2022-10-04 08:00 | 48
2022-10-04 09:00 | 49
2022-10-04 10:00 | 51
2022-10-04 11:00 | 52
2022-10-04 12:00 | 51
2022-10-04 13:00 | 52
2022-10-04 14:00 | 53
2022-10-04 15:00 | 53
2022-10-04 16:00 | 54
2022-10-04 17:00 | 54
2022-10-04 18:00 | 54
2022-10-04 19:00 | 55
2022-10-04 20:00 | 55
2022-10-04 21:00 | 55
2022-10-04 22:00 | 55
2022-10-04 23:00 | 55
2022-10-05 | 56
2022-10-05 01:00 | 55
2022-10-05 02:00 | 56
2022-10-05 03:00 | 56
2022-10-05 04:00 | 56
2022-10-05 05:00 | 56
2022-10-05 06:00 | 56
2022-10-05 07:00 | 55
2022-10-05 08:00 | 55
2022-10-05 09:00 | 56
2022-10-05 10:00 | 57
2022-10-05 11:00 | 58
2022-10-05 12:00 | 58
2022-10-05 13:00 | 59
2022-10-05 14:00 | 59
2022-10-05 15:00 | 59
2022-10-05 16:00 | 58
2022-10-05 17:00 | 56
2022-10-05 18:00 | 56
2022-10-05 19:00 | 56
2022-10-05 20:00 | 57
2022-10-05 21:00 | 57
2022-10-05 22:00 | 56
2022-10-05 23:00 | 57
2022-10-06 | 57
2022-10-06 01:00 | 56
2022-10-06 02:00 | 54
2022-10-06 03:00 | 54
2022-10-06 04:00 | 55
2022-10-06 05:00 | 55
2022-10-06 06:00 | 54
2022-10-06 07:00 | 53
2022-10-06 08:00 | 55
2022-10-06 09:00 | 58
2022-10-06 10:00 | 62
2022-10-06 11:00 | 65
2022-10-06 12:00 | 69
2022-10-06 13:00 | 71
2022-10-06 14:00 | 73
2022-10-06 15:00 | 75
2022-10-06 16:00 | 75
2022-10-06 17:00 | 76
2022-10-06 18:00 | 69
2022-10-06 19:00 | 65
2022-10-06 20:00 | 62
2022-10-06 21:00 | 62
2022-10-06 22:00 | 62
2022-10-06 23:00 | 62
2022-10-07 | 61
2022-10-07 01:00 | 60
2022-10-07 02:00 | 60
2022-10-07 03:00 | 60
2022-10-07 04:00 | 58
2022-10-07 05:00 | 57
2022-10-07 06:00 | 57
2022-10-07 07:00 | 57
2022-10-07 08:00 | 60
2022-10-07 09:00 | 63
2022-10-07 10:00 | 66
2022-10-07 11:00 | 69
2022-10-07 12:00 | 71
2022-10-07 13:00 | 73
2022-10-07 14:00 | 74
2022-10-07 15:00 | 76
2022-10-07 16:00 | 76
2022-10-07 17:00 | 71
2022-10-07 18:00 | 72
2022-10-07 19:00 | 74
2022-10-07 20:00 | 71
2022-10-07 21:00 | 68
2022-10-07 22:00 | 66
2022-10-07 23:00 | 63
2022-10-08 | 60
2022-10-08 01:00 | 59
2022-10-08 02:00 | 58
2022-10-08 03:00 | 55
2022-10-08 04:00 | 54
2022-10-08 05:00 | 48
2022-10-08 06:00 | 50
2022-10-08 07:00 | 51
2022-10-08 08:00 | 51
2022-10-08 09:00 | 53
2022-10-08 10:00 | 54
2022-10-08 11:00 | 56
2022-10-08 12:00 | 56
2022-10-08 13:00 | 58
2022-10-08 14:00 | 60
2022-10-08 15:00 | 60
2022-10-08 16:00 | 60
2022-10-08 17:00 | 59
2022-10-08 18:00 | 58
2022-10-08 19:00 | 55
2022-10-08 20:00 | 54
2022-10-08 21:00 | 52
2022-10-08 22:00 | 50
2022-10-08 23:00 | 49
2022-10-09 | 50
2022-10-09 01:00 | 49
2022-10-09 02:00 | 49
2022-10-09 03:00 | 48
2022-10-09 04:00 | 49
2022-10-09 05:00 | 47
2022-10-09 06:00 | 47
2022-10-09 07:00 | 46
2022-10-09 08:00 | 48
2022-10-09 09:00 | 51
2022-10-09 10:00 | 54
2022-10-09 11:00 | 56
2022-10-09 12:00 | 59
2022-10-09 13:00 | 60
2022-10-09 14:00 | 62
2022-10-09 15:00 | 63
2022-10-09 16:00 | 63
2022-10-09 17:00 | 63
2022-10-09 18:00 | 61
2022-10-09 19:00 | 59
2022-10-09 20:00 | 57
2022-10-09 21:00 | 57
2022-10-09 22:00 | 57
2022-10-09 23:00 | 56
2022-10-10 | 55
2022-10-10 01:00 | 53
2022-10-10 02:00 | 52
2022-10-10 03:00 | 50
2022-10-10 04:00 | 51
2022-10-10 05:00 | 49
2022-10-10 06:00 | 50
2022-10-10 07:00 | 49
2022-10-10 08:00 | 50
2022-10-10 09:00 | 55
2022-10-10 10:00 | 58
2022-10-10 11:00 | 61
2022-10-10 12:00 | 63
2022-10-10 13:00 | 65
2022-10-10 14:00 | 67
2022-10-10 15:00 | 67
2022-10-10 16:00 | 67
2022-10-10 17:00 | 67
2022-10-10 18:00 | 64
2022-10-10 19:00 | 63
2022-10-10 20:00 | 63
2022-10-10 21:00 | 61
2022-10-10 22:00 | 60
2022-10-10 23:00 | 60
2022-10-11 | 58
2022-10-11 01:00 | 58
2022-10-11 02:00 | 56
2022-10-11 03:00 | 55
2022-10-11 04:00 | 53
2022-10-11 05:00 | 53
2022-10-11 06:00 | 52
2022-10-11 07:00 | 53
2022-10-11 08:00 | 54
2022-10-11 09:00 | 58
2022-10-11 10:00 | 61
2022-10-11 11:00 | 64
2022-10-11 12:00 | 68
2022-10-11 13:00 | 68
2022-10-11 14:00 | 68
2022-10-11 15:00 | 69
2022-10-11 16:00 | 71
2022-10-11 17:00 | 66
2022-10-11 18:00 | 63
2022-10-11 19:00 | 62
2022-10-11 20:00 | 62
2022-10-11 21:00 | 62
2022-10-11 22:00 | 61
2022-10-11 23:00 | 60
2022-10-12 | 57
2022-10-12 01:00 | 58
2022-10-12 02:00 | 59
2022-10-12 03:00 | 55
2022-10-12 04:00 | 53
2022-10-12 05:00 | 53
2022-10-12 06:00 | 54
2022-10-12 07:00 | 53
2022-10-12 08:00 | 54
2022-10-12 09:00 | 59
2022-10-12 10:00 | 63
2022-10-12 11:00 | 65
2022-10-12 12:00 | 65
2022-10-12 13:00 | 67
2022-10-12 14:00 | 68
2022-10-12 15:00 | 67
2022-10-12 16:00 | 66
2022-10-12 17:00 | 64
2022-10-12 18:00 | 63
2022-10-12 19:00 | 63
2022-10-12 20:00 | 63
2022-10-12 21:00 | 63
2022-10-12 22:00 | 62
2022-10-12 23:00 | 61
2022-10-13 | 62
2022-10-13 01:00 | 62
2022-10-13 02:00 | 62
2022-10-13 03:00 | 62
2022-10-13 04:00 | 62
2022-10-13 05:00 | 62
2022-10-13 06:00 | 63
2022-10-13 07:00 | 63
2022-10-13 08:00 | 63
2022-10-13 09:00 | 64
2022-10-13 10:00 | 66
2022-10-13 11:00 | 67
2022-10-13 12:00 | 67
2022-10-13 13:00 | 66
2022-10-13 14:00 | 65
2022-10-13 15:00 | 66
2022-10-13 16:00 | 67
2022-10-13 17:00 | 67
2022-10-13 18:00 | 67
2022-10-13 19:00 | 66
2022-10-13 20:00 | 66
2022-10-13 21:00 | 65
2022-10-13 22:00 | 65
2022-10-13 23:00 | 65
2022-10-14 | 56
2022-10-14 01:00 | 55
2022-10-14 02:00 | 54
2022-10-14 03:00 | 53
2022-10-14 04:00 | 53
2022-10-14 05:00 | 54
2022-10-14 06:00 | 54
2022-10-14 07:00 | 54
2022-10-14 08:00 | 55
2022-10-14 09:00 | 57
2022-10-14 10:00 | 59
2022-10-14 11:00 | 61
2022-10-14 12:00 | 63
2022-10-14 13:00 | 64
2022-10-14 14:00 | 66
2022-10-14 15:00 | 68
2022-10-14 16:00 | 69
2022-10-14 17:00 | 68
2022-10-14 18:00 | 66
2022-10-14 19:00 | 63
2022-10-14 20:00 | 61
2022-10-14 21:00 | 58
2022-10-14 22:00 | 55
2022-10-14 23:00 | 56
2022-10-15 | 55
2022-10-15 01:00 | 52
2022-10-15 02:00 | 53
2022-10-15 03:00 | 50
2022-10-15 04:00 | 49
2022-10-15 05:00 | 52
2022-10-15 06:00 | 52
2022-10-15 07:00 | 50
2022-10-15 08:00 | 50
2022-10-15 09:00 | 56
2022-10-15 10:00 | 61
2022-10-15 11:00 | 63
2022-10-15 12:00 | 65
2022-10-15 13:00 | 66
2022-10-15 14:00 | 66
2022-10-15 15:00 | 67
2022-10-15 16:00 | 67
2022-10-15 17:00 | 65
2022-10-15 18:00 | 64
2022-10-15 19:00 | 63
2022-10-15 20:00 | 62
2022-10-15 21:00 | 62
2022-10-15 22:00 | 60
2022-10-15 23:00 | 59
2022-10-16 | 58
2022-10-16 01:00 | 58
2022-10-16 02:00 | 58
2022-10-16 03:00 | 56
2022-10-16 04:00 | 55
2022-10-16 05:00 | 55
2022-10-16 06:00 | 54
2022-10-16 07:00 | 53
2022-10-16 08:00 | 54
2022-10-16 09:00 | 56
2022-10-16 10:00 | 58
2022-10-16 11:00 | 60
2022-10-16 12:00 | 63
2022-10-16 13:00 | 65
2022-10-16 14:00 | 64
2022-10-16 15:00 | 65
2022-10-16 16:00 | 66
2022-10-16 17:00 | 64
2022-10-16 18:00 | 60
2022-10-16 19:00 | 58
2022-10-16 20:00 | 60
2022-10-16 21:00 | 60
2022-10-16 22:00 | 60
2022-10-16 23:00 | 58
2022-10-17 | 57
2022-10-17 01:00 | 56
2022-10-17 02:00 | 57
2022-10-17 03:00 | 56
2022-10-17 04:00 | 56
2022-10-17 05:00 | 60
2022-10-17 06:00 | 58
2022-10-17 07:00 | 59
2022-10-17 08:00 | 60
2022-10-17 09:00 | 59
2022-10-17 10:00 | 61
2022-10-17 11:00 | 62
2022-10-17 12:00 | 63
2022-10-17 13:00 | 65
2022-10-17 14:00 | 64
2022-10-17 15:00 | 66
2022-10-17 16:00 | 66
2022-10-17 17:00 | 64
2022-10-17 18:00 | 63
2022-10-17 19:00 | 63
2022-10-17 20:00 | 61
2022-10-17 21:00 | 57
2022-10-17 22:00 | 57
2022-10-17 23:00 | 57
2022-10-18 | 56.6
2022-10-18 01:00 | 56
2022-10-18 02:00 | 55
2022-10-18 03:00 | 54
2022-10-18 04:00 | 53
2022-10-18 05:00 | 53
2022-10-18 06:00 | 52
2022-10-18 07:00 | 50
2022-10-18 08:00 | 49
2022-10-18 09:00 | 51
2022-10-18 10:00 | 52
2022-10-18 11:00 | 52
2022-10-18 12:00 | 53
2022-10-18 13:00 | 54
2022-10-18 14:00 | 56
2022-10-18 15:00 | 56
2022-10-18 16:00 | 57
2022-10-18 17:00 | 57
2022-10-18 18:00 | 55
2022-10-18 19:00 | 54
2022-10-18 20:00 | 53
2022-10-18 21:00 | 52
2022-10-18 22:00 | 50
2022-10-18 23:00 | 49
2022-10-19 | 48
2022-10-19 01:00 | 48
2022-10-19 02:00 | 48
2022-10-19 03:00 | 47
2022-10-19 04:00 | 45
2022-10-19 05:00 | 45
2022-10-19 06:00 | 44
2022-10-19 07:00 | 44
2022-10-19 08:00 | 45
2022-10-19 09:00 | 47
2022-10-19 10:00 | 50
2022-10-19 11:00 | 51
2022-10-19 12:00 | 53
2022-10-19 13:00 | 54
2022-10-19 14:00 | 55
2022-10-19 15:00 | 55
2022-10-19 16:00 | 54
2022-10-19 17:00 | 54
2022-10-19 18:00 | 52
2022-10-19 19:00 | 52
2022-10-19 20:00 | 51
2022-10-19 21:00 | 51
2022-10-19 22:00 | 50
2022-10-19 23:00 | 51
2022-10-20 | 50
2022-10-20 01:00 | 49
2022-10-20 02:00 | 48
2022-10-20 03:00 | 47
2022-10-20 04:00 | 46
2022-10-20 05:00 | 46
2022-10-20 06:00 | 46
2022-10-20 07:00 | 45
2022-10-20 08:00 | 46
2022-10-20 09:00 | 50
2022-10-20 10:00 | 53
2022-10-20 11:00 | 55
2022-10-20 12:00 | 57
2022-10-20 13:00 | 58
2022-10-20 14:00 | 59
2022-10-20 15:00 | 59
2022-10-20 16:00 | 60
2022-10-20 17:00 | 59
2022-10-20 18:00 | 57
2022-10-20 19:00 | 57
2022-10-20 20:00 | 56
2022-10-20 21:00 | 56
2022-10-20 22:00 | 55
2022-10-20 23:00 | 53
2022-10-21 | 52
2022-10-21 01:00 | 52
2022-10-21 02:00 | 53
2022-10-21 03:00 | 51
2022-10-21 04:00 | 50
2022-10-21 05:00 | 49
2022-10-21 06:00 | 48
2022-10-21 07:00 | 46
2022-10-21 08:00 | 48
2022-10-21 09:00 | 52
2022-10-21 10:00 | 56
2022-10-21 11:00 | 59
2022-10-21 12:00 | 61
2022-10-21 13:00 | 63
2022-10-21 14:00 | 63
2022-10-21 15:00 | 63
2022-10-21 16:00 | 62
2022-10-21 17:00 | 60
2022-10-21 18:00 | 57
2022-10-21 19:00 | 54
2022-10-21 20:00 | 56
2022-10-21 21:00 | 57
2022-10-21 22:00 | 57
2022-10-21 23:00 | 55
2022-10-22 | 53
2022-10-22 01:00 | 53
2022-10-22 02:00 | 52
2022-10-22 03:00 | 50
2022-10-22 04:00 | 47
2022-10-22 05:00 | 45
2022-10-22 06:00 | 44
2022-10-22 07:00 | 46
2022-10-22 08:00 | 46
2022-10-22 09:00 | 53
2022-10-22 10:00 | 58
2022-10-22 11:00 | 62
2022-10-22 12:00 | 62
2022-10-22 13:00 | 64
2022-10-22 14:00 | 63
2022-10-22 15:00 | 64
2022-10-22 16:00 | 63
2022-10-22 17:00 | 62
2022-10-22 18:00 | 59
2022-10-22 19:00 | 56
2022-10-22 20:00 | 56
2022-10-22 21:00 | 53
2022-10-22 22:00 | 53
2022-10-22 23:00 | 53
2022-10-23 | 53
2022-10-23 01:00 | 55
2022-10-23 02:00 | 56
2022-10-23 03:00 | 56
2022-10-23 04:00 | 56
2022-10-23 05:00 | 57
2022-10-23 06:00 | 57
2022-10-23 07:00 | 57
2022-10-23 08:00 | 58
2022-10-23 09:00 | 58
2022-10-23 10:00 | 60
2022-10-23 11:00 | 61
2022-10-23 12:00 | 60
2022-10-23 13:00 | 58
2022-10-23 14:00 | 59
2022-10-23 15:00 | 61
2022-10-23 16:00 | 59
2022-10-23 17:00 | 58
2022-10-23 18:00 | 57
2022-10-23 19:00 | 56
2022-10-23 20:00 | 56
2022-10-23 21:00 | 56
2022-10-23 22:00 | 56
2022-10-23 23:00 | 57
2022-10-24 | 57
2022-10-24 01:00 | 56
2022-10-24 02:00 | 56
2022-10-24 03:00 | 55
2022-10-24 04:00 | 55
2022-10-24 05:00 | 55
2022-10-24 06:00 | 55
2022-10-24 07:00 | 55
2022-10-24 08:00 | 56
2022-10-24 09:00 | 56
2022-10-24 10:00 | 57
2022-10-24 11:00 | 58
2022-10-24 12:00 | 59
2022-10-24 13:00 | 61
2022-10-24 14:00 | 63
2022-10-24 15:00 | 63
2022-10-24 16:00 | 63
2022-10-24 17:00 | 63
2022-10-24 18:00 | 62
2022-10-24 19:00 | 61
2022-10-24 20:00 | 62
2022-10-24 21:00 | 62
2022-10-24 22:00 | 62
2022-10-24 23:00 | 62
2022-10-25 | 62
2022-10-25 01:00 | 62
2022-10-25 02:00 | 62
2022-10-25 03:00 | 64
2022-10-25 04:00 | 64
2022-10-25 05:00 | 64
2022-10-25 06:00 | 64
2022-10-25 07:00 | 64
2022-10-25 08:00 | 65
2022-10-25 09:00 | 65
2022-10-25 10:00 | 65
2022-10-25 11:00 | 66
2022-10-25 12:00 | 68
2022-10-25 13:00 | 73
2022-10-25 14:00 | 71
2022-10-25 15:00 | 70
2022-10-25 16:00 | 70
2022-10-25 17:00 | 67
2022-10-25 18:00 | 65
2022-10-25 19:00 | 64
2022-10-25 20:00 | 64
2022-10-25 21:00 | 63
2022-10-25 22:00 | 63
2022-10-25 23:00 | 63
2022-10-26 | 63
2022-10-26 01:00 | 64
2022-10-26 02:00 | 64
2022-10-26 03:00 | 65
2022-10-26 04:00 | 65
2022-10-26 05:00 | 65
2022-10-26 06:00 | 64
2022-10-26 07:00 | 64
2022-10-26 08:00 | 64
2022-10-26 09:00 | 65
2022-10-26 10:00 | 66
2022-10-26 11:00 | 68
2022-10-26 12:00 | 67
2022-10-26 13:00 | 69
2022-10-26 14:00 | 70
2022-10-26 15:00 | 69
2022-10-26 16:00 | 70
2022-10-26 17:00 | 64
2022-10-26 18:00 | 64
2022-10-26 19:00 | 62
2022-10-26 20:00 | 63
2022-10-26 21:00 | 66
2022-10-26 22:00 | 65
2022-10-26 23:00 | 64
2022-10-27 | 63
2022-10-27 01:00 | 60
2022-10-27 02:00 | 59
2022-10-27 03:00 | 57
2022-10-27 04:00 | 60
2022-10-27 05:00 | 60
2022-10-27 06:00 | 59
2022-10-27 07:00 | 58
2022-10-27 08:00 | 59
2022-10-27 09:00 | 60
2022-10-27 10:00 | 61
2022-10-27 11:00 | 62
2022-10-27 12:00 | 64
2022-10-27 13:00 | 65
2022-10-27 14:00 | 67
2022-10-27 15:00 | 67
2022-10-27 16:00 | 66
2022-10-27 17:00 | 65
2022-10-27 18:00 | 63
2022-10-27 19:00 | 61
2022-10-27 20:00 | 59
2022-10-27 21:00 | 56
2022-10-27 22:00 | 55
2022-10-27 23:00 | 53
2022-10-28 | 52
2022-10-28 01:00 | 51
2022-10-28 02:00 | 50
2022-10-28 03:00 | 49
2022-10-28 04:00 | 48
2022-10-28 05:00 | 48
2022-10-28 06:00 | 47
2022-10-28 07:00 | 46
2022-10-28 08:00 | 47
2022-10-28 09:00 | 49
2022-10-28 10:00 | 51
2022-10-28 11:00 | 54
2022-10-28 12:00 | 55
2022-10-28 13:00 | 56
2022-10-28 14:00 | 57
2022-10-28 15:00 | 58
2022-10-28 16:00 | 58
2022-10-28 17:00 | 55
2022-10-28 18:00 | 53
2022-10-28 19:00 | 51
2022-10-28 20:00 | 50
2022-10-28 21:00 | 50
2022-10-28 22:00 | 48
2022-10-28 23:00 | 48
2022-10-29 | 48
2022-10-29 01:00 | 47
2022-10-29 02:00 | 46
2022-10-29 03:00 | 44
2022-10-29 04:00 | 44
2022-10-29 05:00 | 43
2022-10-29 06:00 | 44
2022-10-29 07:00 | 44
2022-10-29 08:00 | 44
2022-10-29 09:00 | 49
2022-10-29 10:00 | 51
2022-10-29 11:00 | 52
2022-10-29 12:00 | 55
2022-10-29 13:00 | 57
2022-10-29 14:00 | 60
2022-10-29 15:00 | 60
2022-10-29 16:00 | 61
2022-10-29 17:00 | 59
2022-10-29 18:00 | 53
2022-10-29 19:00 | 53
2022-10-29 20:00 | 51
2022-10-29 21:00 | 51
2022-10-29 22:00 | 49
2022-10-29 23:00 | 51
2022-10-30 | 44
2022-10-30 01:00 | 43
2022-10-30 02:00 | 42
2022-10-30 03:00 | 42
2022-10-30 04:00 | 40
2022-10-30 05:00 | 42
2022-10-30 06:00 | 42
2022-10-30 07:00 | 40
2022-10-30 08:00 | 43
2022-10-30 09:00 | 48
2022-10-30 10:00 | 54
2022-10-30 11:00 | 58
2022-10-30 12:00 | 62
2022-10-30 13:00 | 60
2022-10-30 14:00 | 61
2022-10-30 15:00 | 60
2022-10-30 16:00 | 61
2022-10-30 17:00 | 59
2022-10-30 18:00 | 55
2022-10-30 19:00 | 54
2022-10-30 20:00 | 55
2022-10-30 21:00 | 52
2022-10-30 22:00 | 50
2022-10-30 23:00 | 50
2022-10-31 | 54
2022-10-31 01:00 | 57
2022-10-31 02:00 | 53
2022-10-31 03:00 | 55
2022-10-31 04:00 | 52
2022-10-31 05:00 | 53
2022-10-31 06:00 | 50
2022-10-31 07:00 | 50
2022-10-31 08:00 | 50
2022-10-31 09:00 | 56
2022-10-31 10:00 | 59
2022-10-31 11:00 | 60
2022-10-31 12:00 | 61
2022-10-31 13:00 | 62.8
2022-10-31 14:00 | 64
2022-10-31 15:00 | 63
2022-10-31 16:00 | 61
2022-10-31 17:00 | 61
2022-10-31 18:00 | 60
2022-10-31 19:00 | 61
2022-10-31 20:00 | 61
2022-10-31 21:00 | 60
2022-10-31 22:00 | 60
2022-10-31 23:00 | 60
2022-11-01 | 59
2022-11-01 01:00 | 59
2022-11-01 02:00 | 59
2022-11-01 03:00 | 59
2022-11-01 04:00 | 60
2022-11-01 05:00 | 59
2022-11-01 06:00 | 59
2022-11-01 07:00 | 60
2022-11-01 08:00 | 60
2022-11-01 09:00 | 60
2022-11-01 10:00 | 62
2022-11-01 11:00 | 62
2022-11-01 12:00 | 63
2022-11-01 13:00 | 65
2022-11-01 14:00 | 66
2022-11-01 15:00 | 70
2022-11-01 16:00 | 68
2022-11-01 17:00 | 69
2022-11-01 18:00 | 67
2022-11-01 19:00 | 65
2022-11-01 20:00 | 65
2022-11-01 21:00 | 64
2022-11-01 22:00 | 63
2022-11-01 23:00 | 63
2022-11-02 | 63
2022-11-02 01:00 | 61
2022-11-02 02:00 | 60
2022-11-02 03:00 | 60
2022-11-02 04:00 | 57
2022-11-02 05:00 | 58
2022-11-02 06:00 | 56
2022-11-02 07:00 | 56
2022-11-02 08:00 | 56
2022-11-02 09:00 | 59
2022-11-02 10:00 | 62
2022-11-02 11:00 | 65
2022-11-02 12:00 | 68
2022-11-02 13:00 | 69
2022-11-02 14:00 | 70
2022-11-02 15:00 | 71
2022-11-02 16:00 | 71
2022-11-02 17:00 | 66
2022-11-02 18:00 | 62
2022-11-02 19:00 | 61
2022-11-02 20:00 | 57
2022-11-02 21:00 | 58
2022-11-02 22:00 | 56
2022-11-02 23:00 | 53
2022-11-03 | 52
2022-11-03 01:00 | 50
2022-11-03 02:00 | 49
2022-11-03 03:00 | 48
2022-11-03 04:00 | 47
2022-11-03 05:00 | 48
2022-11-03 06:00 | 50
2022-11-03 07:00 | 48
2022-11-03 08:00 | 47
2022-11-03 09:00 | 53
2022-11-03 10:00 | 59
2022-11-03 11:00 | 64
2022-11-03 12:00 | 66
2022-11-03 13:00 | 65
2022-11-03 14:00 | 66
2022-11-03 15:00 | 65
2022-11-03 16:00 | 63
2022-11-03 17:00 | 62
2022-11-03 18:00 | 58
2022-11-03 19:00 | 56
2022-11-03 20:00 | 56
2022-11-03 21:00 | 55
2022-11-03 22:00 | 52
2022-11-03 23:00 | 52
2022-11-04 | 51
2022-11-04 01:00 | 51
2022-11-04 02:00 | 50
2022-11-04 03:00 | 49
2022-11-04 04:00 | 48
2022-11-04 05:00 | 48
2022-11-04 06:00 | 49
2022-11-04 07:00 | 50
2022-11-04 08:00 | 52
2022-11-04 09:00 | 54
2022-11-04 10:00 | 56
2022-11-04 11:00 | 58
2022-11-04 12:00 | 64
2022-11-04 13:00 | 66
2022-11-04 14:00 | 67
2022-11-04 15:00 | 67
2022-11-04 16:00 | 66
2022-11-04 17:00 | 64
2022-11-04 18:00 | 62
2022-11-04 19:00 | 62
2022-11-04 20:00 | 62
2022-11-04 21:00 | 61
2022-11-04 22:00 | 63
2022-11-04 23:00 | 62
2022-11-05 | 62
2022-11-05 01:00 | 61
2022-11-05 02:00 | 62
2022-11-05 03:00 | 62
2022-11-05 04:00 | 61
2022-11-05 05:00 | 61
2022-11-05 06:00 | 61
2022-11-05 07:00 | 62
2022-11-05 08:00 | 63
2022-11-05 09:00 | 65
2022-11-05 10:00 | 67
2022-11-05 11:00 | 68
2022-11-05 12:00 | 70
2022-11-05 13:00 | 72
2022-11-05 14:00 | 72
2022-11-05 15:00 | 71
2022-11-05 16:00 | 70
2022-11-05 17:00 | 68
2022-11-05 18:00 | 66
2022-11-05 19:00 | 66
2022-11-05 20:00 | 64
2022-11-05 21:00 | 65
2022-11-05 22:00 | 65
2022-11-05 23:00 | 65
2022-11-06 | 64
2022-11-06 01:00 | 64
2022-11-06 01:00 | 64
2022-11-06 02:00 | 64
2022-11-06 03:00 | 64
2022-11-06 04:00 | 64
2022-11-06 05:00 | 64
2022-11-06 06:00 | 64
2022-11-06 07:00 | 64
2022-11-06 08:00 | 65
2022-11-06 09:00 | 67
2022-11-06 10:00 | 70
2022-11-06 11:00 | 69
2022-11-06 12:00 | 69
2022-11-06 13:00 | 69
2022-11-06 14:00 | 68
2022-11-06 15:00 | 68
2022-11-06 16:00 | 67
2022-11-06 17:00 | 67
2022-11-06 18:00 | 65
2022-11-06 19:00 | 65
2022-11-06 20:00 | 66
2022-11-06 21:00 | 65
2022-11-06 22:00 | 65
2022-11-06 23:00 | 65
2022-11-07 | 66
2022-11-07 01:00 | 65
2022-11-07 02:00 | 65
2022-11-07 03:00 | 65
2022-11-07 04:00 | 65
2022-11-07 05:00 | 65
2022-11-07 06:00 | 63
2022-11-07 07:00 | 64
2022-11-07 08:00 | 69
2022-11-07 09:00 | 70
2022-11-07 10:00 | 72
2022-11-07 11:00 | 77
2022-11-07 12:00 | 79
2022-11-07 13:00 | 79
2022-11-07 14:00 | 79
2022-11-07 15:00 | 77
2022-11-07 16:00 | 76
2022-11-07 17:00 | 74
2022-11-07 18:00 | 72
2022-11-07 19:00 | 70
2022-11-07 20:00 | 69
2022-11-07 21:00 | 65
2022-11-07 22:00 | 63
2022-11-07 23:00 | 59
2022-11-08 | 56
2022-11-08 01:00 | 53
2022-11-08 02:00 | 52
2022-11-08 03:00 | 51
2022-11-08 04:00 | 50
2022-11-08 05:00 | 49
2022-11-08 06:00 | 48
2022-11-08 07:00 | 48
2022-11-08 08:00 | 49
2022-11-08 09:00 | 51
2022-11-08 10:00 | 54
2022-11-08 11:00 | 55
2022-11-08 12:00 | 56
2022-11-08 13:00 | 58
2022-11-08 14:00 | 58
2022-11-08 15:00 | 59
2022-11-08 16:00 | 58
2022-11-08 17:00 | 55
2022-11-08 18:00 | 53
2022-11-08 19:00 | 52
2022-11-08 20:00 | 51
2022-11-08 21:00 | 50
2022-11-08 22:00 | 49
2022-11-08 23:00 | 47
2022-11-09 | 47
2022-11-09 01:00 | 45
2022-11-09 02:00 | 45
2022-11-09 03:00 | 43
2022-11-09 04:00 | 42
2022-11-09 05:00 | 41
2022-11-09 06:00 | 40
2022-11-09 07:00 | 39
2022-11-09 08:00 | 44
2022-11-09 09:00 | 46
2022-11-09 10:00 | 49
2022-11-09 11:00 | 50
2022-11-09 12:00 | 51
2022-11-09 13:00 | 52
2022-11-09 14:00 | 53
2022-11-09 15:00 | 51
2022-11-09 16:00 | 50
2022-11-09 17:00 | 47
2022-11-09 18:00 | 48
2022-11-09 19:00 | 48
2022-11-09 20:00 | 45
2022-11-09 21:00 | 48
2022-11-09 22:00 | 49
2022-11-09 23:00 | 49
2022-11-10 | 47
2022-11-10 01:00 | 46
2022-11-10 02:00 | 44
2022-11-10 03:00 | 46
2022-11-10 04:00 | 47
2022-11-10 05:00 | 46
2022-11-10 06:00 | 48
2022-11-10 07:00 | 47
2022-11-10 08:00 | 52
2022-11-10 09:00 | 55
2022-11-10 10:00 | 58
2022-11-10 11:00 | 60
2022-11-10 12:00 | 62
2022-11-10 13:00 | 63
2022-11-10 14:00 | 62
2022-11-10 15:00 | 61
2022-11-10 16:00 | 61
2022-11-10 17:00 | 59
2022-11-10 18:00 | 58
2022-11-10 19:00 | 59
2022-11-10 20:00 | 58
2022-11-10 21:00 | 58
2022-11-10 22:00 | 59
2022-11-10 23:00 | 58
2022-11-11 | 59
2022-11-11 01:00 | 59
2022-11-11 02:00 | 58
2022-11-11 03:00 | 58
2022-11-11 04:00 | 58
2022-11-11 05:00 | 58
2022-11-11 06:00 | 59
2022-11-11 07:00 | 60
2022-11-11 08:00 | 63
2022-11-11 09:00 | 65
2022-11-11 10:00 | 67
2022-11-11 11:00 | 68
2022-11-11 12:00 | 67
2022-11-11 13:00 | 65
2022-11-11 14:00 | 65
2022-11-11 15:00 | 66
2022-11-11 16:00 | 66
2022-11-11 17:00 | 67
2022-11-11 18:00 | 67
2022-11-11 19:00 | 66
2022-11-11 20:00 | 66
2022-11-11 21:00 | 67
2022-11-11 22:00 | 67
2022-11-11 23:00 | 66
2022-11-12 | 66
2022-11-12 01:00 | 66
2022-11-12 02:00 | 66
2022-11-12 03:00 | 66
2022-11-12 04:00 | 66
2022-11-12 05:00 | 66
2022-11-12 06:00 | 65
2022-11-12 07:00 | 65
2022-11-12 08:00 | 68
2022-11-12 09:00 | 70
2022-11-12 10:00 | 71
2022-11-12 11:00 | 70
2022-11-12 12:00 | 69
2022-11-12 13:00 | 70
2022-11-12 14:00 | 71
2022-11-12 15:00 | 69
2022-11-12 16:00 | 68
2022-11-12 17:00 | 64
2022-11-12 18:00 | 65
2022-11-12 19:00 | 66
2022-11-12 20:00 | 65
2022-11-12 21:00 | 62
2022-11-12 22:00 | 62
2022-11-12 23:00 | 61
2022-11-13 | 60
2022-11-13 01:00 | 61
2022-11-13 02:00 | 61
2022-11-13 03:00 | 60
2022-11-13 04:00 | 57
2022-11-13 05:00 | 55
2022-11-13 06:00 | 53
2022-11-13 07:00 | 52
2022-11-13 08:00 | 50
2022-11-13 09:00 | 50
2022-11-13 10:00 | 49
2022-11-13 11:00 | 49
2022-11-13 12:00 | 52
2022-11-13 13:00 | 53
2022-11-13 14:00 | 54
2022-11-13 15:00 | 52
2022-11-13 16:00 | 51
2022-11-13 17:00 | 51
2022-11-13 18:00 | 49
2022-11-13 19:00 | 48
2022-11-13 20:00 | 47
2022-11-13 21:00 | 45
2022-11-13 22:00 | 45
2022-11-13 23:00 | 44
2022-11-14 | 42
2022-11-14 01:00 | 42
2022-11-14 02:00 | 40
2022-11-14 03:00 | 40
2022-11-14 04:00 | 40
2022-11-14 05:00 | 40
2022-11-14 06:00 | 40
2022-11-14 07:00 | 40
2022-11-14 08:00 | 40
2022-11-14 09:00 | 42
2022-11-14 10:00 | 43
2022-11-14 11:00 | 44
2022-11-14 12:00 | 46
2022-11-14 13:00 | 46
2022-11-14 14:00 | 47
2022-11-14 15:00 | 46
2022-11-14 16:00 | 45
2022-11-14 17:00 | 44
2022-11-14 18:00 | 43
2022-11-14 19:00 | 42
2022-11-14 20:00 | 41
2022-11-14 21:00 | 39
2022-11-14 22:00 | 38
2022-11-14 23:00 | 37
2022-11-15 | 35
2022-11-15 01:00 | 35
2022-11-15 02:00 | 35
2022-11-15 03:00 | 34
2022-11-15 04:00 | 35
2022-11-15 05:00 | 37
2022-11-15 06:00 | 38
2022-11-15 07:00 | 37
2022-11-15 08:00 | 38
2022-11-15 09:00 | 40
2022-11-15 10:00 | 43
2022-11-15 11:00 | 44
2022-11-15 12:00 | 46
2022-11-15 13:00 | 46
2022-11-15 14:00 | 46
2022-11-15 15:00 | 46
2022-11-15 16:00 | 46
2022-11-15 17:00 | 46
2022-11-15 18:00 | 45
2022-11-15 19:00 | 44
2022-11-15 20:00 | 44
2022-11-15 21:00 | 43
2022-11-15 22:00 | 42
2022-11-15 23:00 | 42
2022-11-16 | 42
2022-11-16 01:00 | 43
2022-11-16 02:00 | 44
2022-11-16 03:00 | 45
2022-11-16 04:00 | 47
2022-11-16 05:00 | 48
2022-11-16 06:00 | 49
2022-11-16 07:00 | 46
2022-11-16 08:00 | 44
2022-11-16 09:00 | 43
2022-11-16 10:00 | 43
2022-11-16 11:00 | 46
2022-11-16 12:00 | 48
2022-11-16 13:00 | 50
2022-11-16 14:00 | 51
2022-11-16 15:00 | 52
2022-11-16 16:00 | 50
2022-11-16 17:00 | 47
2022-11-16 18:00 | 47
2022-11-16 19:00 | 47
2022-11-16 20:00 | 45
2022-11-16 21:00 | 44
2022-11-16 22:00 | 43
2022-11-16 23:00 | 42
2022-11-17 | 41
2022-11-17 01:00 | 40
2022-11-17 02:00 | 39
2022-11-17 03:00 | 39
2022-11-17 04:00 | 39
2022-11-17 05:00 | 39
2022-11-17 06:00 | 39
2022-11-17 07:00 | 39
2022-11-17 08:00 | 40
2022-11-17 09:00 | 40
2022-11-17 10:00 | 43
2022-11-17 11:00 | 45
2022-11-17 12:00 | 46
2022-11-17 13:00 | 47
2022-11-17 14:00 | 47
2022-11-17 15:00 | 46
2022-11-17 16:00 | 44
2022-11-17 17:00 | 42
2022-11-17 18:00 | 42
2022-11-17 19:00 | 42
2022-11-17 20:00 | 41
2022-11-17 21:00 | 40
2022-11-17 22:00 | 39
2022-11-17 23:00 | 39
2022-11-18 | 38
2022-11-18 01:00 | 38
2022-11-18 02:00 | 37
2022-11-18 03:00 | 37
2022-11-18 04:00 | 36
2022-11-18 05:00 | 35
2022-11-18 06:00 | 35
2022-11-18 07:00 | 35
2022-11-18 08:00 | 37
2022-11-18 09:00 | 39
2022-11-18 10:00 | 41
2022-11-18 11:00 | 42
2022-11-18 12:00 | 43
2022-11-18 13:00 | 44
2022-11-18 14:00 | 45
2022-11-18 15:00 | 44
2022-11-18 16:00 | 43
2022-11-18 17:00 | 42
2022-11-18 18:00 | 42
2022-11-18 19:00 | 43
2022-11-18 20:00 | 40
2022-11-18 21:00 | 37
2022-11-18 22:00 | 38
2022-11-18 23:00 | 37
2022-11-19 | 36
2022-11-19 01:00 | 35
2022-11-19 02:00 | 35
2022-11-19 03:00 | 34
2022-11-19 04:00 | 33
2022-11-19 05:00 | 33
2022-11-19 06:00 | 32
2022-11-19 07:00 | 32
2022-11-19 08:00 | 33
2022-11-19 09:00 | 35
2022-11-19 10:00 | 37
2022-11-19 11:00 | 37
2022-11-19 12:00 | 39
2022-11-19 13:00 | 39
2022-11-19 14:00 | 40
2022-11-19 15:00 | 40
2022-11-19 16:00 | 39
2022-11-19 17:00 | 38
2022-11-19 18:00 | 37
2022-11-19 19:00 | 40
2022-11-19 20:00 | 39
2022-11-19 21:00 | 39
2022-11-19 22:00 | 38
2022-11-19 23:00 | 39
2022-11-20 | 40
2022-11-20 01:00 | 43
2022-11-20 02:00 | 39
2022-11-20 03:00 | 37
2022-11-20 04:00 | 36
2022-11-20 05:00 | 36
2022-11-20 06:00 | 36
2022-11-20 07:00 | 36
2022-11-20 08:00 | 36
2022-11-20 09:00 | 36
2022-11-20 10:00 | 36
2022-11-20 11:00 | 37
2022-11-20 12:00 | 38
2022-11-20 13:00 | 37
2022-11-20 14:00 | 37
2022-11-20 15:00 | 37
2022-11-20 16:00 | 36
2022-11-20 17:00 | 34
2022-11-20 18:00 | 34
2022-11-20 19:00 | 33
2022-11-20 20:00 | 32
2022-11-20 21:00 | 32
2022-11-20 22:00 | 32
2022-11-20 23:00 | 31
2022-11-21 | 30
2022-11-21 01:00 | 30
2022-11-21 02:00 | 29
2022-11-21 03:00 | 29
2022-11-21 04:00 | 29
2022-11-21 05:00 | 29
2022-11-21 06:00 | 28
2022-11-21 07:00 | 29
2022-11-21 08:00 | 31
2022-11-21 09:00 | 33
2022-11-21 10:00 | 35
2022-11-21 11:00 | 36
2022-11-21 12:00 | 37
2022-11-21 13:00 | 38
2022-11-21 14:00 | 40
2022-11-21 15:00 | 42
2022-11-21 16:00 | 42
2022-11-21 17:00 | 41
2022-11-21 18:00 | 41
2022-11-21 19:00 | 40
2022-11-21 20:00 | 40
2022-11-21 21:00 | 40
2022-11-21 22:00 | 42
2022-11-21 23:00 | 41
2022-11-22 | 40
2022-11-22 01:00 | 40
2022-11-22 02:00 | 39
2022-11-22 03:00 | 39
2022-11-22 04:00 | 39
2022-11-22 05:00 | 39
2022-11-22 06:00 | 37
2022-11-22 07:00 | 37
2022-11-22 08:00 | 40
2022-11-22 09:00 | 44
2022-11-22 10:00 | 47
2022-11-22 11:00 | 48
2022-11-22 12:00 | 48
2022-11-22 13:00 | 49
2022-11-22 14:00 | 49
2022-11-22 15:00 | 50
2022-11-22 16:00 | 47
2022-11-22 17:00 | 45
2022-11-22 18:00 | 43
2022-11-22 19:00 | 46
2022-11-22 20:00 | 41
2022-11-22 21:00 | 45
2022-11-22 22:00 | 44
2022-11-22 23:00 | 44
2022-11-23 | 40
2022-11-23 01:00 | 41
2022-11-23 02:00 | 40
2022-11-23 03:00 | 36
2022-11-23 04:00 | 37
2022-11-23 05:00 | 35
2022-11-23 06:00 | 38
2022-11-23 07:00 | 36
2022-11-23 08:00 | 42
2022-11-23 09:00 | 47
2022-11-23 10:00 | 51
2022-11-23 11:00 | 54
2022-11-23 12:00 | 55
2022-11-23 13:00 | 56
2022-11-23 14:00 | 56
2022-11-23 15:00 | 56
2022-11-23 16:00 | 54
2022-11-23 17:00 | 51
2022-11-23 18:00 | 49
2022-11-23 19:00 | 47
2022-11-23 20:00 | 48
2022-11-23 21:00 | 47
2022-11-23 22:00 | 42
2022-11-23 23:00 | 40
2022-11-24 | 41
2022-11-24 01:00 | 39
2022-11-24 02:00 | 37
2022-11-24 03:00 | 36
2022-11-24 04:00 | 35
2022-11-24 05:00 | 38
2022-11-24 06:00 | 35
2022-11-24 07:00 | 35
2022-11-24 08:00 | 38
2022-11-24 09:00 | 44
2022-11-24 10:00 | 48
2022-11-24 11:00 | 50
2022-11-24 12:00 | 52
2022-11-24 13:00 | 52
2022-11-24 14:00 | 52
2022-11-24 15:00 | 52
2022-11-24 16:00 | 50
2022-11-24 17:00 | 47
2022-11-24 18:00 | 45
2022-11-24 19:00 | 49
2022-11-24 20:00 | 49
2022-11-24 21:00 | 49
2022-11-24 22:00 | 47
2022-11-24 23:00 | 47
2022-11-25 | 45
2022-11-25 01:00 | 46
2022-11-25 02:00 | 47
2022-11-25 03:00 | 47
2022-11-25 04:00 | 48
2022-11-25 05:00 | 49
2022-11-25 06:00 | 49
2022-11-25 07:00 | 50
2022-11-25 08:00 | 50
2022-11-25 09:00 | 50
2022-11-25 10:00 | 51
2022-11-25 11:00 | 50
2022-11-25 12:00 | 50
2022-11-25 13:00 | 50
2022-11-25 14:00 | 53
2022-11-25 15:00 | 53
2022-11-25 16:00 | 54
2022-11-25 17:00 | 53
2022-11-25 18:00 | 51
2022-11-25 19:00 | 49
2022-11-25 20:00 | 48
2022-11-25 21:00 | 48
2022-11-25 22:00 | 47
2022-11-25 23:00 | 47
2022-11-26 | 46
2022-11-26 01:00 | 45
2022-11-26 02:00 | 45
2022-11-26 03:00 | 45
2022-11-26 04:00 | 45
2022-11-26 05:00 | 45
2022-11-26 06:00 | 44
2022-11-26 07:00 | 43
2022-11-26 08:00 | 45
2022-11-26 09:00 | 46
2022-11-26 10:00 | 48
2022-11-26 11:00 | 50
2022-11-26 12:00 | 52
2022-11-26 13:00 | 55
2022-11-26 14:00 | 56
2022-11-26 15:00 | 57
2022-11-26 16:00 | 56
2022-11-26 17:00 | 48
2022-11-26 18:00 | 52
2022-11-26 19:00 | 51
2022-11-26 20:00 | 50
2022-11-26 21:00 | 49
2022-11-26 22:00 | 49
2022-11-26 23:00 | 48
2022-11-27 | 45
2022-11-27 01:00 | 44
2022-11-27 02:00 | 44
2022-11-27 03:00 | 43
2022-11-27 04:00 | 46
2022-11-27 05:00 | 45
2022-11-27 06:00 | 46
2022-11-27 07:00 | 45
2022-11-27 08:00 | 47
2022-11-27 09:00 | 49
2022-11-27 10:00 | 50
2022-11-27 11:00 | 51
2022-11-27 12:00 | 52
2022-11-27 13:00 | 53
2022-11-27 14:00 | 52
2022-11-27 15:00 | 50
2022-11-27 16:00 | 51
2022-11-27 17:00 | 55
2022-11-27 18:00 | 56
2022-11-27 19:00 | 56
2022-11-27 20:00 | 57
2022-11-27 21:00 | 56
2022-11-27 22:00 | 59
2022-11-27 23:00 | 57
2022-11-28 | 55
2022-11-28 01:00 | 55
2022-11-28 02:00 | 50
2022-11-28 03:00 | 50
2022-11-28 04:00 | 50
2022-11-28 05:00 | 49
2022-11-28 06:00 | 51
2022-11-28 07:00 | 54
2022-11-28 08:00 | 56
2022-11-28 09:00 | 52
2022-11-28 10:00 | 51
2022-11-28 11:00 | 54
2022-11-28 12:00 | 54
2022-11-28 13:00 | 53
2022-11-28 14:00 | 54
2022-11-28 15:00 | 52
2022-11-28 16:00 | 51
2022-11-28 17:00 | 49
2022-11-28 18:00 | 48
2022-11-28 19:00 | 47
2022-11-28 20:00 | 46
2022-11-28 21:00 | 45
2022-11-28 22:00 | 44
2022-11-28 23:00 | 42
2022-11-29 | 41
2022-11-29 01:00 | 39
2022-11-29 02:00 | 39
2022-11-29 03:00 | 39
2022-11-29 04:00 | 36
2022-11-29 05:00 | 36
2022-11-29 06:00 | 37
2022-11-29 07:00 | 37
2022-11-29 08:00 | 36
2022-11-29 09:00 | 40
2022-11-29 10:00 | 41
2022-11-29 11:00 | 42
2022-11-29 12:00 | 42
2022-11-29 13:00 | 43
2022-11-29 14:00 | 43
2022-11-29 15:00 | 43
2022-11-29 16:00 | 43
2022-11-29 17:00 | 41
2022-11-29 18:00 | 37
2022-11-29 19:00 | 40
2022-11-29 20:00 | 38
2022-11-29 21:00 | 38
2022-11-29 22:00 | 38
2022-11-29 23:00 | 38
2022-11-30 | 36
2022-11-30 01:00 | 36
2022-11-30 02:00 | 38
2022-11-30 03:00 | 38
2022-11-30 04:00 | 39
2022-11-30 05:00 | 42
2022-11-30 06:00 | 49
2022-11-30 07:00 | 50
2022-11-30 08:00 | 51
2022-11-30 09:00 | 53
2022-11-30 10:00 | 54
2022-11-30 11:00 | 55
2022-11-30 12:00 | 56
2022-11-30 13:00 | 57
2022-11-30 14:00 | 58
2022-11-30 15:00 | 57
2022-11-30 16:00 | 56
2022-11-30 17:00 | 56
2022-11-30 18:00 | 56
2022-11-30 19:00 | 54
2022-11-30 20:00 | 52
2022-11-30 21:00 | 49
2022-11-30 22:00 | 47
2022-11-30 23:00 | 45
2022-12-01 | 42
2022-12-01 01:00 | 40
2022-12-01 02:00 | 39
2022-12-01 03:00 | 38
2022-12-01 04:00 | 37
2022-12-01 05:00 | 37
2022-12-01 06:00 | 37
2022-12-01 07:00 | 37
2022-12-01 08:00 | 38
2022-12-01 09:00 | 39
2022-12-01 10:00 | 39
2022-12-01 11:00 | 41
2022-12-01 12:00 | 42
2022-12-01 13:00 | 43
2022-12-01 14:00 | 43
2022-12-01 15:00 | 43
2022-12-01 16:00 | 43
2022-12-01 17:00 | 43
2022-12-01 18:00 | 41
2022-12-01 19:00 | 41
2022-12-01 20:00 | 40
2022-12-01 21:00 | 39
2022-12-01 22:00 | 37
2022-12-01 23:00 | 36
2022-12-02 | 36
2022-12-02 01:00 | 33
2022-12-02 02:00 | 33
2022-12-02 03:00 | 33
2022-12-02 04:00 | 32
2022-12-02 05:00 | 32
2022-12-02 06:00 | 32
2022-12-02 07:00 | 33
2022-12-02 08:00 | 32
2022-12-02 09:00 | 37
2022-12-02 10:00 | 38
2022-12-02 11:00 | 41
2022-12-02 12:00 | 41
2022-12-02 13:00 | 41
2022-12-02 14:00 | 42
2022-12-02 15:00 | 42
2022-12-02 16:00 | 41
2022-12-02 17:00 | 40
2022-12-02 18:00 | 40
2022-12-02 19:00 | 42
2022-12-02 20:00 | 41
2022-12-02 21:00 | 44
2022-12-02 22:00 | 45
2022-12-02 23:00 | 45
2022-12-03 | 45
2022-12-03 01:00 | 46
2022-12-03 02:00 | 48
2022-12-03 03:00 | 51
2022-12-03 04:00 | 52
2022-12-03 05:00 | 52
2022-12-03 06:00 | 53
2022-12-03 07:00 | 54
2022-12-03 08:00 | 54
2022-12-03 09:00 | 54
2022-12-03 10:00 | 54
2022-12-03 11:00 | 54
2022-12-03 12:00 | 54
2022-12-03 13:00 | 54
2022-12-03 14:00 | 54
2022-12-03 15:00 | 56
2022-12-03 16:00 | 56
2022-12-03 17:00 | 55
2022-12-03 18:00 | 56
2022-12-03 19:00 | 56
2022-12-03 20:00 | 55
2022-12-03 21:00 | 51
2022-12-03 22:00 | 48
2022-12-03 23:00 | 47
2022-12-04 | 46
2022-12-04 01:00 | 45
2022-12-04 02:00 | 44
2022-12-04 03:00 | 42
2022-12-04 04:00 | 41
2022-12-04 05:00 | 40
2022-12-04 06:00 | 40
2022-12-04 07:00 | 39
2022-12-04 08:00 | 39
2022-12-04 09:00 | 41
2022-12-04 10:00 | 42
2022-12-04 11:00 | 44
2022-12-04 12:00 | 45
2022-12-04 13:00 | 46
2022-12-04 14:00 | 46
2022-12-04 15:00 | 46
2022-12-04 16:00 | 44
2022-12-04 17:00 | 42
2022-12-04 18:00 | 41
2022-12-04 19:00 | 40
2022-12-04 20:00 | 39
2022-12-04 21:00 | 37
2022-12-04 22:00 | 38
2022-12-04 23:00 | 40
2022-12-05 | 37
2022-12-05 01:00 | 36
2022-12-05 02:00 | 33
2022-12-05 03:00 | 31
2022-12-05 04:00 | 30
2022-12-05 05:00 | 30
2022-12-05 06:00 | 30
2022-12-05 07:00 | 34
2022-12-05 08:00 | 37
2022-12-05 09:00 | 40
2022-12-05 10:00 | 42
2022-12-05 11:00 | 44
2022-12-05 12:00 | 45
2022-12-05 13:00 | 46
2022-12-05 14:00 | 45
2022-12-05 15:00 | 47
2022-12-05 16:00 | 45
2022-12-05 17:00 | 43
2022-12-05 18:00 | 41
2022-12-05 19:00 | 40
2022-12-05 20:00 | 39
2022-12-05 21:00 | 37
2022-12-05 22:00 | 38
2022-12-05 23:00 | 38
2022-12-06 | 38
2022-12-06 01:00 | 37
2022-12-06 02:00 | 38
2022-12-06 03:00 | 39
2022-12-06 04:00 | 41
2022-12-06 05:00 | 41
2022-12-06 06:00 | 44
2022-12-06 07:00 | 45
2022-12-06 08:00 | 50
2022-12-06 09:00 | 55
2022-12-06 10:00 | 57
2022-12-06 11:00 | 56
2022-12-06 12:00 | 56
2022-12-06 13:00 | 57
2022-12-06 14:00 | 56
2022-12-06 15:00 | 56
2022-12-06 16:00 | 56
2022-12-06 17:00 | 56
2022-12-06 18:00 | 56
2022-12-06 19:00 | 56
2022-12-06 20:00 | 56
2022-12-06 21:00 | 56
2022-12-06 22:00 | 56
2022-12-06 23:00 | 56
2022-12-07 | 56
2022-12-07 01:00 | 56
2022-12-07 02:00 | 56
2022-12-07 03:00 | 55
2022-12-07 04:00 | 56
2022-12-07 05:00 | 55
2022-12-07 06:00 | 54
2022-12-07 07:00 | 54
2022-12-07 08:00 | 54
2022-12-07 09:00 | 54
2022-12-07 10:00 | 54
2022-12-07 11:00 | 54
2022-12-07 12:00 | 54
2022-12-07 13:00 | 55
2022-12-07 14:00 | 54
2022-12-07 15:00 | 55
2022-12-07 16:00 | 57
2022-12-07 17:00 | 55
2022-12-07 18:00 | 54
2022-12-07 19:00 | 55
2022-12-07 20:00 | 54
2022-12-07 21:00 | 56
2022-12-07 22:00 | 55
2022-12-07 23:00 | 55
2022-12-08 | 55
2022-12-08 01:00 | 55
2022-12-08 02:00 | 54
2022-12-08 03:00 | 52
2022-12-08 04:00 | 51
2022-12-08 05:00 | 50
2022-12-08 06:00 | 49
2022-12-08 07:00 | 49
2022-12-08 08:00 | 50
2022-12-08 09:00 | 50
2022-12-08 10:00 | 51
2022-12-08 11:00 | 51
2022-12-08 12:00 | 53
2022-12-08 13:00 | 54
2022-12-08 14:00 | 54
2022-12-08 15:00 | 55
2022-12-08 16:00 | 52
2022-12-08 17:00 | 50
2022-12-08 18:00 | 50
2022-12-08 19:00 | 49
2022-12-08 20:00 | 48
2022-12-08 21:00 | 47
2022-12-08 22:00 | 46
2022-12-08 23:00 | 45
2022-12-09 | 42
2022-12-09 01:00 | 41
2022-12-09 02:00 | 39
2022-12-09 03:00 | 38
2022-12-09 04:00 | 37
2022-12-09 05:00 | 36
2022-12-09 06:00 | 36
2022-12-09 07:00 | 35
2022-12-09 08:00 | 37
2022-12-09 09:00 | 38
2022-12-09 10:00 | 40
2022-12-09 11:00 | 42
2022-12-09 12:00 | 44
2022-12-09 13:00 | 46
2022-12-09 14:00 | 46
2022-12-09 15:00 | 46
2022-12-09 16:00 | 45
2022-12-09 17:00 | 43
2022-12-09 18:00 | 41
2022-12-09 19:00 | 40
2022-12-09 20:00 | 38
2022-12-09 21:00 | 37
2022-12-09 22:00 | 36
2022-12-09 23:00 | 36
2022-12-10 | 35
2022-12-10 01:00 | 34
2022-12-10 02:00 | 34
2022-12-10 03:00 | 33
2022-12-10 04:00 | 32
2022-12-10 05:00 | 32
2022-12-10 06:00 | 32
2022-12-10 07:00 | 32
2022-12-10 08:00 | 33
2022-12-10 09:00 | 36
2022-12-10 10:00 | 38
2022-12-10 11:00 | 38
2022-12-10 12:00 | 38
2022-12-10 13:00 | 39
2022-12-10 14:00 | 39
2022-12-10 15:00 | 39
2022-12-10 16:00 | 38
2022-12-10 17:00 | 38
2022-12-10 18:00 | 37
2022-12-10 19:00 | 35
2022-12-10 20:00 | 36
2022-12-10 21:00 | 38
2022-12-10 22:00 | 38
2022-12-10 23:00 | 37
2022-12-11 | 37
2022-12-11 01:00 | 37
2022-12-11 02:00 | 37
2022-12-11 03:00 | 36
2022-12-11 04:00 | 36
2022-12-11 05:00 | 37
2022-12-11 06:00 | 37
2022-12-11 07:00 | 37
2022-12-11 08:00 | 38
2022-12-11 09:00 | 38
2022-12-11 10:00 | 39
2022-12-11 11:00 | 40
2022-12-11 12:00 | 41
2022-12-11 13:00 | 41
2022-12-11 14:00 | 41
2022-12-11 15:00 | 40
2022-12-11 16:00 | 40
2022-12-11 17:00 | 39
2022-12-11 18:00 | 39
2022-12-11 19:00 | 39
2022-12-11 20:00 | 39
2022-12-11 21:00 | 38
2022-12-11 22:00 | 36
2022-12-11 23:00 | 34
2022-12-12 | 33
2022-12-12 01:00 | 33
2022-12-12 02:00 | 32
2022-12-12 03:00 | 33
2022-12-12 04:00 | 33
2022-12-12 05:00 | 33
2022-12-12 06:00 | 33
2022-12-12 07:00 | 33
2022-12-12 08:00 | 33
2022-12-12 09:00 | 33
2022-12-12 10:00 | 36
2022-12-12 11:00 | 37
2022-12-12 12:00 | 39
2022-12-12 13:00 | 39
2022-12-12 14:00 | 40
2022-12-12 15:00 | 38
2022-12-12 16:00 | 37
2022-12-12 17:00 | 35
2022-12-12 18:00 | 34
2022-12-12 19:00 | 32
2022-12-12 20:00 | 32
2022-12-12 21:00 | 32
2022-12-12 22:00 | 31
2022-12-12 23:00 | 31
2022-12-13 | 30
2022-12-13 01:00 | 29
2022-12-13 02:00 | 28
2022-12-13 03:00 | 28
2022-12-13 04:00 | 28
2022-12-13 05:00 | 27
2022-12-13 06:00 | 27
2022-12-13 07:00 | 27
2022-12-13 08:00 | 28
2022-12-13 09:00 | 30
2022-12-13 10:00 | 32
2022-12-13 11:00 | 35
2022-12-13 12:00 | 38
2022-12-13 13:00 | 40
2022-12-13 14:00 | 40
2022-12-13 15:00 | 41
2022-12-13 16:00 | 39
2022-12-13 17:00 | 36
2022-12-13 18:00 | 36
2022-12-13 19:00 | 37
2022-12-13 20:00 | 36
2022-12-13 21:00 | 35
2022-12-13 22:00 | 34
2022-12-13 23:00 | 32
2022-12-14 | 32
2022-12-14 01:00 | 32
2022-12-14 02:00 | 32
2022-12-14 03:00 | 31
2022-12-14 04:00 | 32
2022-12-14 05:00 | 32
2022-12-14 06:00 | 32
2022-12-14 07:00 | 31
2022-12-14 08:00 | 31
2022-12-14 09:00 | 32
2022-12-14 10:00 | 34
2022-12-14 11:00 | 35
2022-12-14 12:00 | 36
2022-12-14 13:00 | 38
2022-12-14 14:00 | 39
2022-12-14 15:00 | 40
2022-12-14 16:00 | 38
2022-12-14 17:00 | 36
2022-12-14 18:00 | 35
2022-12-14 19:00 | 35
2022-12-14 20:00 | 34.7
2022-12-14 21:00 | 34
2022-12-14 22:00 | 33
2022-12-14 23:00 | 32
2022-12-15 | 32
2022-12-15 01:00 | 32
2022-12-15 02:00 | 32
2022-12-15 03:00 | 32
2022-12-15 04:00 | 33
2022-12-15 05:00 | 33
2022-12-15 06:00 | 33
2022-12-15 07:00 | 34
2022-12-15 08:00 | 35
2022-12-15 09:00 | 37
2022-12-15 10:00 | 38
2022-12-15 11:00 | 39
2022-12-15 12:00 | 39
2022-12-15 13:00 | 40
2022-12-15 14:00 | 41
2022-12-15 15:00 | 41
2022-12-15 16:00 | 40
2022-12-15 17:00 | 40
2022-12-15 18:00 | 40
2022-12-15 19:00 | 41
2022-12-15 20:00 | 42
2022-12-15 21:00 | 42
2022-12-15 22:00 | 42
2022-12-15 23:00 | 42
2022-12-16 | 43
2022-12-16 01:00 | 42
2022-12-16 02:00 | 43
2022-12-16 03:00 | 43
2022-12-16 04:00 | 43
2022-12-16 05:00 | 43
2022-12-16 06:00 | 44
2022-12-16 07:00 | 45
2022-12-16 08:00 | 45
2022-12-16 09:00 | 46
2022-12-16 10:00 | 46
2022-12-16 11:00 | 47
2022-12-16 12:00 | 47
2022-12-16 13:00 | 46
2022-12-16 14:00 | 45
2022-12-16 15:00 | 44
2022-12-16 16:00 | 42
2022-12-16 17:00 | 39
2022-12-16 18:00 | 39
2022-12-16 19:00 | 39
2022-12-16 20:00 | 39
2022-12-16 21:00 | 39
2022-12-16 22:00 | 39
2022-12-16 23:00 | 39
2022-12-17 | 40
2022-12-17 01:00 | 40
2022-12-17 02:00 | 40
2022-12-17 03:00 | 40
2022-12-17 04:00 | 39
2022-12-17 05:00 | 39
2022-12-17 06:00 | 38
2022-12-17 07:00 | 38
2022-12-17 08:00 | 38
2022-12-17 09:00 | 40
2022-12-17 10:00 | 42
2022-12-17 11:00 | 43
2022-12-17 12:00 | 43
2022-12-17 13:00 | 46
2022-12-17 14:00 | 44
2022-12-17 15:00 | 42
2022-12-17 16:00 | 42
2022-12-17 17:00 | 40
2022-12-17 18:00 | 41
2022-12-17 19:00 | 40
2022-12-17 20:00 | 40
2022-12-17 21:00 | 39
2022-12-17 22:00 | 39
2022-12-17 23:00 | 37
2022-12-18 | 36
2022-12-18 01:00 | 36
2022-12-18 02:00 | 35
2022-12-18 03:00 | 35
2022-12-18 04:00 | 35
2022-12-18 05:00 | 34
2022-12-18 06:00 | 34
2022-12-18 07:00 | 34
2022-12-18 08:00 | 34
2022-12-18 09:00 | 36
2022-12-18 10:00 | 38
2022-12-18 11:00 | 39
2022-12-18 12:00 | 40
2022-12-18 13:00 | 40
2022-12-18 14:00 | 41
2022-12-18 15:00 | 40
2022-12-18 16:00 | 39
2022-12-18 17:00 | 37
2022-12-18 18:00 | 37
2022-12-18 19:00 | 37
2022-12-18 20:00 | 36
2022-12-18 21:00 | 35
2022-12-18 22:00 | 34
2022-12-18 23:00 | 34
2022-12-19 | 33
2022-12-19 01:00 | 32
2022-12-19 02:00 | 31
2022-12-19 03:00 | 31
2022-12-19 04:00 | 31
2022-12-19 05:00 | 31
2022-12-19 06:00 | 31
2022-12-19 07:00 | 31
2022-12-19 08:00 | 32
2022-12-19 09:00 | 33
2022-12-19 10:00 | 35
2022-12-19 11:00 | 37
2022-12-19 12:00 | 38
2022-12-19 13:00 | 39
2022-12-19 14:00 | 39
2022-12-19 15:00 | 37
2022-12-19 16:00 | 36
2022-12-19 17:00 | 35
2022-12-19 18:00 | 35
2022-12-19 19:00 | 35
2022-12-19 20:00 | 34
2022-12-19 21:00 | 34
2022-12-19 22:00 | 34
2022-12-19 23:00 | 34
2022-12-20 | 33
2022-12-20 01:00 | 32
2022-12-20 02:00 | 32
2022-12-20 03:00 | 32
2022-12-20 04:00 | 32
2022-12-20 05:00 | 32
2022-12-20 06:00 | 30
2022-12-20 07:00 | 31
2022-12-20 08:00 | 32
2022-12-20 09:00 | 34
2022-12-20 10:00 | 35
2022-12-20 11:00 | 36
2022-12-20 12:00 | 38
2022-12-20 13:00 | 39
2022-12-20 14:00 | 40
2022-12-20 15:00 | 40
2022-12-20 16:00 | 38
2022-12-20 17:00 | 37
2022-12-20 18:00 | 36
2022-12-20 19:00 | 36
2022-12-20 20:00 | 34
2022-12-20 21:00 | 33
2022-12-20 22:00 | 32
2022-12-20 23:00 | 31
2022-12-21 | 30
2022-12-21 01:00 | 28
2022-12-21 02:00 | 29
2022-12-21 03:00 | 27
2022-12-21 04:00 | 28
2022-12-21 05:00 | 26
2022-12-21 06:00 | 27
2022-12-21 07:00 | 27
2022-12-21 08:00 | 28
2022-12-21 09:00 | 31
2022-12-21 10:00 | 32
2022-12-21 11:00 | 35
2022-12-21 12:00 | 37
2022-12-21 13:00 | 39
2022-12-21 14:00 | 39
2022-12-21 15:00 | 39
2022-12-21 16:00 | 36
2022-12-21 17:00 | 34
2022-12-21 18:00 | 36
2022-12-21 19:00 | 33
2022-12-21 20:00 | 34
2022-12-21 21:00 | 34
2022-12-21 22:00 | 33
2022-12-21 23:00 | 32
2022-12-22 | 32
2022-12-22 01:00 | 31
2022-12-22 02:00 | 30
2022-12-22 03:00 | 31
2022-12-22 04:00 | 30
2022-12-22 05:00 | 30
2022-12-22 06:00 | 31
2022-12-22 07:00 | 32
2022-12-22 08:00 | 34
2022-12-22 09:00 | 38
2022-12-22 10:00 | 43
2022-12-22 11:00 | 44
2022-12-22 12:00 | 45
2022-12-22 13:00 | 45
2022-12-22 14:00 | 44
2022-12-22 15:00 | 45
2022-12-22 16:00 | 46
2022-12-22 17:00 | 46
2022-12-22 18:00 | 47
2022-12-22 19:00 | 46
2022-12-22 20:00 | 46
2022-12-22 21:00 | 46
2022-12-22 22:00 | 47
2022-12-22 23:00 | 49
2022-12-23 | 53
2022-12-23 01:00 | 54
2022-12-23 02:00 | 54
2022-12-23 03:00 | 54
2022-12-23 04:00 | 55
2022-12-23 05:00 | 55
2022-12-23 06:00 | 53
2022-12-23 07:00 | 50
2022-12-23 08:00 | 48
2022-12-23 09:00 | 47
2022-12-23 10:00 | 46
2022-12-23 11:00 | 48
2022-12-23 12:00 | 49
2022-12-23 13:00 | 46
2022-12-23 14:00 | 40
2022-12-23 15:00 | 32
2022-12-23 16:00 | 26
2022-12-23 17:00 | 23
2022-12-23 18:00 | 19
2022-12-23 19:00 | 17
2022-12-23 20:00 | 15
2022-12-23 21:00 | 12
2022-12-23 22:00 | 11
2022-12-23 23:00 | 10
2022-12-24 | 9
2022-12-24 01:00 | 9
2022-12-24 02:00 | 9
2022-12-24 03:00 | 8
2022-12-24 04:00 | 8
2022-12-24 05:00 | 7
2022-12-24 06:00 | 7
2022-12-24 07:00 | 8
2022-12-24 08:00 | 7
2022-12-24 09:00 | 9
2022-12-24 10:00 | 10
2022-12-24 11:00 | 12
2022-12-24 12:00 | 13
2022-12-24 13:00 | 14
2022-12-24 14:00 | 15
2022-12-24 15:00 | 16
2022-12-24 16:00 | 14
2022-12-24 17:00 | 14
2022-12-24 18:00 | 14
2022-12-24 19:00 | 14
2022-12-24 20:00 | 15
2022-12-24 21:00 | 15
2022-12-24 22:00 | 15
2022-12-24 23:00 | 15
2022-12-25 | 14
2022-12-25 01:00 | 14
2022-12-25 02:00 | 15
2022-12-25 03:00 | 15
2022-12-25 04:00 | 15
2022-12-25 05:00 | 16
2022-12-25 06:00 | 17
2022-12-25 07:00 | 18
2022-12-25 08:00 | 18
2022-12-25 09:00 | 21
2022-12-25 10:00 | 23
2022-12-25 11:00 | 24
2022-12-25 12:00 | 26
2022-12-25 13:00 | 27
2022-12-25 14:00 | 27
2022-12-25 15:00 | 28
2022-12-25 16:00 | 27
2022-12-25 17:00 | 26
2022-12-25 18:00 | 26
2022-12-25 19:00 | 25
2022-12-25 20:00 | 24
2022-12-25 21:00 | 23
2022-12-25 22:00 | 22
2022-12-25 23:00 | 21
2022-12-26 | 21
2022-12-26 01:00 | 20
2022-12-26 02:00 | 19
2022-12-26 03:00 | 19
2022-12-26 04:00 | 19
2022-12-26 05:00 | 19
2022-12-26 06:00 | 18
2022-12-26 07:00 | 19
2022-12-26 08:00 | 19
2022-12-26 09:00 | 21
2022-12-26 10:00 | 23
2022-12-26 11:00 | 25
2022-12-26 12:00 | 26
2022-12-26 13:00 | 27
2022-12-26 14:00 | 28
2022-12-26 15:00 | 28
2022-12-26 16:00 | 27
2022-12-26 17:00 | 27
2022-12-26 18:00 | 28
2022-12-26 19:00 | 28
2022-12-26 20:00 | 28
2022-12-26 21:00 | 28
2022-12-26 22:00 | 28
2022-12-26 23:00 | 29
2022-12-27 | 29
2022-12-27 01:00 | 29
2022-12-27 02:00 | 29
2022-12-27 03:00 | 29
2022-12-27 04:00 | 29
2022-12-27 05:00 | 29
2022-12-27 06:00 | 29
2022-12-27 07:00 | 28
2022-12-27 08:00 | 29
2022-12-27 09:00 | 30
2022-12-27 10:00 | 31
2022-12-27 11:00 | 32
2022-12-27 12:00 | 33
2022-12-27 13:00 | 34
2022-12-27 14:00 | 35
2022-12-27 15:00 | 34
2022-12-27 16:00 | 33
2022-12-27 17:00 | 33
2022-12-27 18:00 | 33
2022-12-27 19:00 | 33
2022-12-27 20:00 | 33
2022-12-27 21:00 | 33
2022-12-27 22:00 | 33
2022-12-27 23:00 | 33
2022-12-28 | 34
2022-12-28 01:00 | 34
2022-12-28 02:00 | 33
2022-12-28 03:00 | 32
2022-12-28 04:00 | 28
2022-12-28 05:00 | 31
2022-12-28 06:00 | 30
2022-12-28 07:00 | 30
2022-12-28 08:00 | 33
2022-12-28 09:00 | 34
2022-12-28 10:00 | 38
2022-12-28 11:00 | 40
2022-12-28 12:00 | 43
2022-12-28 13:00 | 43
2022-12-28 14:00 | 44
2022-12-28 15:00 | 44
2022-12-28 16:00 | 43
2022-12-28 17:00 | 40
2022-12-28 18:00 | 38
2022-12-28 19:00 | 36
2022-12-28 20:00 | 37
2022-12-28 21:00 | 39
2022-12-28 22:00 | 37
2022-12-28 23:00 | 38
2022-12-29 | 38
2022-12-29 01:00 | 36
2022-12-29 02:00 | 34
2022-12-29 03:00 | 34
2022-12-29 04:00 | 35
2022-12-29 05:00 | 32
2022-12-29 06:00 | 36
2022-12-29 07:00 | 33
2022-12-29 08:00 | 33
2022-12-29 09:00 | 39
2022-12-29 10:00 | 41
2022-12-29 11:00 | 43
2022-12-29 12:00 | 44
2022-12-29 13:00 | 44
2022-12-29 14:00 | 46
2022-12-29 15:00 | 45
2022-12-29 16:00 | 44
2022-12-29 17:00 | 42
2022-12-29 18:00 | 40
2022-12-29 19:00 | 41
2022-12-29 20:00 | 39
2022-12-29 21:00 | 38
2022-12-29 22:00 | 41
2022-12-29 23:00 | 41
2022-12-30 | 38
2022-12-30 01:00 | 38
2022-12-30 02:00 | 38
2022-12-30 03:00 | 37
2022-12-30 04:00 | 36
2022-12-30 05:00 | 37
2022-12-30 06:00 | 38
2022-12-30 07:00 | 38
2022-12-30 08:00 | 36
2022-12-30 09:00 | 42
2022-12-30 10:00 | 45
2022-12-30 11:00 | 47
2022-12-30 12:00 | 48
2022-12-30 13:00 | 49
2022-12-30 14:00 | 50
2022-12-30 15:00 | 50
2022-12-30 16:00 | 49
2022-12-30 17:00 | 44
2022-12-30 18:00 | 44
2022-12-30 19:00 | 44
2022-12-30 20:00 | 42
2022-12-30 21:00 | 42
2022-12-30 22:00 | 42
2022-12-30 23:00 | 43
2022-12-31 | 43
2022-12-31 01:00 | 43
2022-12-31 02:00 | 42
2022-12-31 03:00 | 42
2022-12-31 04:00 | 44
2022-12-31 05:00 | 45
2022-12-31 06:00 | 45
2022-12-31 07:00 | 46
2022-12-31 08:00 | 48
2022-12-31 09:00 | 48
2022-12-31 10:00 | 49
2022-12-31 11:00 | 49
2022-12-31 12:00 | 50
2022-12-31 13:00 | 50
2022-12-31 14:00 | 50
2022-12-31 15:00 | 51
2022-12-31 16:00 | 50
2022-12-31 17:00 | 50
2022-12-31 18:00 | 50
2022-12-31 19:00 | 50
2022-12-31 20:00 | 48
2022-12-31 21:00 | 49
2022-12-31 22:00 | 49
2022-12-31 23:00 | 49

## Step 1.4 CNY OAT
Datetime | Outdoor Air Temp (F)
2018-01-01 | 10
2018-01-01 01:00 | 10
2018-01-01 02:00 | 10
2018-01-01 03:00 | 9
2018-01-01 04:00 | 9
2018-01-01 05:00 | 9
2018-01-01 06:00 | 8
2018-01-01 07:00 | 8
2018-01-01 08:00 | 9
2018-01-01 09:00 | 10
2018-01-01 10:00 | 12
2018-01-01 11:00 | 13
2018-01-01 12:00 | 15
2018-01-01 13:00 | 16
2018-01-01 14:00 | 18
2018-01-01 15:00 | 19
2018-01-01 16:00 | 19
2018-01-01 17:00 | 19
2018-01-01 18:00 | 19
2018-01-01 19:00 | 18
2018-01-01 20:00 | 18
2018-01-01 21:00 | 18
2018-01-01 22:00 | 18
2018-01-01 23:00 | 17
2018-01-02 | 16
2018-01-02 01:00 | 16
2018-01-02 02:00 | 16
2018-01-02 03:00 | 15
2018-01-02 04:00 | 15
2018-01-02 05:00 | 14
2018-01-02 06:00 | 14
2018-01-02 07:00 | 14
2018-01-02 08:00 | 14
2018-01-02 09:00 | 16
2018-01-02 10:00 | 17
2018-01-02 11:00 | 19
2018-01-02 12:00 | 21
2018-01-02 13:00 | 23
2018-01-02 14:00 | 25
2018-01-02 15:00 | 27
2018-01-02 16:00 | 25
2018-01-02 17:00 | 25
2018-01-02 18:00 | 25
2018-01-02 19:00 | 24
2018-01-02 20:00 | 21
2018-01-02 21:00 | 21
2018-01-02 22:00 | 21
2018-01-02 23:00 | 21
2018-01-03 | 20
2018-01-03 01:00 | 20
2018-01-03 02:00 | 19
2018-01-03 03:00 | 19
2018-01-03 04:00 | 19
2018-01-03 05:00 | 18
2018-01-03 06:00 | 18
2018-01-03 07:00 | 18
2018-01-03 08:00 | 18
2018-01-03 09:00 | 19
2018-01-03 10:00 | 22
2018-01-03 11:00 | 25
2018-01-03 12:00 | 27
2018-01-03 13:00 | 28
2018-01-03 14:00 | 28
2018-01-03 15:00 | 28
2018-01-03 16:00 | 30
2018-01-03 17:00 | 28
2018-01-03 18:00 | 27
2018-01-03 19:00 | 27
2018-01-03 20:00 | 27
2018-01-03 21:00 | 28
2018-01-03 22:00 | 28
2018-01-03 23:00 | 28
2018-01-04 | 29
2018-01-04 01:00 | 29
2018-01-04 02:00 | 28
2018-01-04 03:00 | 28
2018-01-04 04:00 | 28
2018-01-04 05:00 | 27
2018-01-04 06:00 | 25
2018-01-04 07:00 | 24
2018-01-04 08:00 | 24
2018-01-04 09:00 | 22
2018-01-04 10:00 | 22
2018-01-04 11:00 | 25
2018-01-04 12:00 | 25
2018-01-04 13:00 | 24
2018-01-04 14:00 | 25
2018-01-04 15:00 | 24
2018-01-04 16:00 | 25
2018-01-04 17:00 | 26
2018-01-04 18:00 | 26
2018-01-04 19:00 | 26
2018-01-04 20:00 | 25
2018-01-04 21:00 | 24
2018-01-04 22:00 | 23
2018-01-04 23:00 | 22
2018-01-05 | 20
2018-01-05 01:00 | 19
2018-01-05 02:00 | 17
2018-01-05 03:00 | 15
2018-01-05 04:00 | 14
2018-01-05 05:00 | 13
2018-01-05 06:00 | 12
2018-01-05 07:00 | 11
2018-01-05 08:00 | 10
2018-01-05 09:00 | 10
2018-01-05 10:00 | 12
2018-01-05 11:00 | 12
2018-01-05 12:00 | 16
2018-01-05 13:00 | 16
2018-01-05 14:00 | 16
2018-01-05 15:00 | 18
2018-01-05 16:00 | 17
2018-01-05 17:00 | 16
2018-01-05 18:00 | 16
2018-01-05 19:00 | 15
2018-01-05 20:00 | 16
2018-01-05 21:00 | 12
2018-01-05 22:00 | 13
2018-01-05 23:00 | 12
2018-01-06 | 11
2018-01-06 01:00 | 11
2018-01-06 02:00 | 10
2018-01-06 03:00 | 10
2018-01-06 04:00 | 10
2018-01-06 05:00 | 10
2018-01-06 06:00 | 9
2018-01-06 07:00 | 8
2018-01-06 08:00 | 9
2018-01-06 09:00 | 10
2018-01-06 10:00 | 11
2018-01-06 11:00 | 12
2018-01-06 12:00 | 12
2018-01-06 13:00 | 13
2018-01-06 14:00 | 14
2018-01-06 15:00 | 14
2018-01-06 16:00 | 14
2018-01-06 17:00 | 12
2018-01-06 18:00 | 12
2018-01-06 19:00 | 11
2018-01-06 20:00 | 10
2018-01-06 21:00 | 10
2018-01-06 22:00 | 9
2018-01-06 23:00 | 9
2018-01-07 | 8
2018-01-07 01:00 | 8
2018-01-07 02:00 | 9
2018-01-07 03:00 | 9
2018-01-07 04:00 | 7
2018-01-07 05:00 | 7
2018-01-07 06:00 | 7
2018-01-07 07:00 | 6
2018-01-07 08:00 | 7
2018-01-07 09:00 | 9
2018-01-07 10:00 | 9
2018-01-07 11:00 | 12
2018-01-07 12:00 | 12
2018-01-07 13:00 | 15
2018-01-07 14:00 | 18
2018-01-07 15:00 | 18
2018-01-07 16:00 | 18
2018-01-07 17:00 | 18
2018-01-07 18:00 | 18
2018-01-07 19:00 | 18
2018-01-07 20:00 | 18
2018-01-07 21:00 | 18
2018-01-07 22:00 | 18
2018-01-07 23:00 | 18
2018-01-08 | 18
2018-01-08 01:00 | 18
2018-01-08 02:00 | 19
2018-01-08 03:00 | 19
2018-01-08 04:00 | 20
2018-01-08 05:00 | 19
2018-01-08 06:00 | 19
2018-01-08 07:00 | 20
2018-01-08 08:00 | 19
2018-01-08 09:00 | 21
2018-01-08 10:00 | 23
2018-01-08 11:00 | 25
2018-01-08 12:00 | 27
2018-01-08 13:00 | 27
2018-01-08 14:00 | 28
2018-01-08 15:00 | 30
2018-01-08 16:00 | 31
2018-01-08 17:00 | 30.5
2018-01-08 18:00 | 30
2018-01-08 19:00 | 30
2018-01-08 20:00 | 30
2018-01-08 21:00 | 30
2018-01-08 22:00 | 31
2018-01-08 23:00 | 34
2018-01-09 | 32
2018-01-09 01:00 | 32
2018-01-09 02:00 | 30
2018-01-09 03:00 | 30
2018-01-09 04:00 | 32
2018-01-09 05:00 | 34
2018-01-09 06:00 | 34
2018-01-09 07:00 | 34
2018-01-09 08:00 | 34
2018-01-09 09:00 | 36
2018-01-09 10:00 | 38
2018-01-09 11:00 | 39
2018-01-09 12:00 | 43
2018-01-09 13:00 | 42
2018-01-09 14:00 | 43
2018-01-09 15:00 | 43
2018-01-09 16:00 | 42
2018-01-09 17:00 | 39
2018-01-09 18:00 | 39
2018-01-09 19:00 | 38
2018-01-09 20:00 | 37
2018-01-09 21:00 | 36
2018-01-09 22:00 | 36
2018-01-09 23:00 | 36
2018-01-10 | 34
2018-01-10 01:00 | 33
2018-01-10 02:00 | 34
2018-01-10 03:00 | 30
2018-01-10 04:00 | 28
2018-01-10 05:00 | 28
2018-01-10 06:00 | 28
2018-01-10 07:00 | 30
2018-01-10 08:00 | 30
2018-01-10 09:00 | 32
2018-01-10 10:00 | 33
2018-01-10 11:00 | 36
2018-01-10 12:00 | 37
2018-01-10 13:00 | 39
2018-01-10 14:00 | 37
2018-01-10 15:00 | 37
2018-01-10 16:00 | 37
2018-01-10 17:00 | 37
2018-01-10 18:00 | 37
2018-01-10 19:00 | 37
2018-01-10 20:00 | 37
2018-01-10 21:00 | 39
2018-01-10 22:00 | 40
2018-01-10 23:00 | 39
2018-01-11 | 40
2018-01-11 01:00 | 41
2018-01-11 02:00 | 41
2018-01-11 03:00 | 37
2018-01-11 04:00 | 37
2018-01-11 05:00 | 36
2018-01-11 06:00 | 36
2018-01-11 07:00 | 37
2018-01-11 08:00 | 37
2018-01-11 09:00 | 39
2018-01-11 10:00 | 40
2018-01-11 11:00 | 41
2018-01-11 12:00 | 45
2018-01-11 13:00 | 43
2018-01-11 14:00 | 45
2018-01-11 15:00 | 45
2018-01-11 16:00 | 47
2018-01-11 17:00 | 45
2018-01-11 18:00 | 41
2018-01-11 19:00 | 42
2018-01-11 20:00 | 43
2018-01-11 21:00 | 39
2018-01-11 22:00 | 39
2018-01-11 23:00 | 39
2018-01-12 | 39
2018-01-12 01:00 | 40
2018-01-12 02:00 | 39
2018-01-12 03:00 | 37
2018-01-12 04:00 | 39
2018-01-12 05:00 | 45
2018-01-12 06:00 | 54
2018-01-12 07:00 | 53
2018-01-12 08:00 | 52
2018-01-12 09:00 | 52
2018-01-12 10:00 | 54
2018-01-12 11:00 | 55
2018-01-12 12:00 | 57
2018-01-12 13:00 | 60
2018-01-12 14:00 | 57
2018-01-12 15:00 | 54
2018-01-12 16:00 | 55
2018-01-12 17:00 | 55
2018-01-12 18:00 | 54
2018-01-12 19:00 | 51
2018-01-12 20:00 | 50
2018-01-12 21:00 | 50
2018-01-12 22:00 | 51
2018-01-12 23:00 | 54
2018-01-13 | 53
2018-01-13 01:00 | 51
2018-01-13 02:00 | 50
2018-01-13 03:00 | 52
2018-01-13 04:00 | 52
2018-01-13 05:00 | 52
2018-01-13 06:00 | 48
2018-01-13 07:00 | 43
2018-01-13 08:00 | 37
2018-01-13 09:00 | 30
2018-01-13 10:00 | 29
2018-01-13 11:00 | 28
2018-01-13 12:00 | 30
2018-01-13 13:00 | 32
2018-01-13 14:00 | 34
2018-01-13 15:00 | 34
2018-01-13 16:00 | 32
2018-01-13 17:00 | 28
2018-01-13 18:00 | 27
2018-01-13 19:00 | 25
2018-01-13 20:00 | 25
2018-01-13 21:00 | 23
2018-01-13 22:00 | 22
2018-01-13 23:00 | 21
2018-01-14 | 20
2018-01-14 01:00 | 19
2018-01-14 02:00 | 18
2018-01-14 03:00 | 18
2018-01-14 04:00 | 17
2018-01-14 05:00 | 18
2018-01-14 06:00 | 16
2018-01-14 07:00 | 16
2018-01-14 08:00 | 16
2018-01-14 09:00 | 16
2018-01-14 10:00 | 18
2018-01-14 11:00 | 19
2018-01-14 12:00 | 21
2018-01-14 13:00 | 22
2018-01-14 14:00 | 23
2018-01-14 15:00 | 23
2018-01-14 16:00 | 23
2018-01-14 17:00 | 21
2018-01-14 18:00 | 21
2018-01-14 19:00 | 21
2018-01-14 20:00 | 19
2018-01-14 21:00 | 18
2018-01-14 22:00 | 18
2018-01-14 23:00 | 18
2018-01-15 | 17
2018-01-15 01:00 | 17
2018-01-15 02:00 | 18
2018-01-15 03:00 | 18
2018-01-15 04:00 | 17
2018-01-15 05:00 | 18
2018-01-15 06:00 | 19
2018-01-15 07:00 | 19
2018-01-15 08:00 | 18
2018-01-15 09:00 | 21
2018-01-15 10:00 | 24
2018-01-15 11:00 | 25
2018-01-15 12:00 | 27
2018-01-15 13:00 | 27
2018-01-15 14:00 | 28
2018-01-15 15:00 | 28
2018-01-15 16:00 | 29
2018-01-15 17:00 | 28
2018-01-15 18:00 | 27
2018-01-15 19:00 | 26
2018-01-15 20:00 | 27
2018-01-15 21:00 | 27
2018-01-15 22:00 | 26
2018-01-15 23:00 | 25
2018-01-16 | 24
2018-01-16 01:00 | 25
2018-01-16 02:00 | 25
2018-01-16 03:00 | 25
2018-01-16 04:00 | 25
2018-01-16 05:00 | 25
2018-01-16 06:00 | 27
2018-01-16 07:00 | 26
2018-01-16 08:00 | 27
2018-01-16 09:00 | 27
2018-01-16 10:00 | 29
2018-01-16 11:00 | 30
2018-01-16 12:00 | 32
2018-01-16 13:00 | 33
2018-01-16 14:00 | 34
2018-01-16 15:00 | 32
2018-01-16 16:00 | 32
2018-01-16 17:00 | 32
2018-01-16 18:00 | 32
2018-01-16 19:00 | 32
2018-01-16 20:00 | 34
2018-01-16 21:00 | 34
2018-01-16 22:00 | 33
2018-01-16 23:00 | 34
2018-01-17 | 34
2018-01-17 01:00 | 35
2018-01-17 02:00 | 36
2018-01-17 03:00 | 36
2018-01-17 04:00 | 35
2018-01-17 05:00 | 36
2018-01-17 06:00 | 36
2018-01-17 07:00 | 35
2018-01-17 08:00 | 34
2018-01-17 09:00 | 34
2018-01-17 10:00 | 34
2018-01-17 11:00 | 34
2018-01-17 12:00 | 34
2018-01-17 13:00 | 34
2018-01-17 14:00 | 34
2018-01-17 15:00 | 34
2018-01-17 16:00 | 33
2018-01-17 17:00 | 31
2018-01-17 18:00 | 28
2018-01-17 19:00 | 28
2018-01-17 20:00 | 27
2018-01-17 21:00 | 27
2018-01-17 22:00 | 25
2018-01-17 23:00 | 25
2018-01-18 | 23
2018-01-18 01:00 | 23
2018-01-18 02:00 | 21
2018-01-18 03:00 | 21
2018-01-18 04:00 | 21
2018-01-18 05:00 | 21
2018-01-18 06:00 | 21
2018-01-18 07:00 | 22
2018-01-18 08:00 | 21
2018-01-18 09:00 | 23
2018-01-18 10:00 | 25
2018-01-18 11:00 | 28
2018-01-18 12:00 | 30
2018-01-18 13:00 | 31
2018-01-18 14:00 | 32
2018-01-18 15:00 | 32
2018-01-18 16:00 | 33
2018-01-18 17:00 | 32
2018-01-18 18:00 | 30
2018-01-18 19:00 | 30
2018-01-18 20:00 | 28
2018-01-18 21:00 | 28
2018-01-18 22:00 | 28
2018-01-18 23:00 | 27
2018-01-19 | 27
2018-01-19 01:00 | 26
2018-01-19 02:00 | 27
2018-01-19 03:00 | 27
2018-01-19 04:00 | 27
2018-01-19 05:00 | 28
2018-01-19 06:00 | 30
2018-01-19 07:00 | 32
2018-01-19 08:00 | 32
2018-01-19 09:00 | 32
2018-01-19 10:00 | 32
2018-01-19 11:00 | 34
2018-01-19 12:00 | 34
2018-01-19 13:00 | 36
2018-01-19 14:00 | 36
2018-01-19 15:00 | 37
2018-01-19 16:00 | 38
2018-01-19 17:00 | 37
2018-01-19 18:00 | 37
2018-01-19 19:00 | 38
2018-01-19 20:00 | 39
2018-01-19 21:00 | 39
2018-01-19 22:00 | 39
2018-01-19 23:00 | 39
2018-01-20 | 39
2018-01-20 01:00 | 39
2018-01-20 02:00 | 37
2018-01-20 03:00 | 37
2018-01-20 04:00 | 40
2018-01-20 05:00 | 39
2018-01-20 06:00 | 39
2018-01-20 07:00 | 40
2018-01-20 08:00 | 39
2018-01-20 09:00 | 43
2018-01-20 10:00 | 46
2018-01-20 11:00 | 48
2018-01-20 12:00 | 52
2018-01-20 13:00 | 52
2018-01-20 14:00 | 54
2018-01-20 15:00 | 52
2018-01-20 16:00 | 50
2018-01-20 17:00 | 50
2018-01-20 18:00 | 48
2018-01-20 19:00 | 48
2018-01-20 20:00 | 48
2018-01-20 21:00 | 46
2018-01-20 22:00 | 47
2018-01-20 23:00 | 46
2018-01-21 | 45
2018-01-21 01:00 | 43
2018-01-21 02:00 | 43
2018-01-21 03:00 | 43
2018-01-21 04:00 | 43
2018-01-21 05:00 | 43
2018-01-21 06:00 | 45
2018-01-21 07:00 | 44
2018-01-21 08:00 | 45
2018-01-21 09:00 | 45
2018-01-21 10:00 | 45
2018-01-21 11:00 | 46
2018-01-21 12:00 | 46
2018-01-21 13:00 | 48
2018-01-21 14:00 | 50
2018-01-21 15:00 | 52
2018-01-21 16:00 | 48
2018-01-21 17:00 | 48
2018-01-21 18:00 | 50
2018-01-21 19:00 | 49
2018-01-21 20:00 | 46
2018-01-21 21:00 | 48
2018-01-21 22:00 | 47
2018-01-21 23:00 | 46
2018-01-22 | 46
2018-01-22 01:00 | 41
2018-01-22 02:00 | 39
2018-01-22 03:00 | 39
2018-01-22 04:00 | 38
2018-01-22 05:00 | 37
2018-01-22 06:00 | 37
2018-01-22 07:00 | 39
2018-01-22 08:00 | 39
2018-01-22 09:00 | 39
2018-01-22 10:00 | 40
2018-01-22 11:00 | 43
2018-01-22 12:00 | 43
2018-01-22 13:00 | 43
2018-01-22 14:00 | 43
2018-01-22 15:00 | 43
2018-01-22 16:00 | 42
2018-01-22 17:00 | 39
2018-01-22 18:00 | 39
2018-01-22 19:00 | 38
2018-01-22 20:00 | 39
2018-01-22 21:00 | 37
2018-01-22 22:00 | 37
2018-01-22 23:00 | 37
2018-01-23 | 37
2018-01-23 01:00 | 36
2018-01-23 02:00 | 36
2018-01-23 03:00 | 36
2018-01-23 04:00 | 37
2018-01-23 05:00 | 37
2018-01-23 06:00 | 37
2018-01-23 07:00 | 39
2018-01-23 08:00 | 50
2018-01-23 09:00 | 50
2018-01-23 10:00 | 52
2018-01-23 11:00 | 54
2018-01-23 12:00 | 54
2018-01-23 13:00 | 54
2018-01-23 14:00 | 57
2018-01-23 15:00 | 59
2018-01-23 16:00 | 58
2018-01-23 17:00 | 56
2018-01-23 18:00 | 53
2018-01-23 19:00 | 52
2018-01-23 20:00 | 50
2018-01-23 21:00 | 48
2018-01-23 22:00 | 47
2018-01-23 23:00 | 46
2018-01-24 | 45
2018-01-24 01:00 | 45
2018-01-24 02:00 | 45
2018-01-24 03:00 | 44
2018-01-24 04:00 | 44
2018-01-24 05:00 | 44
2018-01-24 06:00 | 44
2018-01-24 07:00 | 44
2018-01-24 08:00 | 42
2018-01-24 09:00 | 41
2018-01-24 10:00 | 40
2018-01-24 11:00 | 39
2018-01-24 12:00 | 41
2018-01-24 13:00 | 41
2018-01-24 14:00 | 39
2018-01-24 15:00 | 39
2018-01-24 16:00 | 37
2018-01-24 17:00 | 37
2018-01-24 18:00 | 36
2018-01-24 19:00 | 34
2018-01-24 20:00 | 34
2018-01-24 21:00 | 30
2018-01-24 22:00 | 30
2018-01-24 23:00 | 28
2018-01-25 | 28
2018-01-25 01:00 | 27
2018-01-25 02:00 | 25
2018-01-25 03:00 | 25
2018-01-25 04:00 | 24
2018-01-25 05:00 | 25
2018-01-25 06:00 | 25
2018-01-25 07:00 | 25
2018-01-25 08:00 | 27
2018-01-25 09:00 | 27
2018-01-25 10:00 | 29
2018-01-25 11:00 | 30
2018-01-25 12:00 | 30
2018-01-25 13:00 | 33
2018-01-25 14:00 | 34
2018-01-25 15:00 | 36
2018-01-25 16:00 | 34
2018-01-25 17:00 | 34
2018-01-25 18:00 | 34
2018-01-25 19:00 | 32
2018-01-25 20:00 | 32
2018-01-25 21:00 | 30
2018-01-25 22:00 | 31
2018-01-25 23:00 | 30
2018-01-26 | 30
2018-01-26 01:00 | 30
2018-01-26 02:00 | 30
2018-01-26 03:00 | 28
2018-01-26 04:00 | 29
2018-01-26 05:00 | 28
2018-01-26 06:00 | 28
2018-01-26 07:00 | 28
2018-01-26 08:00 | 28
2018-01-26 09:00 | 30
2018-01-26 10:00 | 32
2018-01-26 11:00 | 34
2018-01-26 12:00 | 36
2018-01-26 13:00 | 36
2018-01-26 14:00 | 37
2018-01-26 15:00 | 37
2018-01-26 16:00 | 38
2018-01-26 17:00 | 36
2018-01-26 18:00 | 34
2018-01-26 19:00 | 34
2018-01-26 20:00 | 36
2018-01-26 21:00 | 36
2018-01-26 22:00 | 35
2018-01-26 23:00 | 36
2018-01-27 | 35
2018-01-27 01:00 | 36
2018-01-27 02:00 | 36
2018-01-27 03:00 | 36
2018-01-27 04:00 | 36
2018-01-27 05:00 | 37
2018-01-27 06:00 | 37
2018-01-27 07:00 | 38
2018-01-27 08:00 | 37
2018-01-27 09:00 | 39
2018-01-27 10:00 | 43
2018-01-27 11:00 | 45
2018-01-27 12:00 | 48
2018-01-27 13:00 | 53
2018-01-27 14:00 | 55
2018-01-27 15:00 | 55
2018-01-27 16:00 | 56
2018-01-27 17:00 | 55
2018-01-27 18:00 | 54
2018-01-27 19:00 | 53
2018-01-27 20:00 | 54
2018-01-27 21:00 | 52
2018-01-27 22:00 | 50
2018-01-27 23:00 | 50
2018-01-28 | 51
2018-01-28 01:00 | 51
2018-01-28 02:00 | 54
2018-01-28 03:00 | 54
2018-01-28 04:00 | 52
2018-01-28 05:00 | 52
2018-01-28 06:00 | 50
2018-01-28 07:00 | 50
2018-01-28 08:00 | 50
2018-01-28 09:00 | 50
2018-01-28 10:00 | 47
2018-01-28 11:00 | 48
2018-01-28 12:00 | 48
2018-01-28 13:00 | 49
2018-01-28 14:00 | 50
2018-01-28 15:00 | 48
2018-01-28 16:00 | 48
2018-01-28 17:00 | 48
2018-01-28 18:00 | 48
2018-01-28 19:00 | 49
2018-01-28 20:00 | 48
2018-01-28 21:00 | 48
2018-01-28 22:00 | 44
2018-01-28 23:00 | 43
2018-01-29 | 42
2018-01-29 01:00 | 42
2018-01-29 02:00 | 41
2018-01-29 03:00 | 41
2018-01-29 04:00 | 42
2018-01-29 05:00 | 43
2018-01-29 06:00 | 41
2018-01-29 07:00 | 42
2018-01-29 08:00 | 39
2018-01-29 09:00 | 43
2018-01-29 10:00 | 42
2018-01-29 11:00 | 41
2018-01-29 12:00 | 43
2018-01-29 13:00 | 42
2018-01-29 14:00 | 43
2018-01-29 15:00 | 43
2018-01-29 16:00 | 43
2018-01-29 17:00 | 43
2018-01-29 18:00 | 41
2018-01-29 19:00 | 40
2018-01-29 20:00 | 39
2018-01-29 21:00 | 39
2018-01-29 22:00 | 39
2018-01-29 23:00 | 37
2018-01-30 | 35
2018-01-30 01:00 | 32
2018-01-30 02:00 | 32
2018-01-30 03:00 | 30
2018-01-30 04:00 | 31
2018-01-30 05:00 | 30
2018-01-30 06:00 | 30
2018-01-30 07:00 | 31
2018-01-30 08:00 | 30
2018-01-30 09:00 | 32
2018-01-30 10:00 | 33
2018-01-30 11:00 | 34
2018-01-30 12:00 | 36
2018-01-30 13:00 | 36
2018-01-30 14:00 | 36
2018-01-30 15:00 | 37
2018-01-30 16:00 | 35
2018-01-30 17:00 | 34
2018-01-30 18:00 | 30
2018-01-30 19:00 | 30
2018-01-30 20:00 | 28
2018-01-30 21:00 | 28
2018-01-30 22:00 | 28
2018-01-30 23:00 | 27
2018-01-31 | 26
2018-01-31 01:00 | 25
2018-01-31 02:00 | 25
2018-01-31 03:00 | 23.5
2018-01-31 04:00 | 22
2018-01-31 05:00 | 21
2018-01-31 06:00 | 19
2018-01-31 07:00 | 19
2018-01-31 08:00 | 19
2018-01-31 09:00 | 21
2018-01-31 10:00 | 23
2018-01-31 11:00 | 25
2018-01-31 12:00 | 28
2018-01-31 13:00 | 30
2018-01-31 14:00 | 30
2018-01-31 15:00 | 34
2018-01-31 16:00 | 32
2018-01-31 17:00 | 32
2018-01-31 18:00 | 32
2018-01-31 19:00 | 33
2018-01-31 20:00 | 34
2018-01-31 21:00 | 32
2018-01-31 22:00 | 32
2018-01-31 23:00 | 32
2018-02-01 | 33
2018-02-01 01:00 | 33
2018-02-01 02:00 | 34
2018-02-01 03:00 | 34
2018-02-01 04:00 | 34
2018-02-01 05:00 | 34
2018-02-01 06:00 | 36
2018-02-01 07:00 | 36
2018-02-01 08:00 | 37
2018-02-01 09:00 | 37
2018-02-01 10:00 | 38
2018-02-01 11:00 | 39
2018-02-01 12:00 | 41
2018-02-01 13:00 | 43
2018-02-01 14:00 | 43
2018-02-01 15:00 | 45
2018-02-01 16:00 | 44
2018-02-01 17:00 | 43
2018-02-01 18:00 | 43
2018-02-01 19:00 | 43
2018-02-01 20:00 | 45
2018-02-01 21:00 | 43
2018-02-01 22:00 | 41
2018-02-01 23:00 | 37
2018-02-02 | 39
2018-02-02 01:00 | 37
2018-02-02 02:00 | 37
2018-02-02 03:00 | 37
2018-02-02 04:00 | 38
2018-02-02 05:00 | 37
2018-02-02 06:00 | 34
2018-02-02 07:00 | 31
2018-02-02 08:00 | 30
2018-02-02 09:00 | 28
2018-02-02 10:00 | 28
2018-02-02 11:00 | 28
2018-02-02 12:00 | 27
2018-02-02 13:00 | 27
2018-02-02 14:00 | 28
2018-02-02 15:00 | 27
2018-02-02 16:00 | 26
2018-02-02 17:00 | 25
2018-02-02 18:00 | 25
2018-02-02 19:00 | 22
2018-02-02 20:00 | 21
2018-02-02 21:00 | 19
2018-02-02 22:00 | 19
2018-02-02 23:00 | 18
2018-02-03 | 18
2018-02-03 01:00 | 18
2018-02-03 02:00 | 18
2018-02-03 03:00 | 18
2018-02-03 04:00 | 18
2018-02-03 05:00 | 18
2018-02-03 06:00 | 19
2018-02-03 07:00 | 19
2018-02-03 08:00 | 19
2018-02-03 09:00 | 21
2018-02-03 10:00 | 23
2018-02-03 11:00 | 25
2018-02-03 12:00 | 27
2018-02-03 13:00 | 27
2018-02-03 14:00 | 30
2018-02-03 15:00 | 30
2018-02-03 16:00 | 31
2018-02-03 17:00 | 30
2018-02-03 18:00 | 30
2018-02-03 19:00 | 30
2018-02-03 20:00 | 30
2018-02-03 21:00 | 30
2018-02-03 22:00 | 30
2018-02-03 23:00 | 30
2018-02-04 | 31
2018-02-04 01:00 | 31
2018-02-04 02:00 | 30
2018-02-04 03:00 | 32
2018-02-04 04:00 | 32
2018-02-04 05:00 | 34
2018-02-04 06:00 | 34
2018-02-04 07:00 | 34
2018-02-04 08:00 | 36
2018-02-04 09:00 | 37
2018-02-04 10:00 | 38
2018-02-04 11:00 | 39
2018-02-04 12:00 | 43
2018-02-04 13:00 | 42
2018-02-04 14:00 | 39
2018-02-04 15:00 | 41
2018-02-04 16:00 | 38
2018-02-04 17:00 | 37
2018-02-04 18:00 | 37
2018-02-04 19:00 | 45
2018-02-04 20:00 | 46
2018-02-04 21:00 | 46
2018-02-04 22:00 | 45
2018-02-04 23:00 | 39
2018-02-05 | 40
2018-02-05 01:00 | 41
2018-02-05 02:00 | 41
2018-02-05 03:00 | 39
2018-02-05 04:00 | 39
2018-02-05 05:00 | 39
2018-02-05 06:00 | 39
2018-02-05 07:00 | 40
2018-02-05 08:00 | 39
2018-02-05 09:00 | 36
2018-02-05 10:00 | 32
2018-02-05 11:00 | 30
2018-02-05 12:00 | 32
2018-02-05 13:00 | 31
2018-02-05 14:00 | 32
2018-02-05 15:00 | 32
2018-02-05 16:00 | 33
2018-02-05 17:00 | 32
2018-02-05 18:00 | 30
2018-02-05 19:00 | 30
2018-02-05 20:00 | 28
2018-02-05 21:00 | 28
2018-02-05 22:00 | 28
2018-02-05 23:00 | 28
2018-02-06 | 28
2018-02-06 01:00 | 28
2018-02-06 02:00 | 25
2018-02-06 03:00 | 25
2018-02-06 04:00 | 28
2018-02-06 05:00 | 28
2018-02-06 06:00 | 29
2018-02-06 07:00 | 30
2018-02-06 08:00 | 31
2018-02-06 09:00 | 32
2018-02-06 10:00 | 32
2018-02-06 11:00 | 34
2018-02-06 12:00 | 36
2018-02-06 13:00 | 37
2018-02-06 14:00 | 37
2018-02-06 15:00 | 37
2018-02-06 16:00 | 38
2018-02-06 17:00 | 37
2018-02-06 18:00 | 36
2018-02-06 19:00 | 36
2018-02-06 20:00 | 36
2018-02-06 21:00 | 36
2018-02-06 22:00 | 35
2018-02-06 23:00 | 34
2018-02-07 | 33
2018-02-07 01:00 | 32
2018-02-07 02:00 | 30
2018-02-07 03:00 | 30
2018-02-07 04:00 | 30
2018-02-07 05:00 | 30
2018-02-07 06:00 | 30
2018-02-07 07:00 | 32
2018-02-07 08:00 | 30
2018-02-07 09:00 | 30
2018-02-07 10:00 | 31
2018-02-07 11:00 | 31
2018-02-07 12:00 | 30
2018-02-07 13:00 | 33
2018-02-07 14:00 | 33
2018-02-07 15:00 | 34
2018-02-07 16:00 | 34
2018-02-07 17:00 | 39
2018-02-07 18:00 | 39
2018-02-07 19:00 | 46
2018-02-07 20:00 | 43
2018-02-07 21:00 | 41
2018-02-07 22:00 | 39
2018-02-07 23:00 | 36
2018-02-08 | 34
2018-02-08 01:00 | 33
2018-02-08 02:00 | 32
2018-02-08 03:00 | 31
2018-02-08 04:00 | 30
2018-02-08 05:00 | 30
2018-02-08 06:00 | 29
2018-02-08 07:00 | 27
2018-02-08 08:00 | 27
2018-02-08 09:00 | 27
2018-02-08 10:00 | 29
2018-02-08 11:00 | 30
2018-02-08 12:00 | 31
2018-02-08 13:00 | 32
2018-02-08 14:00 | 32
2018-02-08 15:00 | 32
2018-02-08 16:00 | 33
2018-02-08 17:00 | 31
2018-02-08 18:00 | 31
2018-02-08 19:00 | 31
2018-02-08 20:00 | 30
2018-02-08 21:00 | 30
2018-02-08 22:00 | 30
2018-02-08 23:00 | 30
2018-02-09 | 29
2018-02-09 01:00 | 29
2018-02-09 02:00 | 29
2018-02-09 03:00 | 28
2018-02-09 04:00 | 29
2018-02-09 05:00 | 29
2018-02-09 06:00 | 28
2018-02-09 07:00 | 28
2018-02-09 08:00 | 29
2018-02-09 09:00 | 31
2018-02-09 10:00 | 31
2018-02-09 11:00 | 33
2018-02-09 12:00 | 33
2018-02-09 13:00 | 33
2018-02-09 14:00 | 34
2018-02-09 15:00 | 33
2018-02-09 16:00 | 33
2018-02-09 17:00 | 35
2018-02-09 18:00 | 35
2018-02-09 19:00 | 36
2018-02-09 20:00 | 36
2018-02-09 21:00 | 37
2018-02-09 22:00 | 38
2018-02-09 23:00 | 39
2018-02-10 | 39
2018-02-10 01:00 | 39
2018-02-10 02:00 | 40
2018-02-10 03:00 | 40
2018-02-10 04:00 | 40
2018-02-10 05:00 | 40
2018-02-10 06:00 | 40
2018-02-10 07:00 | 41
2018-02-10 08:00 | 42
2018-02-10 09:00 | 45
2018-02-10 10:00 | 48
2018-02-10 11:00 | 49
2018-02-10 12:00 | 50
2018-02-10 13:00 | 51
2018-02-10 14:00 | 43
2018-02-10 15:00 | 44
2018-02-10 16:00 | 45
2018-02-10 17:00 | 44
2018-02-10 18:00 | 43
2018-02-10 19:00 | 43
2018-02-10 20:00 | 42
2018-02-10 21:00 | 42
2018-02-10 22:00 | 43
2018-02-10 23:00 | 42
2018-02-11 | 46
2018-02-11 01:00 | 45
2018-02-11 02:00 | 44
2018-02-11 03:00 | 44
2018-02-11 04:00 | 46
2018-02-11 05:00 | 42
2018-02-11 06:00 | 43
2018-02-11 07:00 | 45
2018-02-11 08:00 | 44
2018-02-11 09:00 | 44
2018-02-11 10:00 | 44
2018-02-11 11:00 | 43
2018-02-11 12:00 | 46
2018-02-11 13:00 | 42
2018-02-11 14:00 | 44
2018-02-11 15:00 | 51
2018-02-11 16:00 | 51
2018-02-11 17:00 | 58
2018-02-11 18:00 | 55
2018-02-11 19:00 | 50
2018-02-11 20:00 | 53
2018-02-11 21:00 | 51
2018-02-11 22:00 | 51
2018-02-11 23:00 | 51
2018-02-12 | 53
2018-02-12 01:00 | 52
2018-02-12 02:00 | 62
2018-02-12 03:00 | 60
2018-02-12 04:00 | 59
2018-02-12 05:00 | 52
2018-02-12 06:00 | 46
2018-02-12 07:00 | 44
2018-02-12 08:00 | 42
2018-02-12 09:00 | 42
2018-02-12 10:00 | 42
2018-02-12 11:00 | 42
2018-02-12 12:00 | 41
2018-02-12 13:00 | 41
2018-02-12 14:00 | 42
2018-02-12 15:00 | 44
2018-02-12 16:00 | 45
2018-02-12 17:00 | 44
2018-02-12 18:00 | 43
2018-02-12 19:00 | 41
2018-02-12 20:00 | 40
2018-02-12 21:00 | 38
2018-02-12 22:00 | 36
2018-02-12 23:00 | 35
2018-02-13 | 34
2018-02-13 01:00 | 33
2018-02-13 02:00 | 32
2018-02-13 03:00 | 31
2018-02-13 04:00 | 30
2018-02-13 05:00 | 29
2018-02-13 06:00 | 28
2018-02-13 07:00 | 27
2018-02-13 08:00 | 27
2018-02-13 09:00 | 29
2018-02-13 10:00 | 30
2018-02-13 11:00 | 31
2018-02-13 12:00 | 33
2018-02-13 13:00 | 34
2018-02-13 14:00 | 35
2018-02-13 15:00 | 36
2018-02-13 16:00 | 37
2018-02-13 17:00 | 34
2018-02-13 18:00 | 33
2018-02-13 19:00 | 33
2018-02-13 20:00 | 33
2018-02-13 21:00 | 34
2018-02-13 22:00 | 35
2018-02-13 23:00 | 36
2018-02-14 | 36
2018-02-14 01:00 | 36
2018-02-14 02:00 | 36
2018-02-14 03:00 | 37
2018-02-14 04:00 | 37
2018-02-14 05:00 | 36
2018-02-14 06:00 | 37
2018-02-14 07:00 | 38
2018-02-14 08:00 | 39
2018-02-14 09:00 | 39
2018-02-14 10:00 | 40
2018-02-14 11:00 | 43
2018-02-14 12:00 | 45
2018-02-14 13:00 | 47
2018-02-14 14:00 | 49
2018-02-14 15:00 | 52
2018-02-14 16:00 | 53
2018-02-14 17:00 | 50
2018-02-14 18:00 | 52
2018-02-14 19:00 | 49
2018-02-14 20:00 | 49
2018-02-14 21:00 | 50
2018-02-14 22:00 | 50
2018-02-14 23:00 | 49
2018-02-15 | 48
2018-02-15 01:00 | 48
2018-02-15 02:00 | 48
2018-02-15 03:00 | 47
2018-02-15 04:00 | 47
2018-02-15 05:00 | 47
2018-02-15 06:00 | 48
2018-02-15 07:00 | 48
2018-02-15 08:00 | 48
2018-02-15 09:00 | 49
2018-02-15 10:00 | 51
2018-02-15 11:00 | 52
2018-02-15 12:00 | 53
2018-02-15 13:00 | 54
2018-02-15 14:00 | 56
2018-02-15 15:00 | 57
2018-02-15 16:00 | 58
2018-02-15 17:00 | 59
2018-02-15 18:00 | 60
2018-02-15 19:00 | 58
2018-02-15 20:00 | 59
2018-02-15 21:00 | 60
2018-02-15 22:00 | 60
2018-02-15 23:00 | 58
2018-02-16 | 58
2018-02-16 01:00 | 57
2018-02-16 02:00 | 57
2018-02-16 03:00 | 57
2018-02-16 04:00 | 57
2018-02-16 05:00 | 59
2018-02-16 06:00 | 58
2018-02-16 07:00 | 55
2018-02-16 08:00 | 52
2018-02-16 09:00 | 53
2018-02-16 10:00 | 57
2018-02-16 11:00 | 57
2018-02-16 12:00 | 58
2018-02-16 13:00 | 58
2018-02-16 14:00 | 59
2018-02-16 15:00 | 53
2018-02-16 16:00 | 51
2018-02-16 17:00 | 47
2018-02-16 18:00 | 46
2018-02-16 19:00 | 44
2018-02-16 20:00 | 42
2018-02-16 21:00 | 41
2018-02-16 22:00 | 40
2018-02-16 23:00 | 39
2018-02-17 | 37
2018-02-17 01:00 | 36
2018-02-17 02:00 | 34
2018-02-17 03:00 | 33
2018-02-17 04:00 | 32
2018-02-17 05:00 | 31
2018-02-17 06:00 | 31
2018-02-17 07:00 | 30
2018-02-17 08:00 | 32
2018-02-17 09:00 | 33
2018-02-17 10:00 | 34
2018-02-17 11:00 | 35
2018-02-17 12:00 | 36
2018-02-17 13:00 | 39
2018-02-17 14:00 | 38
2018-02-17 15:00 | 38
2018-02-17 16:00 | 38
2018-02-17 17:00 | 38
2018-02-17 18:00 | 34
2018-02-17 19:00 | 33
2018-02-17 20:00 | 33
2018-02-17 21:00 | 33
2018-02-17 22:00 | 33
2018-02-17 23:00 | 33
2018-02-18 | 33
2018-02-18 01:00 | 33
2018-02-18 02:00 | 34
2018-02-18 03:00 | 34
2018-02-18 04:00 | 35
2018-02-18 05:00 | 36
2018-02-18 06:00 | 36
2018-02-18 07:00 | 36
2018-02-18 08:00 | 37
2018-02-18 09:00 | 38
2018-02-18 10:00 | 39
2018-02-18 11:00 | 41
2018-02-18 12:00 | 43
2018-02-18 13:00 | 44
2018-02-18 14:00 | 45
2018-02-18 15:00 | 44
2018-02-18 16:00 | 44
2018-02-18 17:00 | 44
2018-02-18 18:00 | 43
2018-02-18 19:00 | 43
2018-02-18 20:00 | 40
2018-02-18 21:00 | 40
2018-02-18 22:00 | 38
2018-02-18 23:00 | 38
2018-02-19 | 36
2018-02-19 01:00 | 34
2018-02-19 02:00 | 34
2018-02-19 03:00 | 36
2018-02-19 04:00 | 36
2018-02-19 05:00 | 36
2018-02-19 06:00 | 37
2018-02-19 07:00 | 39
2018-02-19 08:00 | 40
2018-02-19 09:00 | 43
2018-02-19 10:00 | 45
2018-02-19 11:00 | 47
2018-02-19 12:00 | 47
2018-02-19 13:00 | 48
2018-02-19 14:00 | 48
2018-02-19 15:00 | 48
2018-02-19 16:00 | 49
2018-02-19 17:00 | 48
2018-02-19 18:00 | 48
2018-02-19 19:00 | 48
2018-02-19 20:00 | 47
2018-02-19 21:00 | 47
2018-02-19 22:00 | 47
2018-02-19 23:00 | 46
2018-02-20 | 47
2018-02-20 01:00 | 48
2018-02-20 02:00 | 49
2018-02-20 03:00 | 51
2018-02-20 04:00 | 51
2018-02-20 05:00 | 51
2018-02-20 06:00 | 50
2018-02-20 07:00 | 51
2018-02-20 08:00 | 52
2018-02-20 09:00 | 52
2018-02-20 10:00 | 54
2018-02-20 11:00 | 55
2018-02-20 12:00 | 58
2018-02-20 13:00 | 60
2018-02-20 14:00 | 64
2018-02-20 15:00 | 66
2018-02-20 16:00 | 67
2018-02-20 17:00 | 69
2018-02-20 18:00 | 63
2018-02-20 19:00 | 61
2018-02-20 20:00 | 59
2018-02-20 21:00 | 58
2018-02-20 22:00 | 56
2018-02-20 23:00 | 54
2018-02-21 | 53
2018-02-21 01:00 | 53
2018-02-21 02:00 | 52
2018-02-21 03:00 | 52
2018-02-21 04:00 | 50
2018-02-21 05:00 | 50
2018-02-21 06:00 | 53
2018-02-21 07:00 | 56
2018-02-21 08:00 | 58
2018-02-21 09:00 | 61
2018-02-21 10:00 | 64
2018-02-21 11:00 | 68
2018-02-21 12:00 | 70
2018-02-21 13:00 | 74
2018-02-21 14:00 | 75
2018-02-21 15:00 | 77
2018-02-21 16:00 | 78
2018-02-21 17:00 | 77
2018-02-21 18:00 | 75
2018-02-21 19:00 | 74
2018-02-21 20:00 | 67
2018-02-21 21:00 | 62
2018-02-21 22:00 | 57
2018-02-21 23:00 | 59
2018-02-22 | 58
2018-02-22 01:00 | 57
2018-02-22 02:00 | 56
2018-02-22 03:00 | 53
2018-02-22 04:00 | 51
2018-02-22 05:00 | 49
2018-02-22 06:00 | 46
2018-02-22 07:00 | 46
2018-02-22 08:00 | 47
2018-02-22 09:00 | 46
2018-02-22 10:00 | 46
2018-02-22 11:00 | 46
2018-02-22 12:00 | 46
2018-02-22 13:00 | 45
2018-02-22 14:00 | 43
2018-02-22 15:00 | 43
2018-02-22 16:00 | 41
2018-02-22 17:00 | 37
2018-02-22 18:00 | 39
2018-02-22 19:00 | 39
2018-02-22 20:00 | 39
2018-02-22 21:00 | 37
2018-02-22 22:00 | 38
2018-02-22 23:00 | 37
2018-02-23 | 37
2018-02-23 01:00 | 38
2018-02-23 02:00 | 37
2018-02-23 03:00 | 37
2018-02-23 04:00 | 37
2018-02-23 05:00 | 37
2018-02-23 06:00 | 37
2018-02-23 07:00 | 37
2018-02-23 08:00 | 37
2018-02-23 09:00 | 37
2018-02-23 10:00 | 37
2018-02-23 11:00 | 37
2018-02-23 12:00 | 37
2018-02-23 13:00 | 38
2018-02-23 14:00 | 37
2018-02-23 15:00 | 37
2018-02-23 16:00 | 38
2018-02-23 17:00 | 37
2018-02-23 18:00 | 39
2018-02-23 19:00 | 41
2018-02-23 20:00 | 41
2018-02-23 21:00 | 41
2018-02-23 22:00 | 42
2018-02-23 23:00 | 43
2018-02-24 | 44
2018-02-24 01:00 | 45
2018-02-24 02:00 | 46
2018-02-24 03:00 | 45
2018-02-24 04:00 | 45
2018-02-24 05:00 | 45
2018-02-24 06:00 | 46
2018-02-24 07:00 | 46
2018-02-24 08:00 | 46
2018-02-24 09:00 | 48
2018-02-24 10:00 | 50
2018-02-24 11:00 | 54
2018-02-24 12:00 | 54
2018-02-24 13:00 | 53
2018-02-24 14:00 | 54
2018-02-24 15:00 | 52
2018-02-24 16:00 | 48
2018-02-24 17:00 | 48
2018-02-24 18:00 | 46
2018-02-24 19:00 | 47
2018-02-24 20:00 | 46
2018-02-24 21:00 | 45
2018-02-24 22:00 | 44
2018-02-24 23:00 | 45
2018-02-25 | 43
2018-02-25 01:00 | 43
2018-02-25 02:00 | 43
2018-02-25 03:00 | 43
2018-02-25 04:00 | 42
2018-02-25 05:00 | 41
2018-02-25 06:00 | 41
2018-02-25 07:00 | 40
2018-02-25 08:00 | 41
2018-02-25 09:00 | 39
2018-02-25 10:00 | 40
2018-02-25 11:00 | 39
2018-02-25 12:00 | 41
2018-02-25 13:00 | 41
2018-02-25 14:00 | 39
2018-02-25 15:00 | 41
2018-02-25 16:00 | 42
2018-02-25 17:00 | 43
2018-02-25 18:00 | 43
2018-02-25 19:00 | 44
2018-02-25 20:00 | 45
2018-02-25 21:00 | 45
2018-02-25 22:00 | 44
2018-02-25 23:00 | 43
2018-02-26 | 44
2018-02-26 01:00 | 44
2018-02-26 02:00 | 45
2018-02-26 03:00 | 45
2018-02-26 04:00 | 45
2018-02-26 05:00 | 45
2018-02-26 06:00 | 46
2018-02-26 07:00 | 45
2018-02-26 08:00 | 45
2018-02-26 09:00 | 45
2018-02-26 10:00 | 45
2018-02-26 11:00 | 45
2018-02-26 12:00 | 46
2018-02-26 13:00 | 47
2018-02-26 14:00 | 48
2018-02-26 15:00 | 50
2018-02-26 16:00 | 52
2018-02-26 17:00 | 52
2018-02-26 18:00 | 52
2018-02-26 19:00 | 51
2018-02-26 20:00 | 52
2018-02-26 21:00 | 48
2018-02-26 22:00 | 47
2018-02-26 23:00 | 45
2018-02-27 | 45
2018-02-27 01:00 | 44
2018-02-27 02:00 | 43
2018-02-27 03:00 | 43
2018-02-27 04:00 | 41
2018-02-27 05:00 | 41
2018-02-27 06:00 | 39
2018-02-27 07:00 | 41
2018-02-27 08:00 | 43
2018-02-27 09:00 | 45
2018-02-27 10:00 | 47
2018-02-27 11:00 | 50
2018-02-27 12:00 | 52
2018-02-27 13:00 | 52
2018-02-27 14:00 | 55
2018-02-27 15:00 | 55
2018-02-27 16:00 | 57
2018-02-27 17:00 | 52
2018-02-27 18:00 | 48
2018-02-27 19:00 | 49
2018-02-27 20:00 | 48
2018-02-27 21:00 | 48
2018-02-27 22:00 | 48
2018-02-27 23:00 | 46
2018-02-28 | 46
2018-02-28 01:00 | 45
2018-02-28 02:00 | 46
2018-02-28 03:00 | 46
2018-02-28 04:00 | 46
2018-02-28 05:00 | 45
2018-02-28 06:00 | 43
2018-02-28 07:00 | 43
2018-02-28 08:00 | 43
2018-02-28 09:00 | 46
2018-02-28 10:00 | 48
2018-02-28 11:00 | 50
2018-02-28 12:00 | 52
2018-02-28 13:00 | 56
2018-02-28 14:00 | 57
2018-02-28 15:00 | 61
2018-02-28 16:00 | 61
2018-02-28 17:00 | 61
2018-02-28 18:00 | 54
2018-02-28 19:00 | 53
2018-02-28 20:00 | 54
2018-02-28 21:00 | 55
2018-02-28 22:00 | 56
2018-02-28 23:00 | 55
2018-03-01 | 56
2018-03-01 01:00 | 55
2018-03-01 02:00 | 55
2018-03-01 03:00 | 54
2018-03-01 04:00 | 53
2018-03-01 05:00 | 52
2018-03-01 06:00 | 52
2018-03-01 07:00 | 50
2018-03-01 08:00 | 54
2018-03-01 09:00 | 54
2018-03-01 10:00 | 56
2018-03-01 11:00 | 57
2018-03-01 12:00 | 57
2018-03-01 13:00 | 57
2018-03-01 14:00 | 57
2018-03-01 15:00 | 55
2018-03-01 16:00 | 53
2018-03-01 17:00 | 54
2018-03-01 18:00 | 55
2018-03-01 19:00 | 58
2018-03-01 20:00 | 54
2018-03-01 21:00 | 52
2018-03-01 22:00 | 44
2018-03-01 23:00 | 43
2018-03-02 | 44
2018-03-02 01:00 | 43
2018-03-02 02:00 | 43
2018-03-02 03:00 | 42
2018-03-02 04:00 | 43
2018-03-02 05:00 | 42
2018-03-02 06:00 | 40
2018-03-02 07:00 | 39
2018-03-02 08:00 | 37
2018-03-02 09:00 | 37
2018-03-02 10:00 | 37
2018-03-02 11:00 | 37
2018-03-02 12:00 | 37
2018-03-02 13:00 | 38
2018-03-02 14:00 | 39
2018-03-02 15:00 | 39
2018-03-02 16:00 | 38
2018-03-02 17:00 | 37
2018-03-02 18:00 | 36
2018-03-02 19:00 | 36
2018-03-02 20:00 | 37
2018-03-02 21:00 | 37
2018-03-02 22:00 | 38
2018-03-02 23:00 | 37
2018-03-03 | 38
2018-03-03 01:00 | 38
2018-03-03 02:00 | 37
2018-03-03 03:00 | 39
2018-03-03 04:00 | 39
2018-03-03 05:00 | 39
2018-03-03 06:00 | 39
2018-03-03 07:00 | 39
2018-03-03 08:00 | 39
2018-03-03 09:00 | 39
2018-03-03 10:00 | 40
2018-03-03 11:00 | 43
2018-03-03 12:00 | 45
2018-03-03 13:00 | 46
2018-03-03 14:00 | 45
2018-03-03 15:00 | 46
2018-03-03 16:00 | 46
2018-03-03 17:00 | 45
2018-03-03 18:00 | 45
2018-03-03 19:00 | 43
2018-03-03 20:00 | 43
2018-03-03 21:00 | 43
2018-03-03 22:00 | 42
2018-03-03 23:00 | 43
2018-03-04 | 42
2018-03-04 01:00 | 42
2018-03-04 02:00 | 41
2018-03-04 03:00 | 41
2018-03-04 04:00 | 41
2018-03-04 05:00 | 41
2018-03-04 06:00 | 41
2018-03-04 07:00 | 40
2018-03-04 08:00 | 41
2018-03-04 09:00 | 41
2018-03-04 10:00 | 42
2018-03-04 11:00 | 43
2018-03-04 12:00 | 45
2018-03-04 13:00 | 43
2018-03-04 14:00 | 43
2018-03-04 15:00 | 43
2018-03-04 16:00 | 43
2018-03-04 17:00 | 43
2018-03-04 18:00 | 41
2018-03-04 19:00 | 40
2018-03-04 20:00 | 37
2018-03-04 21:00 | 37
2018-03-04 22:00 | 36
2018-03-04 23:00 | 36
2018-03-05 | 35
2018-03-05 01:00 | 35
2018-03-05 02:00 | 36
2018-03-05 03:00 | 36
2018-03-05 04:00 | 35
2018-03-05 05:00 | 36
2018-03-05 06:00 | 36
2018-03-05 07:00 | 35
2018-03-05 08:00 | 36
2018-03-05 09:00 | 37
2018-03-05 10:00 | 39
2018-03-05 11:00 | 39
2018-03-05 12:00 | 39
2018-03-05 13:00 | 39
2018-03-05 14:00 | 39
2018-03-05 15:00 | 39
2018-03-05 16:00 | 41
2018-03-05 17:00 | 41
2018-03-05 18:00 | 41
2018-03-05 19:00 | 40
2018-03-05 20:00 | 39
2018-03-05 21:00 | 39
2018-03-05 22:00 | 38
2018-03-05 23:00 | 37
2018-03-06 | 37
2018-03-06 01:00 | 37
2018-03-06 02:00 | 36
2018-03-06 03:00 | 36
2018-03-06 04:00 | 35
2018-03-06 05:00 | 36
2018-03-06 06:00 | 36
2018-03-06 07:00 | 35
2018-03-06 08:00 | 37
2018-03-06 09:00 | 37
2018-03-06 10:00 | 40
2018-03-06 11:00 | 43
2018-03-06 12:00 | 43
2018-03-06 13:00 | 45
2018-03-06 14:00 | 46
2018-03-06 15:00 | 45
2018-03-06 16:00 | 45
2018-03-06 17:00 | 43
2018-03-06 18:00 | 43
2018-03-06 19:00 | 41
2018-03-06 20:00 | 41
2018-03-06 21:00 | 41
2018-03-06 22:00 | 40
2018-03-06 23:00 | 39
2018-03-07 | 39
2018-03-07 01:00 | 38
2018-03-07 02:00 | 37
2018-03-07 03:00 | 34
2018-03-07 04:00 | 34
2018-03-07 05:00 | 34
2018-03-07 06:00 | 36
2018-03-07 07:00 | 36
2018-03-07 08:00 | 36
2018-03-07 09:00 | 37
2018-03-07 10:00 | 38
2018-03-07 11:00 | 37
2018-03-07 12:00 | 36
2018-03-07 13:00 | 34
2018-03-07 14:00 | 34
2018-03-07 15:00 | 36
2018-03-07 16:00 | 34
2018-03-07 17:00 | 34
2018-03-07 18:00 | 34
2018-03-07 19:00 | 35
2018-03-07 20:00 | 35
2018-03-07 21:00 | 35
2018-03-07 22:00 | 36
2018-03-07 23:00 | 35
2018-03-08 | 36
2018-03-08 01:00 | 36
2018-03-08 02:00 | 37
2018-03-08 03:00 | 36
2018-03-08 04:00 | 36
2018-03-08 05:00 | 35
2018-03-08 06:00 | 34
2018-03-08 07:00 | 35
2018-03-08 08:00 | 37
2018-03-08 09:00 | 38
2018-03-08 10:00 | 40
2018-03-08 11:00 | 39
2018-03-08 12:00 | 41
2018-03-08 13:00 | 40
2018-03-08 14:00 | 39
2018-03-08 15:00 | 39
2018-03-08 16:00 | 40
2018-03-08 17:00 | 39
2018-03-08 18:00 | 39
2018-03-08 19:00 | 39
2018-03-08 20:00 | 37
2018-03-08 21:00 | 37
2018-03-08 22:00 | 37
2018-03-08 23:00 | 36
2018-03-09 | 35
2018-03-09 01:00 | 34
2018-03-09 02:00 | 34
2018-03-09 03:00 | 34
2018-03-09 04:00 | 32
2018-03-09 05:00 | 32
2018-03-09 06:00 | 32
2018-03-09 07:00 | 32
2018-03-09 08:00 | 32
2018-03-09 09:00 | 34
2018-03-09 10:00 | 36
2018-03-09 11:00 | 37
2018-03-09 12:00 | 39
2018-03-09 13:00 | 41
2018-03-09 14:00 | 43
2018-03-09 15:00 | 43
2018-03-09 16:00 | 44
2018-03-09 17:00 | 43
2018-03-09 18:00 | 41
2018-03-09 19:00 | 40
2018-03-09 20:00 | 39
2018-03-09 21:00 | 39
2018-03-09 22:00 | 38
2018-03-09 23:00 | 37
2018-03-10 | 36
2018-03-10 01:00 | 36
2018-03-10 02:00 | 36
2018-03-10 03:00 | 36
2018-03-10 04:00 | 34
2018-03-10 05:00 | 34
2018-03-10 06:00 | 34
2018-03-10 07:00 | 34
2018-03-10 08:00 | 34
2018-03-10 09:00 | 36
2018-03-10 10:00 | 38
2018-03-10 11:00 | 39
2018-03-10 12:00 | 39
2018-03-10 13:00 | 40
2018-03-10 14:00 | 39
2018-03-10 15:00 | 41
2018-03-10 16:00 | 40
2018-03-10 17:00 | 39
2018-03-10 18:00 | 39
2018-03-10 19:00 | 40
2018-03-10 20:00 | 39
2018-03-10 21:00 | 39
2018-03-10 22:00 | 38
2018-03-10 23:00 | 37
2018-03-11 | 37
2018-03-11 01:00 | 36
2018-03-11 03:00 | 36
2018-03-11 04:00 | 36
2018-03-11 05:00 | 35
2018-03-11 06:00 | 36
2018-03-11 07:00 | 34
2018-03-11 08:00 | 34
2018-03-11 09:00 | 36
2018-03-11 10:00 | 36
2018-03-11 11:00 | 38
2018-03-11 12:00 | 39
2018-03-11 13:00 | 41
2018-03-11 14:00 | 43
2018-03-11 15:00 | 45
2018-03-11 16:00 | 45
2018-03-11 17:00 | 45
2018-03-11 18:00 | 46
2018-03-11 19:00 | 45
2018-03-11 20:00 | 43
2018-03-11 21:00 | 43
2018-03-11 22:00 | 43
2018-03-11 23:00 | 40
2018-03-12 | 37
2018-03-12 01:00 | 37
2018-03-12 02:00 | 36
2018-03-12 03:00 | 34
2018-03-12 04:00 | 34
2018-03-12 05:00 | 33
2018-03-12 06:00 | 34
2018-03-12 07:00 | 34
2018-03-12 08:00 | 35
2018-03-12 09:00 | 36
2018-03-12 10:00 | 37
2018-03-12 11:00 | 38
2018-03-12 12:00 | 39
2018-03-12 13:00 | 41
2018-03-12 14:00 | 41
2018-03-12 15:00 | 41
2018-03-12 16:00 | 41
2018-03-12 17:00 | 41
2018-03-12 18:00 | 41
2018-03-12 19:00 | 41
2018-03-12 20:00 | 41
2018-03-12 21:00 | 43
2018-03-12 22:00 | 37
2018-03-12 23:00 | 38
2018-03-13 | 37
2018-03-13 01:00 | 37
2018-03-13 02:00 | 36
2018-03-13 03:00 | 36
2018-03-13 04:00 | 36
2018-03-13 05:00 | 35
2018-03-13 06:00 | 34
2018-03-13 07:00 | 36
2018-03-13 08:00 | 34
2018-03-13 09:00 | 36
2018-03-13 10:00 | 36
2018-03-13 11:00 | 36
2018-03-13 12:00 | 36
2018-03-13 13:00 | 36
2018-03-13 14:00 | 37
2018-03-13 15:00 | 39
2018-03-13 16:00 | 41
2018-03-13 17:00 | 41
2018-03-13 18:00 | 41
2018-03-13 19:00 | 39
2018-03-13 20:00 | 38
2018-03-13 21:00 | 37
2018-03-13 22:00 | 37
2018-03-13 23:00 | 37
2018-03-14 | 36
2018-03-14 01:00 | 35
2018-03-14 02:00 | 35
2018-03-14 03:00 | 34
2018-03-14 04:00 | 34
2018-03-14 05:00 | 33
2018-03-14 06:00 | 33
2018-03-14 07:00 | 33
2018-03-14 08:00 | 33
2018-03-14 09:00 | 34
2018-03-14 10:00 | 36
2018-03-14 11:00 | 36
2018-03-14 12:00 | 39
2018-03-14 13:00 | 39
2018-03-14 14:00 | 41
2018-03-14 15:00 | 41
2018-03-14 16:00 | 43
2018-03-14 17:00 | 41
2018-03-14 18:00 | 39
2018-03-14 19:00 | 37
2018-03-14 20:00 | 37
2018-03-14 21:00 | 36
2018-03-14 22:00 | 34
2018-03-14 23:00 | 34
2018-03-15 | 34
2018-03-15 01:00 | 35
2018-03-15 02:00 | 35
2018-03-15 03:00 | 34
2018-03-15 04:00 | 34
2018-03-15 05:00 | 34
2018-03-15 06:00 | 34
2018-03-15 07:00 | 34
2018-03-15 08:00 | 35
2018-03-15 09:00 | 36
2018-03-15 10:00 | 37
2018-03-15 11:00 | 39
2018-03-15 12:00 | 43
2018-03-15 13:00 | 45
2018-03-15 14:00 | 46
2018-03-15 15:00 | 46
2018-03-15 16:00 | 48
2018-03-15 17:00 | 48
2018-03-15 18:00 | 45
2018-03-15 19:00 | 44
2018-03-15 20:00 | 43
2018-03-15 21:00 | 41
2018-03-15 22:00 | 40
2018-03-15 23:00 | 39
2018-03-16 | 38
2018-03-16 01:00 | 38
2018-03-16 02:00 | 38
2018-03-16 03:00 | 37
2018-03-16 04:00 | 36
2018-03-16 05:00 | 36
2018-03-16 06:00 | 35
2018-03-16 07:00 | 35
2018-03-16 08:00 | 35
2018-03-16 09:00 | 36
2018-03-16 10:00 | 36
2018-03-16 11:00 | 37
2018-03-16 12:00 | 37
2018-03-16 13:00 | 37
2018-03-16 14:00 | 38
2018-03-16 15:00 | 39
2018-03-16 16:00 | 37
2018-03-16 17:00 | 38
2018-03-16 18:00 | 37
2018-03-16 19:00 | 36
2018-03-16 20:00 | 35
2018-03-16 21:00 | 36
2018-03-16 22:00 | 34
2018-03-16 23:00 | 34
2018-03-17 | 34
2018-03-17 01:00 | 32
2018-03-17 02:00 | 31
2018-03-17 03:00 | 30
2018-03-17 04:00 | 30
2018-03-17 05:00 | 30
2018-03-17 06:00 | 28
2018-03-17 07:00 | 28
2018-03-17 08:00 | 29
2018-03-17 09:00 | 30
2018-03-17 10:00 | 34
2018-03-17 11:00 | 36
2018-03-17 12:00 | 37
2018-03-17 13:00 | 43
2018-03-17 14:00 | 45
2018-03-17 15:00 | 48
2018-03-17 16:00 | 46
2018-03-17 17:00 | 48
2018-03-17 18:00 | 48
2018-03-17 19:00 | 46
2018-03-17 20:00 | 46
2018-03-17 21:00 | 45
2018-03-17 22:00 | 43
2018-03-17 23:00 | 41
2018-03-18 | 39
2018-03-18 01:00 | 37
2018-03-18 02:00 | 36
2018-03-18 03:00 | 36
2018-03-18 04:00 | 36
2018-03-18 05:00 | 33
2018-03-18 06:00 | 30
2018-03-18 07:00 | 30
2018-03-18 08:00 | 30
2018-03-18 09:00 | 30
2018-03-18 10:00 | 30
2018-03-18 11:00 | 32
2018-03-18 12:00 | 34
2018-03-18 13:00 | 36
2018-03-18 14:00 | 40
2018-03-18 15:00 | 41
2018-03-18 16:00 | 43
2018-03-18 17:00 | 43
2018-03-18 18:00 | 45
2018-03-18 19:00 | 43
2018-03-18 20:00 | 42
2018-03-18 21:00 | 43
2018-03-18 22:00 | 41
2018-03-18 23:00 | 41
2018-03-19 | 39
2018-03-19 01:00 | 39
2018-03-19 02:00 | 38
2018-03-19 03:00 | 37
2018-03-19 04:00 | 36
2018-03-19 05:00 | 34
2018-03-19 06:00 | 34
2018-03-19 07:00 | 34
2018-03-19 08:00 | 35
2018-03-19 09:00 | 36
2018-03-19 10:00 | 37
2018-03-19 11:00 | 39
2018-03-19 12:00 | 41
2018-03-19 13:00 | 41
2018-03-19 14:00 | 43
2018-03-19 15:00 | 45
2018-03-19 16:00 | 46
2018-03-19 17:00 | 46
2018-03-19 18:00 | 46
2018-03-19 19:00 | 45
2018-03-19 20:00 | 43
2018-03-19 21:00 | 43
2018-03-19 22:00 | 41
2018-03-19 23:00 | 38
2018-03-20 | 37
2018-03-20 01:00 | 37
2018-03-20 02:00 | 36
2018-03-20 03:00 | 36
2018-03-20 04:00 | 34
2018-03-20 05:00 | 32
2018-03-20 06:00 | 32
2018-03-20 07:00 | 32
2018-03-20 08:00 | 31
2018-03-20 09:00 | 34
2018-03-20 10:00 | 34
2018-03-20 11:00 | 33
2018-03-20 12:00 | 34
2018-03-20 13:00 | 36
2018-03-20 14:00 | 35
2018-03-20 15:00 | 37
2018-03-20 16:00 | 37
2018-03-20 17:00 | 38
2018-03-20 18:00 | 37
2018-03-20 19:00 | 37
2018-03-20 20:00 | 39
2018-03-20 21:00 | 37
2018-03-20 22:00 | 37
2018-03-20 23:00 | 38
2018-03-21 | 37
2018-03-21 01:00 | 38
2018-03-21 02:00 | 39
2018-03-21 03:00 | 39
2018-03-21 04:00 | 39
2018-03-21 05:00 | 39
2018-03-21 06:00 | 37
2018-03-21 07:00 | 36
2018-03-21 08:00 | 34
2018-03-21 09:00 | 34
2018-03-21 10:00 | 32
2018-03-21 11:00 | 33
2018-03-21 12:00 | 34
2018-03-21 13:00 | 34
2018-03-21 14:00 | 33
2018-03-21 15:00 | 34
2018-03-21 16:00 | 33.5
2018-03-21 17:00 | 33
2018-03-21 18:00 | 34
2018-03-21 19:00 | 34
2018-03-21 20:00 | 34
2018-03-21 21:00 | 34
2018-03-21 22:00 | 34
2018-03-21 23:00 | 33
2018-03-22 | 34
2018-03-22 01:00 | 33
2018-03-22 02:00 | 33
2018-03-22 03:00 | 34
2018-03-22 04:00 | 34
2018-03-22 05:00 | 34
2018-03-22 06:00 | 34
2018-03-22 07:00 | 36
2018-03-22 08:00 | 37
2018-03-22 09:00 | 37
2018-03-22 10:00 | 39
2018-03-22 11:00 | 42
2018-03-22 12:00 | 45
2018-03-22 13:00 | 46
2018-03-22 14:00 | 47
2018-03-22 15:00 | 48
2018-03-22 16:00 | 50
2018-03-22 17:00 | 51
2018-03-22 18:00 | 52
2018-03-22 19:00 | 48
2018-03-22 20:00 | 47
2018-03-22 21:00 | 46
2018-03-22 22:00 | 45
2018-03-22 23:00 | 43
2018-03-23 | 41
2018-03-23 01:00 | 40
2018-03-23 02:00 | 39
2018-03-23 03:00 | 39
2018-03-23 04:00 | 37
2018-03-23 05:00 | 37
2018-03-23 06:00 | 37
2018-03-23 07:00 | 37
2018-03-23 08:00 | 37
2018-03-23 09:00 | 37
2018-03-23 10:00 | 39
2018-03-23 11:00 | 42
2018-03-23 12:00 | 46
2018-03-23 13:00 | 46
2018-03-23 14:00 | 48
2018-03-23 15:00 | 50
2018-03-23 16:00 | 48
2018-03-23 17:00 | 48
2018-03-23 18:00 | 46
2018-03-23 19:00 | 46
2018-03-23 20:00 | 45
2018-03-23 21:00 | 45
2018-03-23 22:00 | 45
2018-03-23 23:00 | 43
2018-03-24 | 43
2018-03-24 01:00 | 41
2018-03-24 02:00 | 40
2018-03-24 03:00 | 39
2018-03-24 04:00 | 39
2018-03-24 05:00 | 38
2018-03-24 06:00 | 37
2018-03-24 07:00 | 37
2018-03-24 08:00 | 37
2018-03-24 09:00 | 39
2018-03-24 10:00 | 43
2018-03-24 11:00 | 44
2018-03-24 12:00 | 45
2018-03-24 13:00 | 46
2018-03-24 14:00 | 49
2018-03-24 15:00 | 50
2018-03-24 16:00 | 50
2018-03-24 17:00 | 50
2018-03-24 18:00 | 48
2018-03-24 19:00 | 48
2018-03-24 20:00 | 47
2018-03-24 21:00 | 46
2018-03-24 22:00 | 45
2018-03-24 23:00 | 43
2018-03-25 | 41
2018-03-25 01:00 | 40
2018-03-25 02:00 | 38
2018-03-25 03:00 | 37
2018-03-25 04:00 | 36
2018-03-25 05:00 | 35
2018-03-25 06:00 | 36
2018-03-25 07:00 | 36
2018-03-25 08:00 | 35
2018-03-25 09:00 | 37
2018-03-25 10:00 | 39
2018-03-25 11:00 | 40
2018-03-25 12:00 | 43
2018-03-25 13:00 | 41
2018-03-25 14:00 | 42
2018-03-25 15:00 | 43
2018-03-25 16:00 | 43
2018-03-25 17:00 | 43
2018-03-25 18:00 | 43
2018-03-25 19:00 | 43
2018-03-25 20:00 | 42
2018-03-25 21:00 | 41
2018-03-25 22:00 | 41
2018-03-25 23:00 | 39
2018-03-26 | 37
2018-03-26 01:00 | 37
2018-03-26 02:00 | 37
2018-03-26 03:00 | 36
2018-03-26 04:00 | 35.5
2018-03-26 05:00 | 35
2018-03-26 06:00 | 34
2018-03-26 07:00 | 34
2018-03-26 08:00 | 36
2018-03-26 09:00 | 39
2018-03-26 10:00 | 39
2018-03-26 11:00 | 41
2018-03-26 12:00 | 42
2018-03-26 13:00 | 44
2018-03-26 14:00 | 46
2018-03-26 15:00 | 48
2018-03-26 16:00 | 48
2018-03-26 17:00 | 49
2018-03-26 18:00 | 45
2018-03-26 19:00 | 42
2018-03-26 20:00 | 41
2018-03-26 21:00 | 40
2018-03-26 22:00 | 40
2018-03-26 23:00 | 39
2018-03-27 | 38
2018-03-27 01:00 | 38
2018-03-27 02:00 | 38
2018-03-27 03:00 | 37
2018-03-27 04:00 | 37
2018-03-27 05:00 | 35
2018-03-27 06:00 | 35
2018-03-27 07:00 | 36
2018-03-27 08:00 | 36
2018-03-27 09:00 | 37
2018-03-27 10:00 | 39
2018-03-27 11:00 | 40
2018-03-27 12:00 | 39
2018-03-27 13:00 | 43
2018-03-27 14:00 | 44
2018-03-27 15:00 | 45
2018-03-27 16:00 | 43
2018-03-27 17:00 | 42
2018-03-27 18:00 | 43
2018-03-27 19:00 | 41
2018-03-27 20:00 | 41
2018-03-27 21:00 | 43
2018-03-27 22:00 | 43
2018-03-27 23:00 | 41
2018-03-28 | 41
2018-03-28 01:00 | 40
2018-03-28 02:00 | 39
2018-03-28 03:00 | 39
2018-03-28 04:00 | 39
2018-03-28 05:00 | 40
2018-03-28 06:00 | 39
2018-03-28 07:00 | 39
2018-03-28 08:00 | 41
2018-03-28 09:00 | 43
2018-03-28 10:00 | 43
2018-03-28 11:00 | 44
2018-03-28 12:00 | 45
2018-03-28 13:00 | 46
2018-03-28 14:00 | 49
2018-03-28 15:00 | 50
2018-03-28 16:00 | 52
2018-03-28 17:00 | 52
2018-03-28 18:00 | 52
2018-03-28 19:00 | 50
2018-03-28 20:00 | 49
2018-03-28 21:00 | 48
2018-03-28 22:00 | 48
2018-03-28 23:00 | 50
2018-03-29 | 50
2018-03-29 01:00 | 50
2018-03-29 02:00 | 48
2018-03-29 03:00 | 50
2018-03-29 04:00 | 49
2018-03-29 05:00 | 50
2018-03-29 06:00 | 50
2018-03-29 07:00 | 51
2018-03-29 08:00 | 50
2018-03-29 09:00 | 48
2018-03-29 10:00 | 46
2018-03-29 11:00 | 50
2018-03-29 12:00 | 52
2018-03-29 13:00 | 52
2018-03-29 14:00 | 51
2018-03-29 15:00 | 50
2018-03-29 16:00 | 52
2018-03-29 17:00 | 50
2018-03-29 18:00 | 50
2018-03-29 19:00 | 46
2018-03-29 20:00 | 48
2018-03-29 21:00 | 49
2018-03-29 22:00 | 49
2018-03-29 23:00 | 49
2018-03-30 | 48
2018-03-30 01:00 | 48
2018-03-30 02:00 | 44
2018-03-30 03:00 | 43
2018-03-30 04:00 | 44
2018-03-30 05:00 | 44
2018-03-30 06:00 | 45
2018-03-30 07:00 | 49
2018-03-30 08:00 | 53
2018-03-30 09:00 | 51
2018-03-30 10:00 | 53
2018-03-30 11:00 | 54
2018-03-30 12:00 | 53
2018-03-30 13:00 | 54
2018-03-30 14:00 | 55
2018-03-30 15:00 | 57
2018-03-30 16:00 | 55
2018-03-30 17:00 | 54
2018-03-30 18:00 | 52
2018-03-30 19:00 | 50
2018-03-30 20:00 | 50
2018-03-30 21:00 | 48
2018-03-30 22:00 | 48
2018-03-30 23:00 | 47
2018-03-31 | 46
2018-03-31 01:00 | 45
2018-03-31 02:00 | 44
2018-03-31 03:00 | 43
2018-03-31 04:00 | 43
2018-03-31 05:00 | 41
2018-03-31 06:00 | 41
2018-03-31 07:00 | 39
2018-03-31 08:00 | 41
2018-03-31 09:00 | 43
2018-03-31 10:00 | 45
2018-03-31 11:00 | 48
2018-03-31 12:00 | 50
2018-03-31 13:00 | 54
2018-03-31 14:00 | 55
2018-03-31 15:00 | 55
2018-03-31 16:00 | 55
2018-03-31 17:00 | 51
2018-03-31 18:00 | 48
2018-03-31 19:00 | 48
2018-03-31 20:00 | 47
2018-03-31 21:00 | 46
2018-03-31 22:00 | 46
2018-03-31 23:00 | 47
2018-04-01 | 46
2018-04-01 01:00 | 44
2018-04-01 02:00 | 44
2018-04-01 03:00 | 46
2018-04-01 04:00 | 46
2018-04-01 05:00 | 47
2018-04-01 06:00 | 46
2018-04-01 07:00 | 48
2018-04-01 08:00 | 49
2018-04-01 09:00 | 52
2018-04-01 10:00 | 54
2018-04-01 11:00 | 56
2018-04-01 12:00 | 57
2018-04-01 13:00 | 57
2018-04-01 14:00 | 57
2018-04-01 15:00 | 55
2018-04-01 16:00 | 55
2018-04-01 17:00 | 54
2018-04-01 18:00 | 54
2018-04-01 19:00 | 54
2018-04-01 20:00 | 50
2018-04-01 21:00 | 48
2018-04-01 22:00 | 46
2018-04-01 23:00 | 46
2018-04-02 | 45
2018-04-02 01:00 | 43
2018-04-02 02:00 | 43
2018-04-02 03:00 | 43
2018-04-02 04:00 | 41
2018-04-02 05:00 | 36
2018-04-02 06:00 | 34
2018-04-02 07:00 | 32
2018-04-02 08:00 | 32
2018-04-02 09:00 | 34
2018-04-02 10:00 | 34
2018-04-02 11:00 | 35
2018-04-02 12:00 | 36
2018-04-02 13:00 | 37
2018-04-02 14:00 | 37
2018-04-02 15:00 | 37
2018-04-02 16:00 | 43
2018-04-02 17:00 | 41
2018-04-02 18:00 | 43
2018-04-02 19:00 | 43
2018-04-02 20:00 | 42
2018-04-02 21:00 | 43
2018-04-02 22:00 | 41
2018-04-02 23:00 | 40
2018-04-03 | 39
2018-04-03 01:00 | 39
2018-04-03 02:00 | 39
2018-04-03 03:00 | 39
2018-04-03 04:00 | 39
2018-04-03 05:00 | 39
2018-04-03 06:00 | 39
2018-04-03 07:00 | 39
2018-04-03 08:00 | 41
2018-04-03 09:00 | 43
2018-04-03 10:00 | 43
2018-04-03 11:00 | 43
2018-04-03 12:00 | 43
2018-04-03 13:00 | 41
2018-04-03 14:00 | 41
2018-04-03 15:00 | 41
2018-04-03 16:00 | 43
2018-04-03 17:00 | 42
2018-04-03 18:00 | 41
2018-04-03 19:00 | 41
2018-04-03 20:00 | 41
2018-04-03 21:00 | 41
2018-04-03 22:00 | 41
2018-04-03 23:00 | 41
2018-04-04 | 41
2018-04-04 01:00 | 41
2018-04-04 02:00 | 41
2018-04-04 03:00 | 41
2018-04-04 04:00 | 41
2018-04-04 05:00 | 42
2018-04-04 06:00 | 43
2018-04-04 07:00 | 45
2018-04-04 08:00 | 42
2018-04-04 09:00 | 43
2018-04-04 10:00 | 43
2018-04-04 11:00 | 45
2018-04-04 12:00 | 50
2018-04-04 13:00 | 54
2018-04-04 14:00 | 55
2018-04-04 15:00 | 55
2018-04-04 16:00 | 55
2018-04-04 17:00 | 56
2018-04-04 18:00 | 55
2018-04-04 19:00 | 52
2018-04-04 20:00 | 50
2018-04-04 21:00 | 48
2018-04-04 22:00 | 46
2018-04-04 23:00 | 45
2018-04-05 | 45
2018-04-05 01:00 | 42
2018-04-05 02:00 | 41
2018-04-05 03:00 | 39
2018-04-05 04:00 | 37
2018-04-05 05:00 | 37
2018-04-05 06:00 | 36
2018-04-05 07:00 | 36
2018-04-05 08:00 | 35
2018-04-05 09:00 | 36
2018-04-05 10:00 | 37
2018-04-05 11:00 | 38
2018-04-05 12:00 | 41
2018-04-05 13:00 | 43
2018-04-05 14:00 | 44
2018-04-05 15:00 | 45
2018-04-05 16:00 | 45
2018-04-05 17:00 | 45
2018-04-05 18:00 | 45
2018-04-05 19:00 | 45
2018-04-05 20:00 | 43
2018-04-05 21:00 | 43
2018-04-05 22:00 | 43
2018-04-05 23:00 | 42
2018-04-06 | 41
2018-04-06 01:00 | 40
2018-04-06 02:00 | 39
2018-04-06 03:00 | 37
2018-04-06 04:00 | 37
2018-04-06 05:00 | 38
2018-04-06 06:00 | 37
2018-04-06 07:00 | 37
2018-04-06 08:00 | 40
2018-04-06 09:00 | 39
2018-04-06 10:00 | 39
2018-04-06 11:00 | 41
2018-04-06 12:00 | 43
2018-04-06 13:00 | 46
2018-04-06 14:00 | 50
2018-04-06 15:00 | 55
2018-04-06 16:00 | 57
2018-04-06 17:00 | 61
2018-04-06 18:00 | 63
2018-04-06 19:00 | 61
2018-04-06 20:00 | 57
2018-04-06 21:00 | 55
2018-04-06 22:00 | 52
2018-04-06 23:00 | 51
2018-04-07 | 48
2018-04-07 01:00 | 49
2018-04-07 02:00 | 47
2018-04-07 03:00 | 46
2018-04-07 04:00 | 45
2018-04-07 05:00 | 44
2018-04-07 06:00 | 43
2018-04-07 07:00 | 43
2018-04-07 08:00 | 41
2018-04-07 09:00 | 39
2018-04-07 10:00 | 39
2018-04-07 11:00 | 40
2018-04-07 12:00 | 41
2018-04-07 13:00 | 43
2018-04-07 14:00 | 43
2018-04-07 15:00 | 45
2018-04-07 16:00 | 46
2018-04-07 17:00 | 47
2018-04-07 18:00 | 48
2018-04-07 19:00 | 46
2018-04-07 20:00 | 45
2018-04-07 21:00 | 45
2018-04-07 22:00 | 43
2018-04-07 23:00 | 41
2018-04-08 | 39
2018-04-08 01:00 | 38
2018-04-08 02:00 | 36
2018-04-08 03:00 | 36
2018-04-08 04:00 | 34
2018-04-08 05:00 | 34
2018-04-08 06:00 | 34
2018-04-08 07:00 | 34
2018-04-08 08:00 | 33
2018-04-08 09:00 | 36
2018-04-08 10:00 | 36
2018-04-08 11:00 | 38
2018-04-08 12:00 | 39
2018-04-08 13:00 | 43
2018-04-08 14:00 | 42
2018-04-08 15:00 | 43
2018-04-08 16:00 | 45
2018-04-08 17:00 | 43
2018-04-08 18:00 | 41
2018-04-08 19:00 | 41
2018-04-08 20:00 | 41
2018-04-08 21:00 | 39
2018-04-08 22:00 | 37
2018-04-08 23:00 | 37
2018-04-09 | 36
2018-04-09 01:00 | 35
2018-04-09 02:00 | 35
2018-04-09 03:00 | 34
2018-04-09 04:00 | 34
2018-04-09 05:00 | 34
2018-04-09 06:00 | 34
2018-04-09 07:00 | 34
2018-04-09 08:00 | 34
2018-04-09 09:00 | 36
2018-04-09 10:00 | 37
2018-04-09 11:00 | 39
2018-04-09 12:00 | 41
2018-04-09 13:00 | 43
2018-04-09 14:00 | 45
2018-04-09 15:00 | 46
2018-04-09 16:00 | 48
2018-04-09 17:00 | 46
2018-04-09 18:00 | 43
2018-04-09 19:00 | 41
2018-04-09 20:00 | 41
2018-04-09 21:00 | 43
2018-04-09 22:00 | 43
2018-04-09 23:00 | 43
2018-04-10 | 43
2018-04-10 01:00 | 42
2018-04-10 02:00 | 41
2018-04-10 03:00 | 39
2018-04-10 04:00 | 39
2018-04-10 05:00 | 40
2018-04-10 06:00 | 39
2018-04-10 07:00 | 39
2018-04-10 08:00 | 40
2018-04-10 09:00 | 39
2018-04-10 10:00 | 39
2018-04-10 11:00 | 42
2018-04-10 12:00 | 45
2018-04-10 13:00 | 45
2018-04-10 14:00 | 47
2018-04-10 15:00 | 48
2018-04-10 16:00 | 50
2018-04-10 17:00 | 49
2018-04-10 18:00 | 50
2018-04-10 19:00 | 48
2018-04-10 20:00 | 47
2018-04-10 21:00 | 45
2018-04-10 22:00 | 45
2018-04-10 23:00 | 43
2018-04-11 | 42.5
2018-04-11 01:00 | 42
2018-04-11 02:00 | 41
2018-04-11 03:00 | 38
2018-04-11 04:00 | 37
2018-04-11 05:00 | 39
2018-04-11 06:00 | 39
2018-04-11 07:00 | 39
2018-04-11 08:00 | 40
2018-04-11 09:00 | 43
2018-04-11 10:00 | 45
2018-04-11 11:00 | 46
2018-04-11 12:00 | 48
2018-04-11 13:00 | 50
2018-04-11 14:00 | 49
2018-04-11 15:00 | 50
2018-04-11 16:00 | 50
2018-04-11 17:00 | 49
2018-04-11 18:00 | 48
2018-04-11 19:00 | 46
2018-04-11 20:00 | 46
2018-04-11 21:00 | 46
2018-04-11 22:00 | 46
2018-04-11 23:00 | 46
2018-04-12 | 46
2018-04-12 01:00 | 46
2018-04-12 02:00 | 46
2018-04-12 03:00 | 46
2018-04-12 04:00 | 46
2018-04-12 05:00 | 47
2018-04-12 06:00 | 46
2018-04-12 07:00 | 46
2018-04-12 08:00 | 48
2018-04-12 09:00 | 50
2018-04-12 10:00 | 52
2018-04-12 11:00 | 55
2018-04-12 12:00 | 55
2018-04-12 13:00 | 57
2018-04-12 14:00 | 60
2018-04-12 15:00 | 59
2018-04-12 16:00 | 57
2018-04-12 17:00 | 55
2018-04-12 18:00 | 54
2018-04-12 19:00 | 55
2018-04-12 20:00 | 55
2018-04-12 21:00 | 55
2018-04-12 22:00 | 55
2018-04-12 23:00 | 54
2018-04-13 | 54
2018-04-13 01:00 | 58
2018-04-13 02:00 | 60
2018-04-13 03:00 | 61
2018-04-13 04:00 | 61
2018-04-13 05:00 | 61
2018-04-13 06:00 | 63
2018-04-13 07:00 | 63
2018-04-13 08:00 | 64
2018-04-13 09:00 | 64
2018-04-13 10:00 | 66
2018-04-13 11:00 | 69
2018-04-13 12:00 | 73
2018-04-13 13:00 | 75
2018-04-13 14:00 | 78
2018-04-13 15:00 | 81
2018-04-13 16:00 | 82
2018-04-13 17:00 | 78
2018-04-13 18:00 | 72
2018-04-13 19:00 | 66
2018-04-13 20:00 | 63
2018-04-13 21:00 | 64
2018-04-13 22:00 | 66
2018-04-13 23:00 | 64
2018-04-14 | 61
2018-04-14 01:00 | 61
2018-04-14 02:00 | 61
2018-04-14 03:00 | 63
2018-04-14 04:00 | 63
2018-04-14 05:00 | 60
2018-04-14 06:00 | 57
2018-04-14 07:00 | 57
2018-04-14 08:00 | 61
2018-04-14 09:00 | 63
2018-04-14 10:00 | 61
2018-04-14 11:00 | 65
2018-04-14 12:00 | 66
2018-04-14 13:00 | 66
2018-04-14 14:00 | 68
2018-04-14 15:00 | 66
2018-04-14 16:00 | 61
2018-04-14 17:00 | 55
2018-04-14 18:00 | 54
2018-04-14 19:00 | 52
2018-04-14 20:00 | 55
2018-04-14 21:00 | 52
2018-04-14 22:00 | 52
2018-04-14 23:00 | 50
2018-04-15 | 46
2018-04-15 01:00 | 46
2018-04-15 02:00 | 45
2018-04-15 03:00 | 43
2018-04-15 04:00 | 43
2018-04-15 05:00 | 43
2018-04-15 06:00 | 43
2018-04-15 07:00 | 43
2018-04-15 08:00 | 43
2018-04-15 09:00 | 43
2018-04-15 10:00 | 43
2018-04-15 11:00 | 42
2018-04-15 12:00 | 43
2018-04-15 13:00 | 43
2018-04-15 14:00 | 44
2018-04-15 15:00 | 43
2018-04-15 16:00 | 43
2018-04-15 17:00 | 42
2018-04-15 18:00 | 39
2018-04-15 19:00 | 39
2018-04-15 20:00 | 39
2018-04-15 21:00 | 39
2018-04-15 22:00 | 39
2018-04-15 23:00 | 40
2018-04-16 | 39
2018-04-16 01:00 | 40
2018-04-16 02:00 | 41
2018-04-16 03:00 | 41
2018-04-16 04:00 | 41
2018-04-16 05:00 | 41
2018-04-16 06:00 | 43
2018-04-16 07:00 | 43
2018-04-16 08:00 | 44
2018-04-16 09:00 | 45
2018-04-16 10:00 | 45
2018-04-16 11:00 | 53
2018-04-16 12:00 | 61
2018-04-16 13:00 | 61
2018-04-16 14:00 | 57
2018-04-16 15:00 | 57
2018-04-16 16:00 | 57
2018-04-16 17:00 | 54
2018-04-16 18:00 | 54
2018-04-16 19:00 | 55
2018-04-16 20:00 | 53
2018-04-16 21:00 | 52
2018-04-16 22:00 | 50
2018-04-16 23:00 | 49
2018-04-17 | 48
2018-04-17 01:00 | 47
2018-04-17 02:00 | 47
2018-04-17 03:00 | 46
2018-04-17 04:00 | 45
2018-04-17 05:00 | 43
2018-04-17 06:00 | 43
2018-04-17 07:00 | 43
2018-04-17 08:00 | 42
2018-04-17 09:00 | 43
2018-04-17 10:00 | 45
2018-04-17 11:00 | 46
2018-04-17 12:00 | 46
2018-04-17 13:00 | 46
2018-04-17 14:00 | 47
2018-04-17 15:00 | 46
2018-04-17 16:00 | 46
2018-04-17 17:00 | 46
2018-04-17 18:00 | 45
2018-04-17 19:00 | 45
2018-04-17 20:00 | 42
2018-04-17 21:00 | 43
2018-04-17 22:00 | 43
2018-04-17 23:00 | 42
2018-04-18 | 43
2018-04-18 01:00 | 41
2018-04-18 02:00 | 40
2018-04-18 03:00 | 39
2018-04-18 04:00 | 39
2018-04-18 05:00 | 39
2018-04-18 06:00 | 39
2018-04-18 07:00 | 39
2018-04-18 08:00 | 40
2018-04-18 09:00 | 43
2018-04-18 10:00 | 43
2018-04-18 11:00 | 45
2018-04-18 12:00 | 48
2018-04-18 13:00 | 50
2018-04-18 14:00 | 50
2018-04-18 15:00 | 52
2018-04-18 16:00 | 54
2018-04-18 17:00 | 54
2018-04-18 18:00 | 54
2018-04-18 19:00 | 54
2018-04-18 20:00 | 53
2018-04-18 21:00 | 52
2018-04-18 22:00 | 52
2018-04-18 23:00 | 50
2018-04-19 | 48
2018-04-19 01:00 | 48
2018-04-19 02:00 | 47
2018-04-19 03:00 | 46
2018-04-19 04:00 | 45
2018-04-19 05:00 | 44
2018-04-19 06:00 | 45
2018-04-19 07:00 | 43
2018-04-19 08:00 | 42
2018-04-19 09:00 | 46
2018-04-19 10:00 | 45
2018-04-19 11:00 | 44
2018-04-19 12:00 | 45
2018-04-19 13:00 | 45
2018-04-19 14:00 | 44
2018-04-19 15:00 | 43
2018-04-19 16:00 | 45
2018-04-19 17:00 | 47
2018-04-19 18:00 | 46
2018-04-19 19:00 | 46
2018-04-19 20:00 | 45
2018-04-19 21:00 | 43
2018-04-19 22:00 | 43
2018-04-19 23:00 | 41
2018-04-20 | 39
2018-04-20 01:00 | 40
2018-04-20 02:00 | 39
2018-04-20 03:00 | 39
2018-04-20 04:00 | 39
2018-04-20 05:00 | 38
2018-04-20 06:00 | 37
2018-04-20 07:00 | 37
2018-04-20 08:00 | 40
2018-04-20 09:00 | 39
2018-04-20 10:00 | 43
2018-04-20 11:00 | 44
2018-04-20 12:00 | 46
2018-04-20 13:00 | 48
2018-04-20 14:00 | 50
2018-04-20 15:00 | 50
2018-04-20 16:00 | 50
2018-04-20 17:00 | 50
2018-04-20 18:00 | 48
2018-04-20 19:00 | 46
2018-04-20 20:00 | 45
2018-04-20 21:00 | 45
2018-04-20 22:00 | 45
2018-04-20 23:00 | 43
2018-04-21 | 43
2018-04-21 01:00 | 42
2018-04-21 02:00 | 42
2018-04-21 03:00 | 43
2018-04-21 04:00 | 43
2018-04-21 05:00 | 41
2018-04-21 06:00 | 43
2018-04-21 07:00 | 43
2018-04-21 08:00 | 43
2018-04-21 09:00 | 45
2018-04-21 10:00 | 48
2018-04-21 11:00 | 52
2018-04-21 12:00 | 54
2018-04-21 13:00 | 55
2018-04-21 14:00 | 57
2018-04-21 15:00 | 61
2018-04-21 16:00 | 61
2018-04-21 17:00 | 62
2018-04-21 18:00 | 61
2018-04-21 19:00 | 61
2018-04-21 20:00 | 59
2018-04-21 21:00 | 57
2018-04-21 22:00 | 55
2018-04-21 23:00 | 55
2018-04-22 | 54
2018-04-22 01:00 | 53
2018-04-22 02:00 | 51
2018-04-22 03:00 | 48
2018-04-22 04:00 | 48
2018-04-22 05:00 | 48
2018-04-22 06:00 | 46
2018-04-22 07:00 | 46
2018-04-22 08:00 | 50
2018-04-22 09:00 | 52
2018-04-22 10:00 | 54
2018-04-22 11:00 | 57
2018-04-22 12:00 | 59
2018-04-22 13:00 | 61
2018-04-22 14:00 | 62
2018-04-22 15:00 | 63
2018-04-22 16:00 | 64
2018-04-22 17:00 | 61
2018-04-22 18:00 | 59
2018-04-22 19:00 | 57
2018-04-22 20:00 | 55
2018-04-22 21:00 | 54
2018-04-22 22:00 | 54
2018-04-22 23:00 | 52
2018-04-23 | 52
2018-04-23 01:00 | 50
2018-04-23 02:00 | 49
2018-04-23 03:00 | 48
2018-04-23 04:00 | 46
2018-04-23 05:00 | 46
2018-04-23 06:00 | 45
2018-04-23 07:00 | 46
2018-04-23 08:00 | 49
2018-04-23 09:00 | 52
2018-04-23 10:00 | 54
2018-04-23 11:00 | 56
2018-04-23 12:00 | 57
2018-04-23 13:00 | 57
2018-04-23 14:00 | 60
2018-04-23 15:00 | 63
2018-04-23 16:00 | 63
2018-04-23 17:00 | 62
2018-04-23 18:00 | 57
2018-04-23 19:00 | 57
2018-04-23 20:00 | 54
2018-04-23 21:00 | 54
2018-04-23 22:00 | 52
2018-04-23 23:00 | 51
2018-04-24 | 50
2018-04-24 01:00 | 50
2018-04-24 02:00 | 50
2018-04-24 03:00 | 48
2018-04-24 04:00 | 48
2018-04-24 05:00 | 47
2018-04-24 06:00 | 46
2018-04-24 07:00 | 46
2018-04-24 08:00 | 48
2018-04-24 09:00 | 52
2018-04-24 10:00 | 55
2018-04-24 11:00 | 61
2018-04-24 12:00 | 63
2018-04-24 13:00 | 64
2018-04-24 14:00 | 65
2018-04-24 15:00 | 64
2018-04-24 16:00 | 63
2018-04-24 17:00 | 62
2018-04-24 18:00 | 61
2018-04-24 19:00 | 61
2018-04-24 20:00 | 58
2018-04-24 21:00 | 57
2018-04-24 22:00 | 55
2018-04-24 23:00 | 57
2018-04-25 | 55
2018-04-25 01:00 | 56
2018-04-25 02:00 | 52
2018-04-25 03:00 | 50
2018-04-25 04:00 | 52
2018-04-25 05:00 | 55
2018-04-25 06:00 | 54
2018-04-25 07:00 | 52
2018-04-25 08:00 | 52
2018-04-25 09:00 | 57
2018-04-25 10:00 | 61
2018-04-25 11:00 | 61
2018-04-25 12:00 | 61
2018-04-25 13:00 | 61
2018-04-25 14:00 | 60
2018-04-25 15:00 | 61
2018-04-25 16:00 | 59
2018-04-25 17:00 | 54
2018-04-25 18:00 | 54
2018-04-25 19:00 | 54
2018-04-25 20:00 | 54
2018-04-25 21:00 | 54
2018-04-25 22:00 | 54
2018-04-25 23:00 | 54
2018-04-26 | 54
2018-04-26 01:00 | 55
2018-04-26 02:00 | 54
2018-04-26 03:00 | 55
2018-04-26 04:00 | 57
2018-04-26 05:00 | 58
2018-04-26 06:00 | 57
2018-04-26 07:00 | 57
2018-04-26 08:00 | 58
2018-04-26 09:00 | 57
2018-04-26 10:00 | 57
2018-04-26 11:00 | 59
2018-04-26 12:00 | 63
2018-04-26 13:00 | 63
2018-04-26 14:00 | 65
2018-04-26 15:00 | 66
2018-04-26 16:00 | 68
2018-04-26 17:00 | 69
2018-04-26 18:00 | 70
2018-04-26 19:00 | 70
2018-04-26 20:00 | 64
2018-04-26 21:00 | 64
2018-04-26 22:00 | 63
2018-04-26 23:00 | 60
2018-04-27 | 57
2018-04-27 01:00 | 57
2018-04-27 02:00 | 55
2018-04-27 03:00 | 55
2018-04-27 04:00 | 54
2018-04-27 05:00 | 53
2018-04-27 06:00 | 52
2018-04-27 07:00 | 52
2018-04-27 08:00 | 53
2018-04-27 09:00 | 52
2018-04-27 10:00 | 52
2018-04-27 11:00 | 56
2018-04-27 12:00 | 54
2018-04-27 13:00 | 54
2018-04-27 14:00 | 51
2018-04-27 15:00 | 52
2018-04-27 16:00 | 50
2018-04-27 17:00 | 50
2018-04-27 18:00 | 48
2018-04-27 19:00 | 50
2018-04-27 20:00 | 50
2018-04-27 21:00 | 52
2018-04-27 22:00 | 54
2018-04-27 23:00 | 53
2018-04-28 | 54
2018-04-28 01:00 | 53
2018-04-28 02:00 | 53
2018-04-28 03:00 | 54
2018-04-28 04:00 | 54
2018-04-28 05:00 | 52
2018-04-28 06:00 | 52
2018-04-28 07:00 | 52
2018-04-28 08:00 | 54
2018-04-28 09:00 | 54
2018-04-28 10:00 | 55
2018-04-28 11:00 | 61
2018-04-28 12:00 | 61
2018-04-28 13:00 | 63
2018-04-28 14:00 | 63
2018-04-28 15:00 | 64
2018-04-28 16:00 | 64
2018-04-28 17:00 | 65
2018-04-28 18:00 | 64
2018-04-28 19:00 | 61
2018-04-28 20:00 | 60
2018-04-28 21:00 | 57
2018-04-28 22:00 | 55
2018-04-28 23:00 | 54
2018-04-29 | 55
2018-04-29 01:00 | 54
2018-04-29 02:00 | 54
2018-04-29 03:00 | 55
2018-04-29 04:00 | 54
2018-04-29 05:00 | 53
2018-04-29 06:00 | 54
2018-04-29 07:00 | 52
2018-04-29 08:00 | 50
2018-04-29 09:00 | 52
2018-04-29 10:00 | 50
2018-04-29 11:00 | 53
2018-04-29 12:00 | 55
2018-04-29 13:00 | 55
2018-04-29 14:00 | 57
2018-04-29 15:00 | 57
2018-04-29 16:00 | 55
2018-04-29 17:00 | 54
2018-04-29 18:00 | 54
2018-04-29 19:00 | 52
2018-04-29 20:00 | 50
2018-04-29 21:00 | 48
2018-04-29 22:00 | 48
2018-04-29 23:00 | 49
2018-04-30 | 48
2018-04-30 01:00 | 50
2018-04-30 02:00 | 50
2018-04-30 03:00 | 48
2018-04-30 04:00 | 48
2018-04-30 05:00 | 49
2018-04-30 06:00 | 46
2018-04-30 07:00 | 48
2018-04-30 08:00 | 49
2018-04-30 09:00 | 50
2018-04-30 10:00 | 50
2018-04-30 11:00 | 48
2018-04-30 12:00 | 45
2018-04-30 13:00 | 46
2018-04-30 14:00 | 49
2018-04-30 15:00 | 50
2018-04-30 16:00 | 48
2018-04-30 17:00 | 50
2018-04-30 18:00 | 52
2018-04-30 19:00 | 52
2018-04-30 20:00 | 50
2018-04-30 21:00 | 50
2018-04-30 22:00 | 52
2018-04-30 23:00 | 51
2018-05-01 | 50
2018-05-01 01:00 | 50
2018-05-01 02:00 | 51
2018-05-01 03:00 | 52
2018-05-01 04:00 | 52
2018-05-01 05:00 | 52
2018-05-01 06:00 | 52
2018-05-01 07:00 | 52
2018-05-01 08:00 | 54
2018-05-01 09:00 | 57
2018-05-01 10:00 | 61
2018-05-01 11:00 | 65
2018-05-01 12:00 | 68
2018-05-01 13:00 | 70
2018-05-01 14:00 | 73
2018-05-01 15:00 | 75
2018-05-01 16:00 | 75
2018-05-01 17:00 | 81
2018-05-01 18:00 | 79
2018-05-01 19:00 | 75
2018-05-01 20:00 | 74
2018-05-01 21:00 | 72
2018-05-01 22:00 | 72
2018-05-01 23:00 | 73
2018-05-02 | 72
2018-05-02 01:00 | 70
2018-05-02 02:00 | 70
2018-05-02 03:00 | 70
2018-05-02 04:00 | 68
2018-05-02 05:00 | 67
2018-05-02 06:00 | 66
2018-05-02 07:00 | 66
2018-05-02 08:00 | 70
2018-05-02 09:00 | 75
2018-05-02 10:00 | 81
2018-05-02 11:00 | 82
2018-05-02 12:00 | 84
2018-05-02 13:00 | 86
2018-05-02 14:00 | 88
2018-05-02 15:00 | 90
2018-05-02 16:00 | 90
2018-05-02 17:00 | 89
2018-05-02 18:00 | 90
2018-05-02 19:00 | 88
2018-05-02 20:00 | 85
2018-05-02 21:00 | 84
2018-05-02 22:00 | 82
2018-05-02 23:00 | 81
2018-05-03 | 79
2018-05-03 01:00 | 78
2018-05-03 02:00 | 76
2018-05-03 03:00 | 73
2018-05-03 04:00 | 73
2018-05-03 05:00 | 73
2018-05-03 06:00 | 72
2018-05-03 07:00 | 72
2018-05-03 08:00 | 75
2018-05-03 09:00 | 79
2018-05-03 10:00 | 82
2018-05-03 11:00 | 85
2018-05-03 12:00 | 88
2018-05-03 13:00 | 90
2018-05-03 14:00 | 91
2018-05-03 15:00 | 91
2018-05-03 16:00 | 91
2018-05-03 17:00 | 93
2018-05-03 18:00 | 91
2018-05-03 19:00 | 90
2018-05-03 20:00 | 71
2018-05-03 21:00 | 75
2018-05-03 22:00 | 79
2018-05-03 23:00 | 75
2018-05-04 | 75
2018-05-04 01:00 | 72
2018-05-04 02:00 | 70
2018-05-04 03:00 | 72
2018-05-04 04:00 | 70
2018-05-04 05:00 | 73
2018-05-04 06:00 | 73
2018-05-04 07:00 | 75
2018-05-04 08:00 | 76
2018-05-04 09:00 | 75
2018-05-04 10:00 | 79
2018-05-04 11:00 | 77
2018-05-04 12:00 | 79
2018-05-04 13:00 | 79
2018-05-04 14:00 | 81
2018-05-04 15:00 | 81
2018-05-04 16:00 | 81
2018-05-04 17:00 | 81
2018-05-04 18:00 | 79
2018-05-04 19:00 | 75
2018-05-04 20:00 | 78
2018-05-04 21:00 | 75
2018-05-04 22:00 | 81
2018-05-04 23:00 | 81
2018-05-05 | 79
2018-05-05 01:00 | 77
2018-05-05 02:00 | 72
2018-05-05 03:00 | 70
2018-05-05 04:00 | 66
2018-05-05 05:00 | 65
2018-05-05 06:00 | 63
2018-05-05 07:00 | 61
2018-05-05 08:00 | 61
2018-05-05 09:00 | 61
2018-05-05 10:00 | 63
2018-05-05 11:00 | 65
2018-05-05 12:00 | 68
2018-05-05 13:00 | 72
2018-05-05 14:00 | 74
2018-05-05 15:00 | 73
2018-05-05 16:00 | 75
2018-05-05 17:00 | 71
2018-05-05 18:00 | 70
2018-05-05 19:00 | 68
2018-05-05 20:00 | 67
2018-05-05 21:00 | 66
2018-05-05 22:00 | 66
2018-05-05 23:00 | 65
2018-05-06 | 66
2018-05-06 01:00 | 68
2018-05-06 02:00 | 64
2018-05-06 03:00 | 63
2018-05-06 04:00 | 63
2018-05-06 05:00 | 64
2018-05-06 06:00 | 63
2018-05-06 07:00 | 61
2018-05-06 08:00 | 60
2018-05-06 09:00 | 59
2018-05-06 10:00 | 61
2018-05-06 11:00 | 61
2018-05-06 12:00 | 63
2018-05-06 13:00 | 63
2018-05-06 14:00 | 62
2018-05-06 15:00 | 61
2018-05-06 16:00 | 61
2018-05-06 17:00 | 59
2018-05-06 18:00 | 59
2018-05-06 19:00 | 57
2018-05-06 20:00 | 57
2018-05-06 21:00 | 55
2018-05-06 22:00 | 54
2018-05-06 23:00 | 56
2018-05-07 | 55
2018-05-07 01:00 | 56
2018-05-07 02:00 | 58
2018-05-07 03:00 | 57
2018-05-07 04:00 | 57
2018-05-07 05:00 | 57
2018-05-07 06:00 | 55
2018-05-07 07:00 | 57
2018-05-07 08:00 | 59
2018-05-07 09:00 | 61
2018-05-07 10:00 | 64
2018-05-07 11:00 | 66
2018-05-07 12:00 | 68
2018-05-07 13:00 | 70
2018-05-07 14:00 | 72
2018-05-07 15:00 | 73
2018-05-07 16:00 | 75
2018-05-07 17:00 | 69
2018-05-07 18:00 | 68
2018-05-07 19:00 | 66
2018-05-07 20:00 | 65
2018-05-07 21:00 | 63
2018-05-07 22:00 | 61
2018-05-07 23:00 | 59
2018-05-08 | 57
2018-05-08 01:00 | 57
2018-05-08 02:00 | 56
2018-05-08 03:00 | 54
2018-05-08 04:00 | 55
2018-05-08 05:00 | 55
2018-05-08 06:00 | 54
2018-05-08 07:00 | 55
2018-05-08 08:00 | 57
2018-05-08 09:00 | 59
2018-05-08 10:00 | 63
2018-05-08 11:00 | 64
2018-05-08 12:00 | 66
2018-05-08 13:00 | 69
2018-05-08 14:00 | 71
2018-05-08 15:00 | 70
2018-05-08 16:00 | 71
2018-05-08 17:00 | 68
2018-05-08 18:00 | 68
2018-05-08 19:00 | 65
2018-05-08 20:00 | 63
2018-05-08 21:00 | 61
2018-05-08 22:00 | 60
2018-05-08 23:00 | 59
2018-05-09 | 59
2018-05-09 01:00 | 56
2018-05-09 02:00 | 56
2018-05-09 03:00 | 55
2018-05-09 04:00 | 56
2018-05-09 05:00 | 54
2018-05-09 06:00 | 55
2018-05-09 07:00 | 57
2018-05-09 08:00 | 60
2018-05-09 09:00 | 63
2018-05-09 10:00 | 67
2018-05-09 11:00 | 70
2018-05-09 12:00 | 73
2018-05-09 13:00 | 73
2018-05-09 14:00 | 68
2018-05-09 15:00 | 72
2018-05-09 16:00 | 72
2018-05-09 17:00 | 72
2018-05-09 18:00 | 70
2018-05-09 19:00 | 70
2018-05-09 20:00 | 65
2018-05-09 21:00 | 63
2018-05-09 22:00 | 59
2018-05-09 23:00 | 58
2018-05-10 | 57
2018-05-10 01:00 | 55
2018-05-10 02:00 | 55
2018-05-10 03:00 | 55
2018-05-10 04:00 | 57
2018-05-10 05:00 | 57
2018-05-10 06:00 | 57
2018-05-10 07:00 | 57
2018-05-10 08:00 | 58
2018-05-10 09:00 | 57
2018-05-10 10:00 | 59
2018-05-10 11:00 | 62
2018-05-10 12:00 | 61
2018-05-10 13:00 | 61
2018-05-10 14:00 | 59
2018-05-10 15:00 | 61
2018-05-10 16:00 | 63
2018-05-10 17:00 | 63
2018-05-10 18:00 | 63
2018-05-10 19:00 | 63
2018-05-10 20:00 | 63
2018-05-10 21:00 | 63
2018-05-10 22:00 | 64
2018-05-10 23:00 | 65
2018-05-11 | 63
2018-05-11 01:00 | 63
2018-05-11 02:00 | 61
2018-05-11 03:00 | 61
2018-05-11 04:00 | 63
2018-05-11 05:00 | 61
2018-05-11 06:00 | 63
2018-05-11 07:00 | 63
2018-05-11 08:00 | 63
2018-05-11 09:00 | 64
2018-05-11 10:00 | 64
2018-05-11 11:00 | 65
2018-05-11 12:00 | 64
2018-05-11 13:00 | 66
2018-05-11 14:00 | 69
2018-05-11 15:00 | 72
2018-05-11 16:00 | 72
2018-05-11 17:00 | 72
2018-05-11 18:00 | 72
2018-05-11 19:00 | 70
2018-05-11 20:00 | 68
2018-05-11 21:00 | 66
2018-05-11 22:00 | 66
2018-05-11 23:00 | 66
2018-05-12 | 64
2018-05-12 01:00 | 63
2018-05-12 02:00 | 63
2018-05-12 03:00 | 61
2018-05-12 04:00 | 59
2018-05-12 05:00 | 58
2018-05-12 06:00 | 55
2018-05-12 07:00 | 54
2018-05-12 08:00 | 54
2018-05-12 09:00 | 55
2018-05-12 10:00 | 55
2018-05-12 11:00 | 55
2018-05-12 12:00 | 57
2018-05-12 13:00 | 55
2018-05-12 14:00 | 58
2018-05-12 15:00 | 57
2018-05-12 16:00 | 57
2018-05-12 17:00 | 57
2018-05-12 18:00 | 55
2018-05-12 19:00 | 55
2018-05-12 20:00 | 55
2018-05-12 21:00 | 55
2018-05-12 22:00 | 54
2018-05-12 23:00 | 53
2018-05-13 | 54
2018-05-13 01:00 | 53
2018-05-13 02:00 | 53
2018-05-13 03:00 | 54
2018-05-13 04:00 | 54
2018-05-13 05:00 | 53
2018-05-13 06:00 | 54
2018-05-13 07:00 | 54
2018-05-13 08:00 | 53
2018-05-13 09:00 | 54
2018-05-13 10:00 | 54
2018-05-13 11:00 | 54
2018-05-13 12:00 | 54
2018-05-13 13:00 | 54
2018-05-13 14:00 | 53
2018-05-13 15:00 | 54
2018-05-13 16:00 | 54
2018-05-13 17:00 | 55
2018-05-13 18:00 | 55
2018-05-13 19:00 | 55
2018-05-13 20:00 | 55
2018-05-13 21:00 | 55
2018-05-13 22:00 | 54
2018-05-13 23:00 | 53
2018-05-14 | 54
2018-05-14 01:00 | 54
2018-05-14 02:00 | 53
2018-05-14 03:00 | 54
2018-05-14 04:00 | 54
2018-05-14 05:00 | 53
2018-05-14 06:00 | 54
2018-05-14 07:00 | 54
2018-05-14 08:00 | 55
2018-05-14 09:00 | 55
2018-05-14 10:00 | 57
2018-05-14 11:00 | 61
2018-05-14 12:00 | 63
2018-05-14 13:00 | 63
2018-05-14 14:00 | 66
2018-05-14 15:00 | 68
2018-05-14 16:00 | 70
2018-05-14 17:00 | 69
2018-05-14 18:00 | 68
2018-05-14 19:00 | 64
2018-05-14 20:00 | 61
2018-05-14 21:00 | 61
2018-05-14 22:00 | 59
2018-05-14 23:00 | 59
2018-05-15 | 61
2018-05-15 01:00 | 60
2018-05-15 02:00 | 60
2018-05-15 03:00 | 61
2018-05-15 04:00 | 61
2018-05-15 05:00 | 61
2018-05-15 06:00 | 61
2018-05-15 07:00 | 63
2018-05-15 08:00 | 65
2018-05-15 09:00 | 66
2018-05-15 10:00 | 73
2018-05-15 11:00 | 75
2018-05-15 12:00 | 81
2018-05-15 13:00 | 84
2018-05-15 14:00 | 85
2018-05-15 15:00 | 88
2018-05-15 16:00 | 88
2018-05-15 17:00 | 90
2018-05-15 18:00 | 70
2018-05-15 19:00 | 66
2018-05-15 20:00 | 68
2018-05-15 21:00 | 70
2018-05-15 22:00 | 70
2018-05-15 23:00 | 68
2018-05-16 | 66
2018-05-16 01:00 | 65
2018-05-16 02:00 | 63
2018-05-16 03:00 | 64
2018-05-16 04:00 | 64
2018-05-16 05:00 | 63
2018-05-16 06:00 | 63
2018-05-16 07:00 | 63
2018-05-16 08:00 | 63
2018-05-16 09:00 | 63
2018-05-16 10:00 | 63
2018-05-16 11:00 | 62
2018-05-16 12:00 | 61
2018-05-16 13:00 | 59
2018-05-16 14:00 | 59
2018-05-16 15:00 | 59
2018-05-16 16:00 | 61
2018-05-16 17:00 | 61
2018-05-16 18:00 | 57
2018-05-16 19:00 | 57
2018-05-16 20:00 | 56
2018-05-16 21:00 | 55
2018-05-16 22:00 | 55
2018-05-16 23:00 | 56
2018-05-17 | 55
2018-05-17 01:00 | 55
2018-05-17 02:00 | 55
2018-05-17 03:00 | 55
2018-05-17 04:00 | 55
2018-05-17 05:00 | 55
2018-05-17 06:00 | 55
2018-05-17 07:00 | 55
2018-05-17 08:00 | 56
2018-05-17 09:00 | 57
2018-05-17 10:00 | 59
2018-05-17 11:00 | 60
2018-05-17 12:00 | 61
2018-05-17 13:00 | 63
2018-05-17 14:00 | 65
2018-05-17 15:00 | 70
2018-05-17 16:00 | 72
2018-05-17 17:00 | 72
2018-05-17 18:00 | 73
2018-05-17 19:00 | 73
2018-05-17 20:00 | 70
2018-05-17 21:00 | 70
2018-05-17 22:00 | 70
2018-05-17 23:00 | 68
2018-05-18 | 66
2018-05-18 01:00 | 67
2018-05-18 02:00 | 65
2018-05-18 03:00 | 66
2018-05-18 04:00 | 63
2018-05-18 05:00 | 63
2018-05-18 06:00 | 63
2018-05-18 07:00 | 63
2018-05-18 08:00 | 64
2018-05-18 09:00 | 64
2018-05-18 10:00 | 63
2018-05-18 11:00 | 64
2018-05-18 12:00 | 63
2018-05-18 13:00 | 63
2018-05-18 14:00 | 64
2018-05-18 15:00 | 64
2018-05-18 16:00 | 66
2018-05-18 17:00 | 64
2018-05-18 18:00 | 63
2018-05-18 19:00 | 63
2018-05-18 20:00 | 61
2018-05-18 21:00 | 60
2018-05-18 22:00 | 57
2018-05-18 23:00 | 57
2018-05-19 | 55
2018-05-19 01:00 | 56
2018-05-19 02:00 | 54
2018-05-19 03:00 | 54
2018-05-19 04:00 | 54
2018-05-19 05:00 | 52
2018-05-19 06:00 | 52
2018-05-19 07:00 | 52
2018-05-19 08:00 | 51
2018-05-19 09:00 | 52
2018-05-19 10:00 | 52
2018-05-19 11:00 | 52
2018-05-19 12:00 | 54
2018-05-19 13:00 | 54
2018-05-19 14:00 | 54
2018-05-19 15:00 | 54
2018-05-19 16:00 | 55
2018-05-19 17:00 | 56
2018-05-19 18:00 | 55
2018-05-19 19:00 | 55
2018-05-19 20:00 | 55
2018-05-19 21:00 | 55
2018-05-19 22:00 | 54
2018-05-19 23:00 | 54
2018-05-20 | 55
2018-05-20 01:00 | 55
2018-05-20 02:00 | 55
2018-05-20 03:00 | 55
2018-05-20 04:00 | 58
2018-05-20 05:00 | 58
2018-05-20 06:00 | 59
2018-05-20 07:00 | 64
2018-05-20 08:00 | 68
2018-05-20 09:00 | 71
2018-05-20 10:00 | 74
2018-05-20 11:00 | 77
2018-05-20 12:00 | 80
2018-05-20 13:00 | 82
2018-05-20 14:00 | 81
2018-05-20 15:00 | 81
2018-05-20 16:00 | 83
2018-05-20 17:00 | 78
2018-05-20 18:00 | 77
2018-05-20 19:00 | 74
2018-05-20 20:00 | 73
2018-05-20 21:00 | 71
2018-05-20 22:00 | 71
2018-05-20 23:00 | 70
2018-05-21 | 68
2018-05-21 01:00 | 66
2018-05-21 02:00 | 65
2018-05-21 03:00 | 63
2018-05-21 04:00 | 63
2018-05-21 05:00 | 61
2018-05-21 06:00 | 61
2018-05-21 07:00 | 63
2018-05-21 08:00 | 64
2018-05-21 09:00 | 66
2018-05-21 10:00 | 66
2018-05-21 11:00 | 69
2018-05-21 12:00 | 72
2018-05-21 13:00 | 73
2018-05-21 14:00 | 76
2018-05-21 15:00 | 78
2018-05-21 16:00 | 75
2018-05-21 17:00 | 74
2018-05-21 18:00 | 73
2018-05-21 19:00 | 72
2018-05-21 20:00 | 67
2018-05-21 21:00 | 66
2018-05-21 22:00 | 66
2018-05-21 23:00 | 66
2018-05-22 | 66
2018-05-22 01:00 | 66
2018-05-22 02:00 | 65
2018-05-22 03:00 | 64
2018-05-22 04:00 | 64
2018-05-22 05:00 | 65
2018-05-22 06:00 | 64
2018-05-22 07:00 | 64
2018-05-22 08:00 | 68
2018-05-22 09:00 | 70
2018-05-22 10:00 | 68
2018-05-22 11:00 | 66
2018-05-22 12:00 | 66
2018-05-22 13:00 | 64
2018-05-22 14:00 | 65
2018-05-22 15:00 | 63
2018-05-22 16:00 | 61
2018-05-22 17:00 | 58
2018-05-22 18:00 | 57
2018-05-22 19:00 | 57
2018-05-22 20:00 | 57
2018-05-22 21:00 | 57
2018-05-22 22:00 | 57
2018-05-22 23:00 | 58
2018-05-23 | 58
2018-05-23 01:00 | 58
2018-05-23 02:00 | 58
2018-05-23 03:00 | 59
2018-05-23 04:00 | 60
2018-05-23 05:00 | 60
2018-05-23 06:00 | 61
2018-05-23 07:00 | 62
2018-05-23 08:00 | 64
2018-05-23 09:00 | 67
2018-05-23 10:00 | 68
2018-05-23 11:00 | 71
2018-05-23 12:00 | 72
2018-05-23 13:00 | 72
2018-05-23 14:00 | 75
2018-05-23 15:00 | 79
2018-05-23 16:00 | 79
2018-05-23 17:00 | 82
2018-05-23 18:00 | 81
2018-05-23 19:00 | 79
2018-05-23 20:00 | 77
2018-05-23 21:00 | 77
2018-05-23 22:00 | 79
2018-05-23 23:00 | 76
2018-05-24 | 72
2018-05-24 01:00 | 70
2018-05-24 02:00 | 69
2018-05-24 03:00 | 66
2018-05-24 04:00 | 66
2018-05-24 05:00 | 66
2018-05-24 06:00 | 66
2018-05-24 07:00 | 66
2018-05-24 08:00 | 68
2018-05-24 09:00 | 72
2018-05-24 10:00 | 73
2018-05-24 11:00 | 75
2018-05-24 12:00 | 79
2018-05-24 13:00 | 79
2018-05-24 14:00 | 80
2018-05-24 15:00 | 82
2018-05-24 16:00 | 84
2018-05-24 17:00 | 85
2018-05-24 18:00 | 82
2018-05-24 19:00 | 79
2018-05-24 20:00 | 76
2018-05-24 21:00 | 75
2018-05-24 22:00 | 75
2018-05-24 23:00 | 74
2018-05-25 | 72
2018-05-25 01:00 | 71
2018-05-25 02:00 | 71
2018-05-25 03:00 | 70
2018-05-25 04:00 | 70
2018-05-25 05:00 | 69
2018-05-25 06:00 | 68
2018-05-25 07:00 | 70
2018-05-25 08:00 | 73
2018-05-25 09:00 | 75
2018-05-25 10:00 | 81
2018-05-25 11:00 | 82
2018-05-25 12:00 | 84
2018-05-25 13:00 | 86
2018-05-25 14:00 | 87
2018-05-25 15:00 | 88
2018-05-25 16:00 | 88
2018-05-25 17:00 | 88
2018-05-25 18:00 | 88
2018-05-25 19:00 | 88
2018-05-25 20:00 | 86
2018-05-25 21:00 | 84
2018-05-25 22:00 | 82
2018-05-25 23:00 | 80
2018-05-26 | 79
2018-05-26 01:00 | 78
2018-05-26 02:00 | 77
2018-05-26 03:00 | 75
2018-05-26 04:00 | 75
2018-05-26 05:00 | 75
2018-05-26 06:00 | 75
2018-05-26 07:00 | 75
2018-05-26 08:00 | 77
2018-05-26 09:00 | 81
2018-05-26 10:00 | 82
2018-05-26 11:00 | 84
2018-05-26 12:00 | 90
2018-05-26 13:00 | 90
2018-05-26 14:00 | 91
2018-05-26 15:00 | 90
2018-05-26 16:00 | 90
2018-05-26 17:00 | 87
2018-05-26 18:00 | 88
2018-05-26 19:00 | 84
2018-05-26 20:00 | 83
2018-05-26 21:00 | 80
2018-05-26 22:00 | 79
2018-05-26 23:00 | 80
2018-05-27 | 82
2018-05-27 01:00 | 82
2018-05-27 02:00 | 81
2018-05-27 03:00 | 70
2018-05-27 04:00 | 68
2018-05-27 05:00 | 71
2018-05-27 06:00 | 67
2018-05-27 07:00 | 67
2018-05-27 08:00 | 65
2018-05-27 09:00 | 61
2018-05-27 10:00 | 61
2018-05-27 11:00 | 62
2018-05-27 12:00 | 64
2018-05-27 13:00 | 64
2018-05-27 14:00 | 62
2018-05-27 15:00 | 61
2018-05-27 16:00 | 61
2018-05-27 17:00 | 61
2018-05-27 18:00 | 61
2018-05-27 19:00 | 60
2018-05-27 20:00 | 59
2018-05-27 21:00 | 58
2018-05-27 22:00 | 58
2018-05-27 23:00 | 57
2018-05-28 | 57
2018-05-28 01:00 | 57
2018-05-28 02:00 | 56
2018-05-28 03:00 | 56
2018-05-28 04:00 | 56
2018-05-28 05:00 | 56
2018-05-28 06:00 | 56
2018-05-28 07:00 | 57
2018-05-28 08:00 | 57
2018-05-28 09:00 | 58
2018-05-28 10:00 | 58
2018-05-28 11:00 | 59
2018-05-28 12:00 | 61
2018-05-28 13:00 | 64
2018-05-28 14:00 | 66
2018-05-28 15:00 | 69
2018-05-28 16:00 | 69
2018-05-28 17:00 | 69
2018-05-28 18:00 | 67
2018-05-28 19:00 | 63
2018-05-28 20:00 | 61
2018-05-28 21:00 | 61
2018-05-28 22:00 | 61
2018-05-28 23:00 | 62
2018-05-29 | 62
2018-05-29 01:00 | 62
2018-05-29 02:00 | 64
2018-05-29 03:00 | 65
2018-05-29 04:00 | 65
2018-05-29 05:00 | 66
2018-05-29 06:00 | 67
2018-05-29 07:00 | 67
2018-05-29 08:00 | 69
2018-05-29 09:00 | 73
2018-05-29 10:00 | 75
2018-05-29 11:00 | 78
2018-05-29 12:00 | 82
2018-05-29 13:00 | 85
2018-05-29 14:00 | 86
2018-05-29 15:00 | 87
2018-05-29 16:00 | 86
2018-05-29 17:00 | 84
2018-05-29 18:00 | 82
2018-05-29 19:00 | 81
2018-05-29 20:00 | 78
2018-05-29 21:00 | 77
2018-05-29 22:00 | 75
2018-05-29 23:00 | 75
2018-05-30 | 73
2018-05-30 01:00 | 70
2018-05-30 02:00 | 65
2018-05-30 03:00 | 64
2018-05-30 04:00 | 63
2018-05-30 05:00 | 64
2018-05-30 06:00 | 63
2018-05-30 07:00 | 63
2018-05-30 08:00 | 63
2018-05-30 09:00 | 64
2018-05-30 10:00 | 64
2018-05-30 11:00 | 65
2018-05-30 12:00 | 66
2018-05-30 13:00 | 72
2018-05-30 14:00 | 72
2018-05-30 15:00 | 70
2018-05-30 16:00 | 75
2018-05-30 17:00 | 73
2018-05-30 18:00 | 72
2018-05-30 19:00 | 70
2018-05-30 20:00 | 64
2018-05-30 21:00 | 63
2018-05-30 22:00 | 63
2018-05-30 23:00 | 62
2018-05-31 | 63
2018-05-31 01:00 | 62
2018-05-31 02:00 | 62
2018-05-31 03:00 | 63
2018-05-31 04:00 | 63
2018-05-31 05:00 | 62
2018-05-31 06:00 | 63
2018-05-31 07:00 | 63
2018-05-31 08:00 | 63
2018-05-31 09:00 | 64
2018-05-31 10:00 | 64
2018-05-31 11:00 | 65
2018-05-31 12:00 | 64
2018-05-31 13:00 | 64
2018-05-31 14:00 | 64
2018-05-31 15:00 | 64
2018-05-31 16:00 | 68
2018-05-31 17:00 | 68
2018-05-31 18:00 | 70
2018-05-31 19:00 | 68
2018-05-31 20:00 | 67
2018-05-31 21:00 | 66
2018-05-31 22:00 | 66
2018-05-31 23:00 | 66
2018-06-01 | 64
2018-06-01 01:00 | 66
2018-06-01 02:00 | 66
2018-06-01 03:00 | 66
2018-06-01 04:00 | 64
2018-06-01 05:00 | 64
2018-06-01 06:00 | 64
2018-06-01 07:00 | 64
2018-06-01 08:00 | 64
2018-06-01 09:00 | 64
2018-06-01 10:00 | 68
2018-06-01 11:00 | 70
2018-06-01 12:00 | 70
2018-06-01 13:00 | 72
2018-06-01 14:00 | 74
2018-06-01 15:00 | 73
2018-06-01 16:00 | 79
2018-06-01 17:00 | 79
2018-06-01 18:00 | 81
2018-06-01 19:00 | 77
2018-06-01 20:00 | 75
2018-06-01 21:00 | 73
2018-06-01 22:00 | 73
2018-06-01 23:00 | 73
2018-06-02 | 72
2018-06-02 01:00 | 73
2018-06-02 02:00 | 69
2018-06-02 03:00 | 72
2018-06-02 04:00 | 72
2018-06-02 05:00 | 70
2018-06-02 06:00 | 70
2018-06-02 07:00 | 73
2018-06-02 08:00 | 76
2018-06-02 09:00 | 77
2018-06-02 10:00 | 80
2018-06-02 11:00 | 83
2018-06-02 12:00 | 86
2018-06-02 13:00 | 84
2018-06-02 14:00 | 84
2018-06-02 15:00 | 87
2018-06-02 16:00 | 85
2018-06-02 17:00 | 85
2018-06-02 18:00 | 85
2018-06-02 19:00 | 82
2018-06-02 20:00 | 76
2018-06-02 21:00 | 75
2018-06-02 22:00 | 73
2018-06-02 23:00 | 74
2018-06-03 | 73
2018-06-03 01:00 | 68
2018-06-03 02:00 | 65
2018-06-03 03:00 | 64
2018-06-03 04:00 | 62
2018-06-03 05:00 | 63
2018-06-03 06:00 | 62
2018-06-03 07:00 | 62
2018-06-03 08:00 | 63
2018-06-03 09:00 | 62
2018-06-03 10:00 | 63
2018-06-03 11:00 | 63
2018-06-03 12:00 | 63
2018-06-03 13:00 | 63
2018-06-03 14:00 | 63
2018-06-03 15:00 | 63
2018-06-03 16:00 | 63
2018-06-03 17:00 | 64
2018-06-03 18:00 | 64
2018-06-03 19:00 | 62
2018-06-03 20:00 | 60
2018-06-03 21:00 | 59
2018-06-03 22:00 | 57
2018-06-03 23:00 | 55
2018-06-04 | 54
2018-06-04 01:00 | 53
2018-06-04 02:00 | 53
2018-06-04 03:00 | 53
2018-06-04 04:00 | 53
2018-06-04 05:00 | 54
2018-06-04 06:00 | 54
2018-06-04 07:00 | 53
2018-06-04 08:00 | 54
2018-06-04 09:00 | 58
2018-06-04 10:00 | 57
2018-06-04 11:00 | 60
2018-06-04 12:00 | 61
2018-06-04 13:00 | 63
2018-06-04 14:00 | 65
2018-06-04 15:00 | 66
2018-06-04 16:00 | 68
2018-06-04 17:00 | 70
2018-06-04 18:00 | 70
2018-06-04 19:00 | 70
2018-06-04 20:00 | 70
2018-06-04 21:00 | 66
2018-06-04 22:00 | 63
2018-06-04 23:00 | 62
2018-06-05 | 63
2018-06-05 01:00 | 61
2018-06-05 02:00 | 61
2018-06-05 03:00 | 61
2018-06-05 04:00 | 61
2018-06-05 05:00 | 60
2018-06-05 06:00 | 59
2018-06-05 07:00 | 64
2018-06-05 08:00 | 66
2018-06-05 09:00 | 68
2018-06-05 10:00 | 72
2018-06-05 11:00 | 74
2018-06-05 12:00 | 75
2018-06-05 13:00 | 75
2018-06-05 14:00 | 75
2018-06-05 15:00 | 72
2018-06-05 16:00 | 75
2018-06-05 17:00 | 74
2018-06-05 18:00 | 73
2018-06-05 19:00 | 72
2018-06-05 20:00 | 71
2018-06-05 21:00 | 70
2018-06-05 22:00 | 66
2018-06-05 23:00 | 65
2018-06-06 | 64
2018-06-06 01:00 | 63
2018-06-06 02:00 | 62
2018-06-06 03:00 | 63
2018-06-06 04:00 | 61
2018-06-06 05:00 | 61
2018-06-06 06:00 | 61
2018-06-06 07:00 | 61
2018-06-06 08:00 | 62
2018-06-06 09:00 | 63
2018-06-06 10:00 | 64
2018-06-06 11:00 | 66
2018-06-06 12:00 | 66
2018-06-06 13:00 | 70
2018-06-06 14:00 | 69
2018-06-06 15:00 | 70
2018-06-06 16:00 | 70
2018-06-06 17:00 | 67
2018-06-06 18:00 | 64
2018-06-06 19:00 | 63
2018-06-06 20:00 | 62
2018-06-06 21:00 | 61
2018-06-06 22:00 | 61
2018-06-06 23:00 | 60
2018-06-07 | 61
2018-06-07 01:00 | 61
2018-06-07 02:00 | 61
2018-06-07 03:00 | 61
2018-06-07 04:00 | 63
2018-06-07 05:00 | 61
2018-06-07 06:00 | 63
2018-06-07 07:00 | 63
2018-06-07 08:00 | 62
2018-06-07 09:00 | 63
2018-06-07 10:00 | 63
2018-06-07 11:00 | 65
2018-06-07 12:00 | 68
2018-06-07 13:00 | 70
2018-06-07 14:00 | 71
2018-06-07 15:00 | 72
2018-06-07 16:00 | 70
2018-06-07 17:00 | 69
2018-06-07 18:00 | 66
2018-06-07 19:00 | 64
2018-06-07 20:00 | 64
2018-06-07 21:00 | 63
2018-06-07 22:00 | 63
2018-06-07 23:00 | 62
2018-06-08 | 63
2018-06-08 01:00 | 62
2018-06-08 02:00 | 62
2018-06-08 03:00 | 63
2018-06-08 04:00 | 63
2018-06-08 05:00 | 62
2018-06-08 06:00 | 63
2018-06-08 07:00 | 64
2018-06-08 08:00 | 67
2018-06-08 09:00 | 70
2018-06-08 10:00 | 73
2018-06-08 11:00 | 76
2018-06-08 12:00 | 79
2018-06-08 13:00 | 81
2018-06-08 14:00 | 82
2018-06-08 15:00 | 81
2018-06-08 16:00 | 81
2018-06-08 17:00 | 79
2018-06-08 18:00 | 79
2018-06-08 19:00 | 79
2018-06-08 20:00 | 77
2018-06-08 21:00 | 75
2018-06-08 22:00 | 79
2018-06-08 23:00 | 78
2018-06-09 | 77
2018-06-09 01:00 | 77
2018-06-09 02:00 | 75
2018-06-09 03:00 | 73
2018-06-09 04:00 | 72
2018-06-09 05:00 | 70
2018-06-09 06:00 | 70
2018-06-09 07:00 | 72
2018-06-09 08:00 | 72
2018-06-09 09:00 | 73
2018-06-09 10:00 | 73
2018-06-09 11:00 | 75
2018-06-09 12:00 | 75
2018-06-09 13:00 | 79
2018-06-09 14:00 | 80
2018-06-09 15:00 | 81
2018-06-09 16:00 | 79
2018-06-09 17:00 | 79
2018-06-09 18:00 | 79
2018-06-09 19:00 | 77
2018-06-09 20:00 | 73
2018-06-09 21:00 | 73
2018-06-09 22:00 | 73
2018-06-09 23:00 | 74
2018-06-10 | 73
2018-06-10 01:00 | 72
2018-06-10 02:00 | 71
2018-06-10 03:00 | 72
2018-06-10 04:00 | 70
2018-06-10 05:00 | 70
2018-06-10 06:00 | 70
2018-06-10 07:00 | 70
2018-06-10 08:00 | 67
2018-06-10 09:00 | 68
2018-06-10 10:00 | 68
2018-06-10 11:00 | 68
2018-06-10 12:00 | 70
2018-06-10 13:00 | 70
2018-06-10 14:00 | 70
2018-06-10 15:00 | 71
2018-06-10 16:00 | 70
2018-06-10 17:00 | 69
2018-06-10 18:00 | 68
2018-06-10 19:00 | 66
2018-06-10 20:00 | 66
2018-06-10 21:00 | 66
2018-06-10 22:00 | 66
2018-06-10 23:00 | 65
2018-06-11 | 64
2018-06-11 01:00 | 61
2018-06-11 02:00 | 60
2018-06-11 03:00 | 61
2018-06-11 04:00 | 61
2018-06-11 05:00 | 60
2018-06-11 06:00 | 61
2018-06-11 07:00 | 61
2018-06-11 08:00 | 62
2018-06-11 09:00 | 63
2018-06-11 10:00 | 65
2018-06-11 11:00 | 66
2018-06-11 12:00 | 67
2018-06-11 13:00 | 69
2018-06-11 14:00 | 69
2018-06-11 15:00 | 70
2018-06-11 16:00 | 69
2018-06-11 17:00 | 71
2018-06-11 18:00 | 73
2018-06-11 19:00 | 69
2018-06-11 20:00 | 66
2018-06-11 21:00 | 64
2018-06-11 22:00 | 63
2018-06-11 23:00 | 62
2018-06-12 | 62
2018-06-12 01:00 | 61
2018-06-12 02:00 | 61
2018-06-12 03:00 | 61
2018-06-12 04:00 | 61
2018-06-12 05:00 | 60
2018-06-12 06:00 | 60
2018-06-12 07:00 | 62
2018-06-12 08:00 | 65
2018-06-12 09:00 | 67
2018-06-12 10:00 | 70
2018-06-12 11:00 | 71
2018-06-12 12:00 | 72
2018-06-12 13:00 | 73
2018-06-12 14:00 | 74
2018-06-12 15:00 | 73
2018-06-12 16:00 | 73
2018-06-12 17:00 | 72
2018-06-12 18:00 | 72
2018-06-12 19:00 | 68
2018-06-12 20:00 | 67
2018-06-12 21:00 | 66
2018-06-12 22:00 | 64
2018-06-12 23:00 | 65
2018-06-13 | 66
2018-06-13 01:00 | 66
2018-06-13 02:00 | 65
2018-06-13 03:00 | 64
2018-06-13 04:00 | 66
2018-06-13 05:00 | 67
2018-06-13 06:00 | 68
2018-06-13 07:00 | 68
2018-06-13 08:00 | 68
2018-06-13 09:00 | 70
2018-06-13 10:00 | 72
2018-06-13 11:00 | 71
2018-06-13 12:00 | 71
2018-06-13 13:00 | 70
2018-06-13 14:00 | 70
2018-06-13 15:00 | 72
2018-06-13 16:00 | 74
2018-06-13 17:00 | 77
2018-06-13 18:00 | 75
2018-06-13 19:00 | 81
2018-06-13 20:00 | 80
2018-06-13 21:00 | 79
2018-06-13 22:00 | 79
2018-06-13 23:00 | 77
2018-06-14 | 77
2018-06-14 01:00 | 77
2018-06-14 02:00 | 76
2018-06-14 03:00 | 75
2018-06-14 04:00 | 73
2018-06-14 05:00 | 71
2018-06-14 06:00 | 72
2018-06-14 07:00 | 70
2018-06-14 08:00 | 71
2018-06-14 09:00 | 73
2018-06-14 10:00 | 75
2018-06-14 11:00 | 77
2018-06-14 12:00 | 81
2018-06-14 13:00 | 81
2018-06-14 14:00 | 82
2018-06-14 15:00 | 82
2018-06-14 16:00 | 84
2018-06-14 17:00 | 84
2018-06-14 18:00 | 82
2018-06-14 19:00 | 82
2018-06-14 20:00 | 81
2018-06-14 21:00 | 79
2018-06-14 22:00 | 77
2018-06-14 23:00 | 74
2018-06-15 | 72
2018-06-15 01:00 | 71
2018-06-15 02:00 | 70
2018-06-15 03:00 | 70
2018-06-15 04:00 | 68
2018-06-15 05:00 | 67
2018-06-15 06:00 | 66
2018-06-15 07:00 | 64
2018-06-15 08:00 | 66
2018-06-15 09:00 | 68
2018-06-15 10:00 | 70
2018-06-15 11:00 | 70
2018-06-15 12:00 | 72
2018-06-15 13:00 | 72
2018-06-15 14:00 | 73
2018-06-15 15:00 | 73
2018-06-15 16:00 | 75
2018-06-15 17:00 | 74
2018-06-15 18:00 | 75
2018-06-15 19:00 | 75
2018-06-15 20:00 | 75
2018-06-15 21:00 | 73
2018-06-15 22:00 | 72
2018-06-15 23:00 | 72
2018-06-16 | 70
2018-06-16 01:00 | 69
2018-06-16 02:00 | 70
2018-06-16 03:00 | 70
2018-06-16 04:00 | 70
2018-06-16 05:00 | 68
2018-06-16 06:00 | 68
2018-06-16 07:00 | 68
2018-06-16 08:00 | 70
2018-06-16 09:00 | 73
2018-06-16 10:00 | 75
2018-06-16 11:00 | 78
2018-06-16 12:00 | 81
2018-06-16 13:00 | 81
2018-06-16 14:00 | 82
2018-06-16 15:00 | 84
2018-06-16 16:00 | 84
2018-06-16 17:00 | 85
2018-06-16 18:00 | 86
2018-06-16 19:00 | 81
2018-06-16 20:00 | 78
2018-06-16 21:00 | 77
2018-06-16 22:00 | 79
2018-06-16 23:00 | 76
2018-06-17 | 75
2018-06-17 01:00 | 74
2018-06-17 02:00 | 74
2018-06-17 03:00 | 73
2018-06-17 04:00 | 72
2018-06-17 05:00 | 72
2018-06-17 06:00 | 70
2018-06-17 07:00 | 68
2018-06-17 08:00 | 73
2018-06-17 09:00 | 79
2018-06-17 10:00 | 81
2018-06-17 11:00 | 85
2018-06-17 12:00 | 88
2018-06-17 13:00 | 88
2018-06-17 14:00 | 89
2018-06-17 15:00 | 90
2018-06-17 16:00 | 90
2018-06-17 17:00 | 87
2018-06-17 18:00 | 84
2018-06-17 19:00 | 84
2018-06-17 20:00 | 82
2018-06-17 21:00 | 81
2018-06-17 22:00 | 79
2018-06-17 23:00 | 78
2018-06-18 | 79
2018-06-18 01:00 | 77
2018-06-18 02:00 | 76
2018-06-18 03:00 | 75
2018-06-18 04:00 | 75
2018-06-18 05:00 | 75
2018-06-18 06:00 | 73
2018-06-18 07:00 | 75
2018-06-18 08:00 | 77
2018-06-18 09:00 | 81
2018-06-18 10:00 | 84
2018-06-18 11:00 | 87
2018-06-18 12:00 | 90
2018-06-18 13:00 | 90
2018-06-18 14:00 | 89
2018-06-18 15:00 | 91
2018-06-18 16:00 | 91
2018-06-18 17:00 | 90
2018-06-18 18:00 | 90
2018-06-18 19:00 | 90
2018-06-18 20:00 | 91
2018-06-18 21:00 | 86
2018-06-18 22:00 | 81
2018-06-18 23:00 | 81
2018-06-19 | 81
2018-06-19 01:00 | 82
2018-06-19 02:00 | 79
2018-06-19 03:00 | 81
2018-06-19 04:00 | 81
2018-06-19 05:00 | 79
2018-06-19 06:00 | 81
2018-06-19 07:00 | 81
2018-06-19 08:00 | 80
2018-06-19 09:00 | 81
2018-06-19 10:00 | 82
2018-06-19 11:00 | 82
2018-06-19 12:00 | 82
2018-06-19 13:00 | 84
2018-06-19 14:00 | 86
2018-06-19 15:00 | 88
2018-06-19 16:00 | 88
2018-06-19 17:00 | 88
2018-06-19 18:00 | 88
2018-06-19 19:00 | 88
2018-06-19 20:00 | 84
2018-06-19 21:00 | 82
2018-06-19 22:00 | 79
2018-06-19 23:00 | 79
2018-06-20 | 77
2018-06-20 01:00 | 76
2018-06-20 02:00 | 74
2018-06-20 03:00 | 72
2018-06-20 04:00 | 72
2018-06-20 05:00 | 70
2018-06-20 06:00 | 70
2018-06-20 07:00 | 70
2018-06-20 08:00 | 71
2018-06-20 09:00 | 72
2018-06-20 10:00 | 72
2018-06-20 11:00 | 74
2018-06-20 12:00 | 75
2018-06-20 13:00 | 79
2018-06-20 14:00 | 82
2018-06-20 15:00 | 82
2018-06-20 16:00 | 82
2018-06-20 17:00 | 82
2018-06-20 18:00 | 79
2018-06-20 19:00 | 79
2018-06-20 20:00 | 76
2018-06-20 21:00 | 75
2018-06-20 22:00 | 73
2018-06-20 23:00 | 71
2018-06-21 | 73
2018-06-21 01:00 | 73
2018-06-21 02:00 | 69
2018-06-21 03:00 | 68
2018-06-21 04:00 | 66
2018-06-21 05:00 | 67
2018-06-21 06:00 | 66
2018-06-21 07:00 | 66
2018-06-21 08:00 | 67
2018-06-21 09:00 | 70
2018-06-21 10:00 | 73
2018-06-21 11:00 | 74
2018-06-21 12:00 | 77
2018-06-21 13:00 | 79
2018-06-21 14:00 | 82
2018-06-21 15:00 | 82
2018-06-21 16:00 | 84
2018-06-21 17:00 | 85
2018-06-21 18:00 | 86
2018-06-21 19:00 | 82
2018-06-21 20:00 | 83
2018-06-21 21:00 | 79
2018-06-21 22:00 | 79
2018-06-21 23:00 | 78
2018-06-22 | 75
2018-06-22 01:00 | 72
2018-06-22 02:00 | 71
2018-06-22 03:00 | 70
2018-06-22 04:00 | 70
2018-06-22 05:00 | 68
2018-06-22 06:00 | 68
2018-06-22 07:00 | 68
2018-06-22 08:00 | 68
2018-06-22 09:00 | 70
2018-06-22 10:00 | 72
2018-06-22 11:00 | 71
2018-06-22 12:00 | 70
2018-06-22 13:00 | 70
2018-06-22 14:00 | 73
2018-06-22 15:00 | 73
2018-06-22 16:00 | 73
2018-06-22 17:00 | 74
2018-06-22 18:00 | 73
2018-06-22 19:00 | 72
2018-06-22 20:00 | 70
2018-06-22 21:00 | 70
2018-06-22 22:00 | 68
2018-06-22 23:00 | 68
2018-06-23 | 64
2018-06-23 01:00 | 64
2018-06-23 02:00 | 64
2018-06-23 03:00 | 64
2018-06-23 04:00 | 64
2018-06-23 05:00 | 65
2018-06-23 06:00 | 66
2018-06-23 07:00 | 66
2018-06-23 08:00 | 65
2018-06-23 09:00 | 64
2018-06-23 10:00 | 64
2018-06-23 11:00 | 64
2018-06-23 12:00 | 64
2018-06-23 13:00 | 63
2018-06-23 14:00 | 64
2018-06-23 15:00 | 64
2018-06-23 16:00 | 64
2018-06-23 17:00 | 66
2018-06-23 18:00 | 66
2018-06-23 19:00 | 65
2018-06-23 20:00 | 65
2018-06-23 21:00 | 65
2018-06-23 22:00 | 65
2018-06-23 23:00 | 65
2018-06-24 | 65
2018-06-24 01:00 | 66
2018-06-24 02:00 | 66
2018-06-24 03:00 | 66
2018-06-24 04:00 | 67
2018-06-24 05:00 | 68
2018-06-24 06:00 | 68
2018-06-24 07:00 | 68
2018-06-24 08:00 | 68
2018-06-24 09:00 | 70
2018-06-24 10:00 | 74
2018-06-24 11:00 | 77
2018-06-24 12:00 | 80
2018-06-24 13:00 | 83
2018-06-24 14:00 | 79
2018-06-24 15:00 | 80
2018-06-24 16:00 | 80
2018-06-24 17:00 | 78
2018-06-24 18:00 | 80
2018-06-24 19:00 | 84
2018-06-24 20:00 | 87
2018-06-24 21:00 | 87
2018-06-24 22:00 | 74
2018-06-24 23:00 | 75
2018-06-25 | 73
2018-06-25 01:00 | 73
2018-06-25 02:00 | 73
2018-06-25 03:00 | 71
2018-06-25 04:00 | 69
2018-06-25 05:00 | 69
2018-06-25 06:00 | 69
2018-06-25 07:00 | 69
2018-06-25 08:00 | 71
2018-06-25 09:00 | 73
2018-06-25 10:00 | 75
2018-06-25 11:00 | 77
2018-06-25 12:00 | 77
2018-06-25 13:00 | 79
2018-06-25 14:00 | 78
2018-06-25 15:00 | 81
2018-06-25 16:00 | 81
2018-06-25 17:00 | 81
2018-06-25 18:00 | 81
2018-06-25 19:00 | 79
2018-06-25 20:00 | 79
2018-06-25 21:00 | 77
2018-06-25 22:00 | 73
2018-06-25 23:00 | 74
2018-06-26 | 72
2018-06-26 01:00 | 71
2018-06-26 02:00 | 69
2018-06-26 03:00 | 68
2018-06-26 04:00 | 66
2018-06-26 05:00 | 64
2018-06-26 06:00 | 64
2018-06-26 07:00 | 64
2018-06-26 08:00 | 66
2018-06-26 09:00 | 66
2018-06-26 10:00 | 70
2018-06-26 11:00 | 72
2018-06-26 12:00 | 75
2018-06-26 13:00 | 75
2018-06-26 14:00 | 75
2018-06-26 15:00 | 75
2018-06-26 16:00 | 75
2018-06-26 17:00 | 75
2018-06-26 18:00 | 73
2018-06-26 19:00 | 73
2018-06-26 20:00 | 73
2018-06-26 21:00 | 72
2018-06-26 22:00 | 72
2018-06-26 23:00 | 70
2018-06-27 | 70
2018-06-27 01:00 | 70
2018-06-27 02:00 | 69
2018-06-27 03:00 | 70
2018-06-27 04:00 | 68
2018-06-27 05:00 | 68
2018-06-27 06:00 | 68
2018-06-27 07:00 | 70
2018-06-27 08:00 | 70
2018-06-27 09:00 | 72
2018-06-27 10:00 | 73
2018-06-27 11:00 | 72
2018-06-27 12:00 | 73
2018-06-27 13:00 | 73
2018-06-27 14:00 | 75
2018-06-27 15:00 | 73
2018-06-27 16:00 | 73
2018-06-27 17:00 | 74
2018-06-27 18:00 | 73
2018-06-27 19:00 | 73
2018-06-27 20:00 | 72
2018-06-27 21:00 | 72
2018-06-27 22:00 | 72
2018-06-27 23:00 | 71
2018-06-28 | 72
2018-06-28 01:00 | 72
2018-06-28 02:00 | 72
2018-06-28 03:00 | 72
2018-06-28 04:00 | 72
2018-06-28 05:00 | 72
2018-06-28 06:00 | 72
2018-06-28 07:00 | 72
2018-06-28 08:00 | 72
2018-06-28 09:00 | 73
2018-06-28 10:00 | 75
2018-06-28 11:00 | 79
2018-06-28 12:00 | 83
2018-06-28 13:00 | 84
2018-06-28 14:00 | 84
2018-06-28 15:00 | 82
2018-06-28 16:00 | 84
2018-06-28 17:00 | 78
2018-06-28 18:00 | 79
2018-06-28 19:00 | 77
2018-06-28 20:00 | 79
2018-06-28 21:00 | 77
2018-06-28 22:00 | 79
2018-06-28 23:00 | 78
2018-06-29 | 79
2018-06-29 01:00 | 77
2018-06-29 02:00 | 75
2018-06-29 03:00 | 73
2018-06-29 04:00 | 73
2018-06-29 05:00 | 73
2018-06-29 06:00 | 72
2018-06-29 07:00 | 73
2018-06-29 08:00 | 76
2018-06-29 09:00 | 79
2018-06-29 10:00 | 81
2018-06-29 11:00 | 84
2018-06-29 12:00 | 84
2018-06-29 13:00 | 86
2018-06-29 14:00 | 88
2018-06-29 15:00 | 90
2018-06-29 16:00 | 91
2018-06-29 17:00 | 90
2018-06-29 18:00 | 90
2018-06-29 19:00 | 88
2018-06-29 20:00 | 87
2018-06-29 21:00 | 84
2018-06-29 22:00 | 84
2018-06-29 23:00 | 82
2018-06-30 | 81
2018-06-30 01:00 | 80
2018-06-30 02:00 | 79
2018-06-30 03:00 | 77
2018-06-30 04:00 | 79
2018-06-30 05:00 | 77
2018-06-30 06:00 | 73
2018-06-30 07:00 | 75
2018-06-30 08:00 | 78
2018-06-30 09:00 | 81
2018-06-30 10:00 | 84
2018-06-30 11:00 | 87
2018-06-30 12:00 | 88
2018-06-30 13:00 | 91
2018-06-30 14:00 | 93
2018-06-30 15:00 | 93
2018-06-30 16:00 | 95
2018-06-30 17:00 | 94
2018-06-30 18:00 | 95
2018-06-30 19:00 | 95
2018-06-30 20:00 | 89
2018-06-30 21:00 | 88
2018-06-30 22:00 | 86
2018-06-30 23:00 | 83
2018-07-01 | 84
2018-07-01 01:00 | 85
2018-07-01 02:00 | 83
2018-07-01 03:00 | 84
2018-07-01 04:00 | 82
2018-07-01 05:00 | 82
2018-07-01 06:00 | 79
2018-07-01 07:00 | 82
2018-07-01 08:00 | 83
2018-07-01 09:00 | 84
2018-07-01 10:00 | 88
2018-07-01 11:00 | 91
2018-07-01 12:00 | 93
2018-07-01 13:00 | 93
2018-07-01 14:00 | 94
2018-07-01 15:00 | 95
2018-07-01 16:00 | 95
2018-07-01 17:00 | 96
2018-07-01 18:00 | 97
2018-07-01 19:00 | 93
2018-07-01 20:00 | 92
2018-07-01 21:00 | 91
2018-07-01 22:00 | 90
2018-07-01 23:00 | 87
2018-07-02 | 88
2018-07-02 01:00 | 85
2018-07-02 02:00 | 88
2018-07-02 03:00 | 88
2018-07-02 04:00 | 86
2018-07-02 05:00 | 83
2018-07-02 06:00 | 79
2018-07-02 07:00 | 79
2018-07-02 08:00 | 78
2018-07-02 09:00 | 79
2018-07-02 10:00 | 84
2018-07-02 11:00 | 84
2018-07-02 12:00 | 86
2018-07-02 13:00 | 93
2018-07-02 14:00 | 94
2018-07-02 15:00 | 93
2018-07-02 16:00 | 93
2018-07-02 17:00 | 92
2018-07-02 18:00 | 90
2018-07-02 19:00 | 88
2018-07-02 20:00 | 85
2018-07-02 21:00 | 84
2018-07-02 22:00 | 82
2018-07-02 23:00 | 82
2018-07-03 | 82
2018-07-03 01:00 | 80
2018-07-03 02:00 | 80
2018-07-03 03:00 | 81
2018-07-03 04:00 | 79
2018-07-03 05:00 | 80
2018-07-03 06:00 | 81
2018-07-03 07:00 | 81
2018-07-03 08:00 | 80
2018-07-03 09:00 | 81
2018-07-03 10:00 | 84
2018-07-03 11:00 | 88
2018-07-03 12:00 | 90
2018-07-03 13:00 | 91
2018-07-03 14:00 | 90
2018-07-03 15:00 | 86
2018-07-03 16:00 | 84
2018-07-03 17:00 | 84
2018-07-03 18:00 | 84
2018-07-03 19:00 | 82
2018-07-03 20:00 | 80
2018-07-03 21:00 | 82
2018-07-03 22:00 | 81
2018-07-03 23:00 | 80
2018-07-04 | 81
2018-07-04 01:00 | 79
2018-07-04 02:00 | 79
2018-07-04 03:00 | 79
2018-07-04 04:00 | 79
2018-07-04 05:00 | 79
2018-07-04 06:00 | 81
2018-07-04 07:00 | 81
2018-07-04 08:00 | 79
2018-07-04 09:00 | 81
2018-07-04 10:00 | 84
2018-07-04 11:00 | 85
2018-07-04 12:00 | 88
2018-07-04 13:00 | 88
2018-07-04 14:00 | 89
2018-07-04 15:00 | 88
2018-07-04 16:00 | 84
2018-07-04 17:00 | 86
2018-07-04 18:00 | 84
2018-07-04 19:00 | 82
2018-07-04 20:00 | 82
2018-07-04 21:00 | 82
2018-07-04 22:00 | 81
2018-07-04 23:00 | 80
2018-07-05 | 81
2018-07-05 01:00 | 79
2018-07-05 02:00 | 79
2018-07-05 03:00 | 79
2018-07-05 04:00 | 79
2018-07-05 05:00 | 79
2018-07-05 06:00 | 79
2018-07-05 07:00 | 79
2018-07-05 08:00 | 80
2018-07-05 09:00 | 82
2018-07-05 10:00 | 82
2018-07-05 11:00 | 86
2018-07-05 12:00 | 88
2018-07-05 13:00 | 90
2018-07-05 14:00 | 89
2018-07-05 15:00 | 88
2018-07-05 16:00 | 88
2018-07-05 17:00 | 88
2018-07-05 18:00 | 88
2018-07-05 19:00 | 84
2018-07-05 20:00 | 84
2018-07-05 21:00 | 82
2018-07-05 22:00 | 82
2018-07-05 23:00 | 83
2018-07-06 | 82
2018-07-06 01:00 | 81
2018-07-06 02:00 | 80
2018-07-06 03:00 | 81
2018-07-06 04:00 | 81
2018-07-06 05:00 | 81
2018-07-06 06:00 | 81
2018-07-06 07:00 | 81
2018-07-06 08:00 | 79
2018-07-06 09:00 | 77
2018-07-06 10:00 | 77
2018-07-06 11:00 | 79
2018-07-06 12:00 | 81
2018-07-06 13:00 | 81
2018-07-06 14:00 | 82
2018-07-06 15:00 | 81
2018-07-06 16:00 | 81
2018-07-06 17:00 | 81
2018-07-06 18:00 | 82
2018-07-06 19:00 | 82
2018-07-06 20:00 | 80
2018-07-06 21:00 | 79
2018-07-06 22:00 | 75
2018-07-06 23:00 | 75
2018-07-07 | 73
2018-07-07 01:00 | 71
2018-07-07 02:00 | 69
2018-07-07 03:00 | 66
2018-07-07 04:00 | 66
2018-07-07 05:00 | 65
2018-07-07 06:00 | 64
2018-07-07 07:00 | 64
2018-07-07 08:00 | 66
2018-07-07 09:00 | 68
2018-07-07 10:00 | 70
2018-07-07 11:00 | 71
2018-07-07 12:00 | 72
2018-07-07 13:00 | 73
2018-07-07 14:00 | 75
2018-07-07 15:00 | 77
2018-07-07 16:00 | 75
2018-07-07 17:00 | 75
2018-07-07 18:00 | 73
2018-07-07 19:00 | 72
2018-07-07 20:00 | 71
2018-07-07 21:00 | 70
2018-07-07 22:00 | 70
2018-07-07 23:00 | 68
2018-07-08 | 68
2018-07-08 01:00 | 68
2018-07-08 02:00 | 68
2018-07-08 03:00 | 68
2018-07-08 04:00 | 66
2018-07-08 05:00 | 67
2018-07-08 06:00 | 68
2018-07-08 07:00 | 70
2018-07-08 08:00 | 70
2018-07-08 09:00 | 72
2018-07-08 10:00 | 73
2018-07-08 11:00 | 76
2018-07-08 12:00 | 79
2018-07-08 13:00 | 81
2018-07-08 14:00 | 82
2018-07-08 15:00 | 82
2018-07-08 16:00 | 82
2018-07-08 17:00 | 80
2018-07-08 18:00 | 79
2018-07-08 19:00 | 79
2018-07-08 20:00 | 76
2018-07-08 21:00 | 74
2018-07-08 22:00 | 73
2018-07-08 23:00 | 73
2018-07-09 | 72
2018-07-09 01:00 | 72
2018-07-09 02:00 | 71
2018-07-09 03:00 | 71
2018-07-09 04:00 | 70
2018-07-09 05:00 | 70
2018-07-09 06:00 | 70
2018-07-09 07:00 | 72
2018-07-09 08:00 | 75
2018-07-09 09:00 | 77
2018-07-09 10:00 | 80
2018-07-09 11:00 | 83
2018-07-09 12:00 | 85
2018-07-09 13:00 | 87
2018-07-09 14:00 | 89
2018-07-09 15:00 | 88
2018-07-09 16:00 | 88
2018-07-09 17:00 | 85
2018-07-09 18:00 | 84
2018-07-09 19:00 | 80
2018-07-09 20:00 | 80
2018-07-09 21:00 | 79
2018-07-09 22:00 | 79
2018-07-09 23:00 | 78
2018-07-10 | 77
2018-07-10 01:00 | 76
2018-07-10 02:00 | 75
2018-07-10 03:00 | 76
2018-07-10 04:00 | 75
2018-07-10 05:00 | 75
2018-07-10 06:00 | 74
2018-07-10 07:00 | 76
2018-07-10 08:00 | 78
2018-07-10 09:00 | 80
2018-07-10 10:00 | 84
2018-07-10 11:00 | 87
2018-07-10 12:00 | 92
2018-07-10 13:00 | 92
2018-07-10 14:00 | 93
2018-07-10 15:00 | 94
2018-07-10 16:00 | 95
2018-07-10 17:00 | 94
2018-07-10 18:00 | 95
2018-07-10 19:00 | 90
2018-07-10 20:00 | 87
2018-07-10 21:00 | 84
2018-07-10 22:00 | 82
2018-07-10 23:00 | 82
2018-07-11 | 80
2018-07-11 01:00 | 82
2018-07-11 02:00 | 81
2018-07-11 03:00 | 80
2018-07-11 04:00 | 80
2018-07-11 05:00 | 78
2018-07-11 06:00 | 77
2018-07-11 07:00 | 77
2018-07-11 08:00 | 77
2018-07-11 09:00 | 78
2018-07-11 10:00 | 81
2018-07-11 11:00 | 83
2018-07-11 12:00 | 83
2018-07-11 13:00 | 84
2018-07-11 14:00 | 83
2018-07-11 15:00 | 86
2018-07-11 16:00 | 86
2018-07-11 17:00 | 86
2018-07-11 18:00 | 82
2018-07-11 19:00 | 81
2018-07-11 20:00 | 78
2018-07-11 21:00 | 77
2018-07-11 22:00 | 76
2018-07-11 23:00 | 76
2018-07-12 | 76
2018-07-12 01:00 | 76
2018-07-12 02:00 | 75
2018-07-12 03:00 | 75
2018-07-12 04:00 | 75
2018-07-12 05:00 | 72
2018-07-12 06:00 | 68
2018-07-12 07:00 | 70
2018-07-12 08:00 | 72
2018-07-12 09:00 | 74
2018-07-12 10:00 | 76
2018-07-12 11:00 | 76
2018-07-12 12:00 | 80
2018-07-12 13:00 | 82
2018-07-12 14:00 | 83
2018-07-12 15:00 | 82
2018-07-12 16:00 | 85
2018-07-12 17:00 | 83
2018-07-12 18:00 | 81
2018-07-12 19:00 | 79
2018-07-12 20:00 | 77
2018-07-12 21:00 | 76
2018-07-12 22:00 | 75
2018-07-12 23:00 | 74
2018-07-13 | 74
2018-07-13 01:00 | 75
2018-07-13 02:00 | 74
2018-07-13 03:00 | 74
2018-07-13 04:00 | 73
2018-07-13 05:00 | 73
2018-07-13 06:00 | 71
2018-07-13 07:00 | 73
2018-07-13 08:00 | 73
2018-07-13 09:00 | 77
2018-07-13 10:00 | 80
2018-07-13 11:00 | 82
2018-07-13 12:00 | 82
2018-07-13 13:00 | 84
2018-07-13 14:00 | 84
2018-07-13 15:00 | 84
2018-07-13 16:00 | 83
2018-07-13 17:00 | 82
2018-07-13 18:00 | 82
2018-07-13 19:00 | 81
2018-07-13 20:00 | 79
2018-07-13 21:00 | 76
2018-07-13 22:00 | 76
2018-07-13 23:00 | 75
2018-07-14 | 76
2018-07-14 01:00 | 75
2018-07-14 02:00 | 75
2018-07-14 03:00 | 74
2018-07-14 04:00 | 75
2018-07-14 05:00 | 74
2018-07-14 06:00 | 74
2018-07-14 07:00 | 75
2018-07-14 08:00 | 77
2018-07-14 09:00 | 79
2018-07-14 10:00 | 81
2018-07-14 11:00 | 83
2018-07-14 12:00 | 87
2018-07-14 13:00 | 87
2018-07-14 14:00 | 89
2018-07-14 15:00 | 89
2018-07-14 16:00 | 90
2018-07-14 17:00 | 89
2018-07-14 18:00 | 88
2018-07-14 19:00 | 89
2018-07-14 20:00 | 89
2018-07-14 21:00 | 88
2018-07-14 22:00 | 87
2018-07-14 23:00 | 86
2018-07-15 | 82
2018-07-15 01:00 | 72
2018-07-15 02:00 | 74
2018-07-15 03:00 | 73
2018-07-15 04:00 | 73
2018-07-15 05:00 | 72
2018-07-15 06:00 | 72
2018-07-15 07:00 | 73
2018-07-15 08:00 | 74
2018-07-15 09:00 | 73
2018-07-15 10:00 | 74
2018-07-15 11:00 | 75
2018-07-15 12:00 | 77
2018-07-15 13:00 | 77
2018-07-15 14:00 | 81
2018-07-15 15:00 | 81
2018-07-15 16:00 | 82
2018-07-15 17:00 | 86
2018-07-15 18:00 | 86
2018-07-15 19:00 | 86
2018-07-15 20:00 | 84
2018-07-15 21:00 | 82
2018-07-15 22:00 | 82
2018-07-15 23:00 | 80
2018-07-16 | 81
2018-07-16 01:00 | 80
2018-07-16 02:00 | 80
2018-07-16 03:00 | 80
2018-07-16 04:00 | 79
2018-07-16 05:00 | 78
2018-07-16 06:00 | 79
2018-07-16 07:00 | 79
2018-07-16 08:00 | 81
2018-07-16 09:00 | 82
2018-07-16 10:00 | 85
2018-07-16 11:00 | 88
2018-07-16 12:00 | 90
2018-07-16 13:00 | 91
2018-07-16 14:00 | 92
2018-07-16 15:00 | 90
2018-07-16 16:00 | 89
2018-07-16 17:00 | 90
2018-07-16 18:00 | 86
2018-07-16 19:00 | 85
2018-07-16 20:00 | 85
2018-07-16 21:00 | 83
2018-07-16 22:00 | 83
2018-07-16 23:00 | 82
2018-07-17 | 83
2018-07-17 01:00 | 84
2018-07-17 02:00 | 83
2018-07-17 03:00 | 82
2018-07-17 04:00 | 81
2018-07-17 05:00 | 80
2018-07-17 06:00 | 79
2018-07-17 07:00 | 80
2018-07-17 08:00 | 81
2018-07-17 09:00 | 83
2018-07-17 10:00 | 86
2018-07-17 11:00 | 88
2018-07-17 12:00 | 88
2018-07-17 13:00 | 88
2018-07-17 14:00 | 88
2018-07-17 15:00 | 80.5
2018-07-17 16:00 | 73
2018-07-17 17:00 | 75
2018-07-17 18:00 | 75
2018-07-17 19:00 | 74
2018-07-17 20:00 | 73
2018-07-17 21:00 | 73
2018-07-17 22:00 | 74
2018-07-17 23:00 | 75
2018-07-18 | 74
2018-07-18 01:00 | 74
2018-07-18 02:00 | 73
2018-07-18 03:00 | 74
2018-07-18 04:00 | 74
2018-07-18 05:00 | 72
2018-07-18 06:00 | 71
2018-07-18 07:00 | 72
2018-07-18 08:00 | 73
2018-07-18 09:00 | 75
2018-07-18 10:00 | 77
2018-07-18 11:00 | 79
2018-07-18 12:00 | 81
2018-07-18 13:00 | 82
2018-07-18 14:00 | 82
2018-07-18 15:00 | 84
2018-07-18 16:00 | 84
2018-07-18 17:00 | 85
2018-07-18 18:00 | 85
2018-07-18 19:00 | 84
2018-07-18 20:00 | 82
2018-07-18 21:00 | 80
2018-07-18 22:00 | 80
2018-07-18 23:00 | 77
2018-07-19 | 76
2018-07-19 01:00 | 75
2018-07-19 02:00 | 73
2018-07-19 03:00 | 71
2018-07-19 04:00 | 71
2018-07-19 05:00 | 70
2018-07-19 06:00 | 69
2018-07-19 07:00 | 69
2018-07-19 08:00 | 70
2018-07-19 09:00 | 72
2018-07-19 10:00 | 73
2018-07-19 11:00 | 74
2018-07-19 12:00 | 77
2018-07-19 13:00 | 78
2018-07-19 14:00 | 79
2018-07-19 15:00 | 81
2018-07-19 16:00 | 83
2018-07-19 17:00 | 82
2018-07-19 18:00 | 81
2018-07-19 19:00 | 80
2018-07-19 20:00 | 78
2018-07-19 21:00 | 76
2018-07-19 22:00 | 75
2018-07-19 23:00 | 74
2018-07-20 | 74
2018-07-20 01:00 | 74
2018-07-20 02:00 | 73
2018-07-20 03:00 | 73
2018-07-20 04:00 | 73
2018-07-20 05:00 | 73
2018-07-20 06:00 | 72
2018-07-20 07:00 | 70
2018-07-20 08:00 | 72
2018-07-20 09:00 | 74
2018-07-20 10:00 | 76
2018-07-20 11:00 | 79
2018-07-20 12:00 | 79
2018-07-20 13:00 | 81
2018-07-20 14:00 | 82
2018-07-20 15:00 | 81
2018-07-20 16:00 | 82
2018-07-20 17:00 | 82
2018-07-20 18:00 | 81
2018-07-20 19:00 | 79
2018-07-20 20:00 | 76
2018-07-20 21:00 | 75
2018-07-20 22:00 | 75
2018-07-20 23:00 | 74
2018-07-21 | 73
2018-07-21 01:00 | 73
2018-07-21 02:00 | 73
2018-07-21 03:00 | 73
2018-07-21 04:00 | 72
2018-07-21 05:00 | 70
2018-07-21 06:00 | 70
2018-07-21 07:00 | 72
2018-07-21 08:00 | 72
2018-07-21 09:00 | 73
2018-07-21 10:00 | 75
2018-07-21 11:00 | 77
2018-07-21 12:00 | 77
2018-07-21 13:00 | 75
2018-07-21 14:00 | 76
2018-07-21 15:00 | 75
2018-07-21 16:00 | 75
2018-07-21 17:00 | 76
2018-07-21 18:00 | 73
2018-07-21 19:00 | 72
2018-07-21 20:00 | 71
2018-07-21 21:00 | 70
2018-07-21 22:00 | 66
2018-07-21 23:00 | 68
2018-07-22 | 69
2018-07-22 01:00 | 72
2018-07-22 02:00 | 74
2018-07-22 03:00 | 74
2018-07-22 04:00 | 76
2018-07-22 05:00 | 76
2018-07-22 06:00 | 75
2018-07-22 07:00 | 75
2018-07-22 08:00 | 75
2018-07-22 09:00 | 74
2018-07-22 10:00 | 76
2018-07-22 11:00 | 77
2018-07-22 12:00 | 79
2018-07-22 13:00 | 82
2018-07-22 14:00 | 82
2018-07-22 15:00 | 82
2018-07-22 16:00 | 82
2018-07-22 17:00 | 80
2018-07-22 18:00 | 79
2018-07-22 19:00 | 79
2018-07-22 20:00 | 77
2018-07-22 21:00 | 77
2018-07-22 22:00 | 78
2018-07-22 23:00 | 77
2018-07-23 | 78
2018-07-23 01:00 | 78
2018-07-23 02:00 | 78
2018-07-23 03:00 | 78
2018-07-23 04:00 | 78
2018-07-23 05:00 | 78
2018-07-23 06:00 | 77
2018-07-23 07:00 | 77
2018-07-23 08:00 | 77
2018-07-23 09:00 | 76
2018-07-23 10:00 | 77
2018-07-23 11:00 | 79
2018-07-23 12:00 | 81
2018-07-23 13:00 | 82
2018-07-23 14:00 | 84
2018-07-23 15:00 | 86
2018-07-23 16:00 | 85
2018-07-23 17:00 | 84
2018-07-23 18:00 | 84
2018-07-23 19:00 | 81
2018-07-23 20:00 | 81
2018-07-23 21:00 | 80
2018-07-23 22:00 | 79
2018-07-23 23:00 | 79
2018-07-24 | 79
2018-07-24 01:00 | 79
2018-07-24 02:00 | 78
2018-07-24 03:00 | 77
2018-07-24 04:00 | 78
2018-07-24 05:00 | 77
2018-07-24 06:00 | 77
2018-07-24 07:00 | 78
2018-07-24 08:00 | 81
2018-07-24 09:00 | 82
2018-07-24 10:00 | 83
2018-07-24 11:00 | 84
2018-07-24 12:00 | 84
2018-07-24 13:00 | 84
2018-07-24 14:00 | 85
2018-07-24 15:00 | 86
2018-07-24 16:00 | 84
2018-07-24 17:00 | 84
2018-07-24 18:00 | 82
2018-07-24 19:00 | 82
2018-07-24 20:00 | 81
2018-07-24 21:00 | 81
2018-07-24 22:00 | 81
2018-07-24 23:00 | 79
2018-07-25 | 79
2018-07-25 01:00 | 79
2018-07-25 02:00 | 79
2018-07-25 03:00 | 79
2018-07-25 04:00 | 79
2018-07-25 05:00 | 77
2018-07-25 06:00 | 79
2018-07-25 07:00 | 73
2018-07-25 08:00 | 75
2018-07-25 09:00 | 79
2018-07-25 10:00 | 77
2018-07-25 11:00 | 77
2018-07-25 12:00 | 78
2018-07-25 13:00 | 79
2018-07-25 14:00 | 79
2018-07-25 15:00 | 80
2018-07-25 16:00 | 79
2018-07-25 17:00 | 79
2018-07-25 18:00 | 79
2018-07-25 19:00 | 77
2018-07-25 20:00 | 77
2018-07-25 21:00 | 76
2018-07-25 22:00 | 76
2018-07-25 23:00 | 76
2018-07-26 | 75
2018-07-26 01:00 | 75
2018-07-26 02:00 | 75
2018-07-26 03:00 | 75
2018-07-26 04:00 | 75
2018-07-26 05:00 | 75
2018-07-26 06:00 | 75
2018-07-26 07:00 | 75
2018-07-26 08:00 | 77
2018-07-26 09:00 | 77
2018-07-26 10:00 | 78
2018-07-26 11:00 | 79
2018-07-26 12:00 | 80
2018-07-26 13:00 | 81
2018-07-26 14:00 | 85
2018-07-26 15:00 | 87
2018-07-26 16:00 | 86
2018-07-26 17:00 | 88
2018-07-26 18:00 | 85
2018-07-26 19:00 | 85
2018-07-26 20:00 | 84
2018-07-26 21:00 | 86
2018-07-26 22:00 | 85
2018-07-26 23:00 | 83
2018-07-27 | 83
2018-07-27 01:00 | 82
2018-07-27 02:00 | 80
2018-07-27 03:00 | 80
2018-07-27 04:00 | 79
2018-07-27 05:00 | 78
2018-07-27 06:00 | 77
2018-07-27 07:00 | 78
2018-07-27 08:00 | 79
2018-07-27 09:00 | 82
2018-07-27 10:00 | 84
2018-07-27 11:00 | 86
2018-07-27 12:00 | 88
2018-07-27 13:00 | 89
2018-07-27 14:00 | 89
2018-07-27 15:00 | 88
2018-07-27 16:00 | 84
2018-07-27 17:00 | 83
2018-07-27 18:00 | 80
2018-07-27 19:00 | 78
2018-07-27 20:00 | 78
2018-07-27 21:00 | 73
2018-07-27 22:00 | 74
2018-07-27 23:00 | 73
2018-07-28 | 75
2018-07-28 01:00 | 75
2018-07-28 02:00 | 75
2018-07-28 03:00 | 75
2018-07-28 04:00 | 72
2018-07-28 05:00 | 72
2018-07-28 06:00 | 72
2018-07-28 07:00 | 73
2018-07-28 08:00 | 75
2018-07-28 09:00 | 78
2018-07-28 10:00 | 81
2018-07-28 11:00 | 80
2018-07-28 12:00 | 83
2018-07-28 13:00 | 84
2018-07-28 14:00 | 84
2018-07-28 15:00 | 85
2018-07-28 16:00 | 88
2018-07-28 17:00 | 89
2018-07-28 18:00 | 85
2018-07-28 19:00 | 84
2018-07-28 20:00 | 82
2018-07-28 21:00 | 82
2018-07-28 22:00 | 83
2018-07-28 23:00 | 83
2018-07-29 | 81
2018-07-29 01:00 | 79
2018-07-29 02:00 | 78
2018-07-29 03:00 | 76
2018-07-29 04:00 | 75
2018-07-29 05:00 | 74
2018-07-29 06:00 | 73
2018-07-29 07:00 | 73
2018-07-29 08:00 | 74
2018-07-29 09:00 | 75
2018-07-29 10:00 | 76
2018-07-29 11:00 | 78
2018-07-29 12:00 | 78
2018-07-29 13:00 | 80
2018-07-29 14:00 | 82
2018-07-29 15:00 | 83
2018-07-29 16:00 | 82
2018-07-29 17:00 | 84
2018-07-29 18:00 | 83
2018-07-29 19:00 | 82
2018-07-29 20:00 | 81
2018-07-29 21:00 | 80
2018-07-29 22:00 | 80
2018-07-29 23:00 | 80
2018-07-30 | 79
2018-07-30 01:00 | 79
2018-07-30 02:00 | 78
2018-07-30 03:00 | 77
2018-07-30 04:00 | 74
2018-07-30 05:00 | 75
2018-07-30 06:00 | 74
2018-07-30 07:00 | 73
2018-07-30 08:00 | 74
2018-07-30 09:00 | 76
2018-07-30 10:00 | 77
2018-07-30 11:00 | 77
2018-07-30 12:00 | 79
2018-07-30 13:00 | 79
2018-07-30 14:00 | 81
2018-07-30 15:00 | 81
2018-07-30 16:00 | 81
2018-07-30 17:00 | 79
2018-07-30 18:00 | 79
2018-07-30 19:00 | 77
2018-07-30 20:00 | 76
2018-07-30 21:00 | 75
2018-07-30 22:00 | 73
2018-07-30 23:00 | 74
2018-07-31 | 73
2018-07-31 01:00 | 73
2018-07-31 02:00 | 73
2018-07-31 03:00 | 72
2018-07-31 04:00 | 73
2018-07-31 05:00 | 71
2018-07-31 06:00 | 72
2018-07-31 07:00 | 72
2018-07-31 08:00 | 73
2018-07-31 09:00 | 75
2018-07-31 10:00 | 77
2018-07-31 11:00 | 80
2018-07-31 12:00 | 81
2018-07-31 13:00 | 82
2018-07-31 14:00 | 82
2018-07-31 15:00 | 81
2018-07-31 16:00 | 81
2018-07-31 17:00 | 80
2018-07-31 18:00 | 81
2018-07-31 19:00 | 79
2018-07-31 20:00 | 77
2018-07-31 21:00 | 77
2018-07-31 22:00 | 75
2018-07-31 23:00 | 76
2018-08-01 | 75
2018-08-01 01:00 | 76
2018-08-01 02:00 | 76
2018-08-01 03:00 | 75
2018-08-01 04:00 | 75
2018-08-01 05:00 | 75
2018-08-01 06:00 | 77
2018-08-01 07:00 | 79
2018-08-01 08:00 | 78
2018-08-01 09:00 | 79
2018-08-01 10:00 | 81
2018-08-01 11:00 | 80
2018-08-01 12:00 | 82
2018-08-01 13:00 | 88
2018-08-01 14:00 | 88
2018-08-01 15:00 | 84
2018-08-01 16:00 | 91
2018-08-01 17:00 | 90
2018-08-01 18:00 | 90
2018-08-01 19:00 | 86
2018-08-01 20:00 | 85
2018-08-01 21:00 | 84
2018-08-01 22:00 | 84
2018-08-01 23:00 | 85
2018-08-02 | 82
2018-08-02 01:00 | 83
2018-08-02 02:00 | 82
2018-08-02 03:00 | 81
2018-08-02 04:00 | 81
2018-08-02 05:00 | 80
2018-08-02 06:00 | 79
2018-08-02 07:00 | 79
2018-08-02 08:00 | 81
2018-08-02 09:00 | 82
2018-08-02 10:00 | 82
2018-08-02 11:00 | 86
2018-08-02 12:00 | 88
2018-08-02 13:00 | 88
2018-08-02 14:00 | 88
2018-08-02 15:00 | 90
2018-08-02 16:00 | 88
2018-08-02 17:00 | 89
2018-08-02 18:00 | 90
2018-08-02 19:00 | 86
2018-08-02 20:00 | 83
2018-08-02 21:00 | 82
2018-08-02 22:00 | 82
2018-08-02 23:00 | 80
2018-08-03 | 81
2018-08-03 01:00 | 80
2018-08-03 02:00 | 80
2018-08-03 03:00 | 81
2018-08-03 04:00 | 81
2018-08-03 05:00 | 80
2018-08-03 06:00 | 79
2018-08-03 07:00 | 81
2018-08-03 08:00 | 80
2018-08-03 09:00 | 81
2018-08-03 10:00 | 82
2018-08-03 11:00 | 84
2018-08-03 12:00 | 84
2018-08-03 13:00 | 86
2018-08-03 14:00 | 87
2018-08-03 15:00 | 79
2018-08-03 16:00 | 77
2018-08-03 17:00 | 79
2018-08-03 18:00 | 82
2018-08-03 19:00 | 81
2018-08-03 20:00 | 81
2018-08-03 21:00 | 79
2018-08-03 22:00 | 79
2018-08-03 23:00 | 80
2018-08-04 | 79
2018-08-04 01:00 | 79
2018-08-04 02:00 | 78
2018-08-04 03:00 | 79
2018-08-04 04:00 | 77
2018-08-04 05:00 | 77
2018-08-04 06:00 | 79
2018-08-04 07:00 | 79
2018-08-04 08:00 | 79
2018-08-04 09:00 | 81
2018-08-04 10:00 | 73
2018-08-04 11:00 | 75
2018-08-04 12:00 | 75
2018-08-04 13:00 | 79
2018-08-04 14:00 | 79
2018-08-04 15:00 | 84
2018-08-04 16:00 | 84
2018-08-04 17:00 | 88
2018-08-04 18:00 | 88
2018-08-04 19:00 | 88
2018-08-04 20:00 | 87
2018-08-04 21:00 | 88
2018-08-04 22:00 | 84
2018-08-04 23:00 | 84
2018-08-05 | 81
2018-08-05 01:00 | 81
2018-08-05 02:00 | 80
2018-08-05 03:00 | 79
2018-08-05 04:00 | 79
2018-08-05 05:00 | 79
2018-08-05 06:00 | 79
2018-08-05 07:00 | 79
2018-08-05 08:00 | 80
2018-08-05 09:00 | 82
2018-08-05 10:00 | 84
2018-08-05 11:00 | 88
2018-08-05 12:00 | 90
2018-08-05 13:00 | 91
2018-08-05 14:00 | 93
2018-08-05 15:00 | 93
2018-08-05 16:00 | 93
2018-08-05 17:00 | 91
2018-08-05 18:00 | 90
2018-08-05 19:00 | 90
2018-08-05 20:00 | 88
2018-08-05 21:00 | 86
2018-08-05 22:00 | 88
2018-08-05 23:00 | 87
2018-08-06 | 84
2018-08-06 01:00 | 85
2018-08-06 02:00 | 83
2018-08-06 03:00 | 82
2018-08-06 04:00 | 82
2018-08-06 05:00 | 83
2018-08-06 06:00 | 81
2018-08-06 07:00 | 81
2018-08-06 08:00 | 84
2018-08-06 09:00 | 84
2018-08-06 10:00 | 88
2018-08-06 11:00 | 91
2018-08-06 12:00 | 91
2018-08-06 13:00 | 91
2018-08-06 14:00 | 93
2018-08-06 15:00 | 93
2018-08-06 16:00 | 95
2018-08-06 17:00 | 90
2018-08-06 18:00 | 91
2018-08-06 19:00 | 90
2018-08-06 20:00 | 90
2018-08-06 21:00 | 90
2018-08-06 22:00 | 88
2018-08-06 23:00 | 86
2018-08-07 | 84
2018-08-07 01:00 | 84
2018-08-07 02:00 | 83
2018-08-07 03:00 | 82
2018-08-07 04:00 | 82
2018-08-07 05:00 | 81
2018-08-07 06:00 | 81
2018-08-07 07:00 | 81
2018-08-07 08:00 | 81
2018-08-07 09:00 | 82
2018-08-07 10:00 | 84
2018-08-07 11:00 | 88
2018-08-07 12:00 | 90
2018-08-07 13:00 | 91
2018-08-07 14:00 | 90
2018-08-07 15:00 | 90
2018-08-07 16:00 | 90
2018-08-07 17:00 | 89
2018-08-07 18:00 | 88
2018-08-07 19:00 | 84
2018-08-07 20:00 | 79
2018-08-07 21:00 | 75
2018-08-07 22:00 | 79
2018-08-07 23:00 | 79
2018-08-08 | 79
2018-08-08 01:00 | 81
2018-08-08 02:00 | 80
2018-08-08 03:00 | 81
2018-08-08 04:00 | 79
2018-08-08 05:00 | 77
2018-08-08 06:00 | 79
2018-08-08 07:00 | 79
2018-08-08 08:00 | 81
2018-08-08 09:00 | 82
2018-08-08 10:00 | 84
2018-08-08 11:00 | 87
2018-08-08 12:00 | 88
2018-08-08 13:00 | 90
2018-08-08 14:00 | 90
2018-08-08 15:00 | 91
2018-08-08 16:00 | 91
2018-08-08 17:00 | 90
2018-08-08 18:00 | 88
2018-08-08 19:00 | 88
2018-08-08 20:00 | 85
2018-08-08 21:00 | 84
2018-08-08 22:00 | 84
2018-08-08 23:00 | 85
2018-08-09 | 84
2018-08-09 01:00 | 84
2018-08-09 02:00 | 83
2018-08-09 03:00 | 75
2018-08-09 04:00 | 77
2018-08-09 05:00 | 78
2018-08-09 06:00 | 79
2018-08-09 07:00 | 79
2018-08-09 08:00 | 78
2018-08-09 09:00 | 81
2018-08-09 10:00 | 82
2018-08-09 11:00 | 85
2018-08-09 12:00 | 86
2018-08-09 13:00 | 88
2018-08-09 14:00 | 89
2018-08-09 15:00 | 88
2018-08-09 16:00 | 88
2018-08-09 17:00 | 89
2018-08-09 18:00 | 90
2018-08-09 19:00 | 88
2018-08-09 20:00 | 85
2018-08-09 21:00 | 84
2018-08-09 22:00 | 82
2018-08-09 23:00 | 82
2018-08-10 | 81
2018-08-10 01:00 | 79
2018-08-10 02:00 | 78
2018-08-10 03:00 | 77
2018-08-10 04:00 | 75
2018-08-10 05:00 | 76
2018-08-10 06:00 | 77
2018-08-10 07:00 | 77
2018-08-10 08:00 | 78
2018-08-10 09:00 | 81
2018-08-10 10:00 | 82
2018-08-10 11:00 | 84
2018-08-10 12:00 | 86
2018-08-10 13:00 | 88
2018-08-10 14:00 | 88
2018-08-10 15:00 | 90
2018-08-10 16:00 | 90
2018-08-10 17:00 | 88
2018-08-10 18:00 | 86
2018-08-10 19:00 | 84
2018-08-10 20:00 | 83
2018-08-10 21:00 | 82
2018-08-10 22:00 | 82
2018-08-10 23:00 | 82
2018-08-11 | 81
2018-08-11 01:00 | 82
2018-08-11 02:00 | 83
2018-08-11 03:00 | 75
2018-08-11 04:00 | 75
2018-08-11 05:00 | 75
2018-08-11 06:00 | 75
2018-08-11 07:00 | 77
2018-08-11 08:00 | 76
2018-08-11 09:00 | 73
2018-08-11 10:00 | 73
2018-08-11 11:00 | 73
2018-08-11 12:00 | 75
2018-08-11 13:00 | 75
2018-08-11 14:00 | 76
2018-08-11 15:00 | 77
2018-08-11 16:00 | 75
2018-08-11 17:00 | 75
2018-08-11 18:00 | 75
2018-08-11 19:00 | 77
2018-08-11 20:00 | 77
2018-08-11 21:00 | 75
2018-08-11 22:00 | 75
2018-08-11 23:00 | 76
2018-08-12 | 75
2018-08-12 01:00 | 75
2018-08-12 02:00 | 74
2018-08-12 03:00 | 73
2018-08-12 04:00 | 73
2018-08-12 05:00 | 74
2018-08-12 06:00 | 73
2018-08-12 07:00 | 73
2018-08-12 08:00 | 74
2018-08-12 09:00 | 73
2018-08-12 10:00 | 75
2018-08-12 11:00 | 78
2018-08-12 12:00 | 79
2018-08-12 13:00 | 81
2018-08-12 14:00 | 81
2018-08-12 15:00 | 81
2018-08-12 16:00 | 82
2018-08-12 17:00 | 83
2018-08-12 18:00 | 81
2018-08-12 19:00 | 79
2018-08-12 20:00 | 78
2018-08-12 21:00 | 77
2018-08-12 22:00 | 77
2018-08-12 23:00 | 76
2018-08-13 | 77
2018-08-13 01:00 | 75
2018-08-13 02:00 | 75
2018-08-13 03:00 | 75
2018-08-13 04:00 | 75
2018-08-13 05:00 | 74
2018-08-13 06:00 | 73
2018-08-13 07:00 | 73
2018-08-13 08:00 | 75
2018-08-13 09:00 | 73
2018-08-13 10:00 | 73
2018-08-13 11:00 | 72
2018-08-13 12:00 | 72
2018-08-13 13:00 | 73
2018-08-13 14:00 | 74
2018-08-13 15:00 | 75
2018-08-13 16:00 | 73
2018-08-13 17:00 | 74
2018-08-13 18:00 | 75
2018-08-13 19:00 | 73
2018-08-13 20:00 | 74
2018-08-13 21:00 | 73
2018-08-13 22:00 | 75
2018-08-13 23:00 | 75
2018-08-14 | 73
2018-08-14 01:00 | 74
2018-08-14 02:00 | 74
2018-08-14 03:00 | 73
2018-08-14 04:00 | 73
2018-08-14 05:00 | 73
2018-08-14 06:00 | 73
2018-08-14 07:00 | 73
2018-08-14 08:00 | 75
2018-08-14 09:00 | 77
2018-08-14 10:00 | 79
2018-08-14 11:00 | 80
2018-08-14 12:00 | 82
2018-08-14 13:00 | 82
2018-08-14 14:00 | 87
2018-08-14 15:00 | 84
2018-08-14 16:00 | 73
2018-08-14 17:00 | 75
2018-08-14 18:00 | 75
2018-08-14 19:00 | 75
2018-08-14 20:00 | 75
2018-08-14 21:00 | 75
2018-08-14 22:00 | 73
2018-08-14 23:00 | 75
2018-08-15 | 73
2018-08-15 01:00 | 74
2018-08-15 02:00 | 74
2018-08-15 03:00 | 73
2018-08-15 04:00 | 73
2018-08-15 05:00 | 73
2018-08-15 06:00 | 73
2018-08-15 07:00 | 73
2018-08-15 08:00 | 75
2018-08-15 09:00 | 77
2018-08-15 10:00 | 79
2018-08-15 11:00 | 82
2018-08-15 12:00 | 84
2018-08-15 13:00 | 86
2018-08-15 14:00 | 88
2018-08-15 15:00 | 88
2018-08-15 16:00 | 90
2018-08-15 17:00 | 89
2018-08-15 18:00 | 90
2018-08-15 19:00 | 90
2018-08-15 20:00 | 88
2018-08-15 21:00 | 88
2018-08-15 22:00 | 86
2018-08-15 23:00 | 85
2018-08-16 | 84
2018-08-16 01:00 | 83
2018-08-16 02:00 | 83
2018-08-16 03:00 | 82
2018-08-16 04:00 | 81
2018-08-16 05:00 | 80
2018-08-16 06:00 | 79
2018-08-16 07:00 | 79
2018-08-16 08:00 | 80
2018-08-16 09:00 | 81
2018-08-16 10:00 | 82
2018-08-16 11:00 | 84
2018-08-16 12:00 | 88
2018-08-16 13:00 | 90
2018-08-16 14:00 | 91
2018-08-16 15:00 | 91
2018-08-16 16:00 | 91
2018-08-16 17:00 | 92
2018-08-16 18:00 | 91
2018-08-16 19:00 | 90
2018-08-16 20:00 | 89
2018-08-16 21:00 | 90
2018-08-16 22:00 | 88
2018-08-16 23:00 | 86
2018-08-17 | 84
2018-08-17 01:00 | 85
2018-08-17 02:00 | 84
2018-08-17 03:00 | 82
2018-08-17 04:00 | 82
2018-08-17 05:00 | 82
2018-08-17 06:00 | 82
2018-08-17 07:00 | 82
2018-08-17 08:00 | 83
2018-08-17 09:00 | 84
2018-08-17 10:00 | 84
2018-08-17 11:00 | 88
2018-08-17 12:00 | 88
2018-08-17 13:00 | 90
2018-08-17 14:00 | 88
2018-08-17 15:00 | 88
2018-08-17 16:00 | 88
2018-08-17 17:00 | 87
2018-08-17 18:00 | 84
2018-08-17 19:00 | 84
2018-08-17 20:00 | 84
2018-08-17 21:00 | 84
2018-08-17 22:00 | 84
2018-08-17 23:00 | 77
2018-08-18 | 76
2018-08-18 01:00 | 75
2018-08-18 02:00 | 76
2018-08-18 03:00 | 78
2018-08-18 04:00 | 78
2018-08-18 05:00 | 78
2018-08-18 06:00 | 78
2018-08-18 07:00 | 76
2018-08-18 08:00 | 77
2018-08-18 09:00 | 78
2018-08-18 10:00 | 80
2018-08-18 11:00 | 83
2018-08-18 12:00 | 84
2018-08-18 13:00 | 86
2018-08-18 14:00 | 87
2018-08-18 15:00 | 86
2018-08-18 16:00 | 89
2018-08-18 17:00 | 89
2018-08-18 18:00 | 82
2018-08-18 19:00 | 79
2018-08-18 20:00 | 76
2018-08-18 21:00 | 76
2018-08-18 22:00 | 75
2018-08-18 23:00 | 74
2018-08-19 | 73
2018-08-19 01:00 | 73
2018-08-19 02:00 | 72
2018-08-19 03:00 | 73
2018-08-19 04:00 | 73
2018-08-19 05:00 | 72
2018-08-19 06:00 | 71
2018-08-19 07:00 | 71
2018-08-19 08:00 | 71
2018-08-19 09:00 | 70
2018-08-19 10:00 | 72
2018-08-19 11:00 | 72
2018-08-19 12:00 | 72
2018-08-19 13:00 | 71
2018-08-19 14:00 | 72
2018-08-19 15:00 | 73
2018-08-19 16:00 | 72
2018-08-19 17:00 | 74
2018-08-19 18:00 | 73
2018-08-19 19:00 | 73
2018-08-19 20:00 | 73
2018-08-19 21:00 | 73
2018-08-19 22:00 | 73
2018-08-19 23:00 | 72
2018-08-20 | 72
2018-08-20 01:00 | 71
2018-08-20 02:00 | 70
2018-08-20 03:00 | 70
2018-08-20 04:00 | 69
2018-08-20 05:00 | 69
2018-08-20 06:00 | 69
2018-08-20 07:00 | 69
2018-08-20 08:00 | 70
2018-08-20 09:00 | 71
2018-08-20 10:00 | 70
2018-08-20 11:00 | 72
2018-08-20 12:00 | 72
2018-08-20 13:00 | 72
2018-08-20 14:00 | 72
2018-08-20 15:00 | 74
2018-08-20 16:00 | 75
2018-08-20 17:00 | 76
2018-08-20 18:00 | 76
2018-08-20 19:00 | 74
2018-08-20 20:00 | 73
2018-08-20 21:00 | 73
2018-08-20 22:00 | 73
2018-08-20 23:00 | 72
2018-08-21 | 72
2018-08-21 01:00 | 71
2018-08-21 02:00 | 70.5
2018-08-21 03:00 | 70
2018-08-21 04:00 | 69
2018-08-21 05:00 | 69
2018-08-21 06:00 | 68
2018-08-21 07:00 | 69
2018-08-21 08:00 | 70
2018-08-21 09:00 | 72
2018-08-21 10:00 | 74
2018-08-21 11:00 | 75
2018-08-21 12:00 | 76
2018-08-21 13:00 | 76
2018-08-21 14:00 | 79
2018-08-21 15:00 | 78
2018-08-21 16:00 | 81
2018-08-21 17:00 | 77
2018-08-21 18:00 | 75
2018-08-21 19:00 | 75
2018-08-21 20:00 | 75
2018-08-21 21:00 | 73
2018-08-21 22:00 | 79
2018-08-21 23:00 | 75
2018-08-22 | 73
2018-08-22 01:00 | 74
2018-08-22 02:00 | 73
2018-08-22 03:00 | 73
2018-08-22 04:00 | 75
2018-08-22 05:00 | 75
2018-08-22 06:00 | 75
2018-08-22 07:00 | 75
2018-08-22 08:00 | 75
2018-08-22 09:00 | 75
2018-08-22 10:00 | 79
2018-08-22 11:00 | 81
2018-08-22 12:00 | 81
2018-08-22 13:00 | 82
2018-08-22 14:00 | 85
2018-08-22 15:00 | 84
2018-08-22 16:00 | 86
2018-08-22 17:00 | 86
2018-08-22 18:00 | 84
2018-08-22 19:00 | 84
2018-08-22 20:00 | 82
2018-08-22 21:00 | 77
2018-08-22 22:00 | 75
2018-08-22 23:00 | 75
2018-08-23 | 73
2018-08-23 01:00 | 73
2018-08-23 02:00 | 73
2018-08-23 03:00 | 72
2018-08-23 04:00 | 72
2018-08-23 05:00 | 71
2018-08-23 06:00 | 70
2018-08-23 07:00 | 70
2018-08-23 08:00 | 68
2018-08-23 09:00 | 70
2018-08-23 10:00 | 72
2018-08-23 11:00 | 73
2018-08-23 12:00 | 73
2018-08-23 13:00 | 75
2018-08-23 14:00 | 77
2018-08-23 15:00 | 79
2018-08-23 16:00 | 79
2018-08-23 17:00 | 80
2018-08-23 18:00 | 79
2018-08-23 19:00 | 79
2018-08-23 20:00 | 78
2018-08-23 21:00 | 77
2018-08-23 22:00 | 75
2018-08-23 23:00 | 75
2018-08-24 | 75
2018-08-24 01:00 | 73
2018-08-24 02:00 | 73
2018-08-24 03:00 | 72
2018-08-24 04:00 | 72
2018-08-24 05:00 | 71
2018-08-24 06:00 | 70
2018-08-24 07:00 | 72
2018-08-24 08:00 | 72
2018-08-24 09:00 | 73
2018-08-24 10:00 | 75
2018-08-24 11:00 | 78
2018-08-24 12:00 | 81
2018-08-24 13:00 | 82
2018-08-24 14:00 | 83
2018-08-24 15:00 | 84
2018-08-24 16:00 | 82
2018-08-24 17:00 | 83
2018-08-24 18:00 | 81
2018-08-24 19:00 | 79
2018-08-24 20:00 | 77
2018-08-24 21:00 | 75
2018-08-24 22:00 | 75
2018-08-24 23:00 | 75
2018-08-25 | 75
2018-08-25 01:00 | 74
2018-08-25 02:00 | 74
2018-08-25 03:00 | 73
2018-08-25 04:00 | 73
2018-08-25 05:00 | 72
2018-08-25 06:00 | 72
2018-08-25 07:00 | 72
2018-08-25 08:00 | 74
2018-08-25 09:00 | 73
2018-08-25 10:00 | 75
2018-08-25 11:00 | 79
2018-08-25 12:00 | 81
2018-08-25 13:00 | 79
2018-08-25 14:00 | 81
2018-08-25 15:00 | 81
2018-08-25 16:00 | 79
2018-08-25 17:00 | 79
2018-08-25 18:00 | 79
2018-08-25 19:00 | 77
2018-08-25 20:00 | 75
2018-08-25 21:00 | 75
2018-08-25 22:00 | 73
2018-08-25 23:00 | 73
2018-08-26 | 73
2018-08-26 01:00 | 73
2018-08-26 02:00 | 73
2018-08-26 03:00 | 73
2018-08-26 04:00 | 73
2018-08-26 05:00 | 73
2018-08-26 06:00 | 72
2018-08-26 07:00 | 72
2018-08-26 08:00 | 73
2018-08-26 09:00 | 75
2018-08-26 10:00 | 77
2018-08-26 11:00 | 80
2018-08-26 12:00 | 81
2018-08-26 13:00 | 82
2018-08-26 14:00 | 84
2018-08-26 15:00 | 84
2018-08-26 16:00 | 82
2018-08-26 17:00 | 82
2018-08-26 18:00 | 82
2018-08-26 19:00 | 82
2018-08-26 20:00 | 84
2018-08-26 21:00 | 82
2018-08-26 22:00 | 82
2018-08-26 23:00 | 82
2018-08-27 | 82
2018-08-27 01:00 | 81
2018-08-27 02:00 | 80
2018-08-27 03:00 | 79
2018-08-27 04:00 | 79
2018-08-27 05:00 | 78
2018-08-27 06:00 | 77
2018-08-27 07:00 | 77
2018-08-27 08:00 | 78
2018-08-27 09:00 | 79
2018-08-27 10:00 | 81
2018-08-27 11:00 | 83
2018-08-27 12:00 | 84
2018-08-27 13:00 | 88
2018-08-27 14:00 | 89
2018-08-27 15:00 | 90
2018-08-27 16:00 | 90
2018-08-27 17:00 | 91
2018-08-27 18:00 | 88
2018-08-27 19:00 | 86
2018-08-27 20:00 | 86
2018-08-27 21:00 | 86
2018-08-27 22:00 | 86
2018-08-27 23:00 | 87
2018-08-28 | 86
2018-08-28 01:00 | 85
2018-08-28 02:00 | 85
2018-08-28 03:00 | 84
2018-08-28 04:00 | 82
2018-08-28 05:00 | 82
2018-08-28 06:00 | 82
2018-08-28 07:00 | 81
2018-08-28 08:00 | 83
2018-08-28 09:00 | 84
2018-08-28 10:00 | 88
2018-08-28 11:00 | 89
2018-08-28 12:00 | 93
2018-08-28 13:00 | 95
2018-08-28 14:00 | 96
2018-08-28 15:00 | 97
2018-08-28 16:00 | 97
2018-08-28 17:00 | 97
2018-08-28 18:00 | 97
2018-08-28 19:00 | 95
2018-08-28 20:00 | 93
2018-08-28 21:00 | 91
2018-08-28 22:00 | 91
2018-08-28 23:00 | 90
2018-08-29 | 90
2018-08-29 01:00 | 88
2018-08-29 02:00 | 87
2018-08-29 03:00 | 88
2018-08-29 04:00 | 88
2018-08-29 05:00 | 86
2018-08-29 06:00 | 84
2018-08-29 07:00 | 84
2018-08-29 08:00 | 86
2018-08-29 09:00 | 88
2018-08-29 10:00 | 90
2018-08-29 11:00 | 93
2018-08-29 12:00 | 93
2018-08-29 13:00 | 97
2018-08-29 14:00 | 96
2018-08-29 15:00 | 97
2018-08-29 16:00 | 97
2018-08-29 17:00 | 97
2018-08-29 18:00 | 97
2018-08-29 19:00 | 95
2018-08-29 20:00 | 93
2018-08-29 21:00 | 91
2018-08-29 22:00 | 91
2018-08-29 23:00 | 90
2018-08-30 | 90
2018-08-30 01:00 | 88
2018-08-30 02:00 | 87
2018-08-30 03:00 | 86
2018-08-30 04:00 | 86
2018-08-30 05:00 | 85
2018-08-30 06:00 | 82
2018-08-30 07:00 | 82
2018-08-30 08:00 | 81
2018-08-30 09:00 | 82
2018-08-30 10:00 | 84
2018-08-30 11:00 | 86
2018-08-30 12:00 | 88
2018-08-30 13:00 | 90
2018-08-30 14:00 | 90
2018-08-30 15:00 | 90
2018-08-30 16:00 | 90
2018-08-30 17:00 | 89
2018-08-30 18:00 | 90
2018-08-30 19:00 | 90
2018-08-30 20:00 | 87
2018-08-30 21:00 | 84
2018-08-30 22:00 | 82
2018-08-30 23:00 | 82
2018-08-31 | 81
2018-08-31 01:00 | 79
2018-08-31 02:00 | 78
2018-08-31 03:00 | 77
2018-08-31 04:00 | 75
2018-08-31 05:00 | 77
2018-08-31 06:00 | 75
2018-08-31 07:00 | 75
2018-08-31 08:00 | 75
2018-08-31 09:00 | 75
2018-08-31 10:00 | 75
2018-08-31 11:00 | 76
2018-08-31 12:00 | 77
2018-08-31 13:00 | 75
2018-08-31 14:00 | 76
2018-08-31 15:00 | 75
2018-08-31 16:00 | 75
2018-08-31 17:00 | 75
2018-08-31 18:00 | 75
2018-08-31 19:00 | 73
2018-08-31 20:00 | 74
2018-08-31 21:00 | 75
2018-08-31 22:00 | 73
2018-08-31 23:00 | 73
2018-09-01 | 73
2018-09-01 01:00 | 72
2018-09-01 02:00 | 72
2018-09-01 03:00 | 72
2018-09-01 04:00 | 72
2018-09-01 05:00 | 71
2018-09-01 06:00 | 72
2018-09-01 07:00 | 70
2018-09-01 08:00 | 70
2018-09-01 09:00 | 72
2018-09-01 10:00 | 73
2018-09-01 11:00 | 74
2018-09-01 12:00 | 73
2018-09-01 13:00 | 75
2018-09-01 14:00 | 77
2018-09-01 15:00 | 79
2018-09-01 16:00 | 79
2018-09-01 17:00 | 77
2018-09-01 18:00 | 75
2018-09-01 19:00 | 75
2018-09-01 20:00 | 74
2018-09-01 21:00 | 73
2018-09-01 22:00 | 73
2018-09-01 23:00 | 72
2018-09-02 | 72
2018-09-02 01:00 | 72
2018-09-02 02:00 | 72
2018-09-02 03:00 | 72
2018-09-02 04:00 | 72
2018-09-02 05:00 | 71
2018-09-02 06:00 | 72
2018-09-02 07:00 | 72
2018-09-02 08:00 | 73
2018-09-02 09:00 | 75
2018-09-02 10:00 | 77
2018-09-02 11:00 | 80
2018-09-02 12:00 | 81
2018-09-02 13:00 | 82
2018-09-02 14:00 | 80
2018-09-02 15:00 | 81
2018-09-02 16:00 | 81
2018-09-02 17:00 | 81
2018-09-02 18:00 | 81
2018-09-02 19:00 | 79
2018-09-02 20:00 | 77
2018-09-02 21:00 | 79
2018-09-02 22:00 | 79
2018-09-02 23:00 | 78
2018-09-03 | 79
2018-09-03 01:00 | 78
2018-09-03 02:00 | 77
2018-09-03 03:00 | 79
2018-09-03 04:00 | 79
2018-09-03 05:00 | 78
2018-09-03 06:00 | 79
2018-09-03 07:00 | 79
2018-09-03 08:00 | 79
2018-09-03 09:00 | 81
2018-09-03 10:00 | 82
2018-09-03 11:00 | 86
2018-09-03 12:00 | 88
2018-09-03 13:00 | 90
2018-09-03 14:00 | 92
2018-09-03 15:00 | 91
2018-09-03 16:00 | 90
2018-09-03 17:00 | 88
2018-09-03 18:00 | 86
2018-09-03 19:00 | 84
2018-09-03 20:00 | 85
2018-09-03 21:00 | 84
2018-09-03 22:00 | 84
2018-09-03 23:00 | 86
2018-09-04 | 84
2018-09-04 01:00 | 84
2018-09-04 02:00 | 83
2018-09-04 03:00 | 82
2018-09-04 04:00 | 82
2018-09-04 05:00 | 81
2018-09-04 06:00 | 81
2018-09-04 07:00 | 81
2018-09-04 08:00 | 82
2018-09-04 09:00 | 84
2018-09-04 10:00 | 88
2018-09-04 11:00 | 89
2018-09-04 12:00 | 90
2018-09-04 13:00 | 91
2018-09-04 14:00 | 90
2018-09-04 15:00 | 91
2018-09-04 16:00 | 91
2018-09-04 17:00 | 92
2018-09-04 18:00 | 91
2018-09-04 19:00 | 90
2018-09-04 20:00 | 90
2018-09-04 21:00 | 88
2018-09-04 22:00 | 84
2018-09-04 23:00 | 84
2018-09-05 | 84
2018-09-05 01:00 | 82
2018-09-05 02:00 | 82
2018-09-05 03:00 | 81
2018-09-05 04:00 | 81
2018-09-05 05:00 | 80
2018-09-05 06:00 | 81
2018-09-05 07:00 | 79
2018-09-05 08:00 | 80
2018-09-05 09:00 | 82
2018-09-05 10:00 | 84
2018-09-05 11:00 | 87
2018-09-05 12:00 | 88
2018-09-05 13:00 | 90
2018-09-05 14:00 | 90
2018-09-05 15:00 | 90
2018-09-05 16:00 | 90
2018-09-05 17:00 | 87
2018-09-05 18:00 | 86
2018-09-05 19:00 | 82
2018-09-05 20:00 | 81
2018-09-05 21:00 | 81
2018-09-05 22:00 | 81
2018-09-05 23:00 | 80
2018-09-06 | 81
2018-09-06 01:00 | 80
2018-09-06 02:00 | 80
2018-09-06 03:00 | 81
2018-09-06 04:00 | 79
2018-09-06 05:00 | 79
2018-09-06 06:00 | 81
2018-09-06 07:00 | 81
2018-09-06 08:00 | 82
2018-09-06 09:00 | 82
2018-09-06 10:00 | 84
2018-09-06 11:00 | 89
2018-09-06 12:00 | 91
2018-09-06 13:00 | 93
2018-09-06 14:00 | 96
2018-09-06 15:00 | 91
2018-09-06 16:00 | 93
2018-09-06 17:00 | 91
2018-09-06 18:00 | 91
2018-09-06 19:00 | 77
2018-09-06 20:00 | 77
2018-09-06 21:00 | 79
2018-09-06 22:00 | 77
2018-09-06 23:00 | 77
2018-09-07 | 77
2018-09-07 01:00 | 77
2018-09-07 02:00 | 77
2018-09-07 03:00 | 75
2018-09-07 04:00 | 75
2018-09-07 05:00 | 76
2018-09-07 06:00 | 75
2018-09-07 07:00 | 75
2018-09-07 08:00 | 77
2018-09-07 09:00 | 77
2018-09-07 10:00 | 75
2018-09-07 11:00 | 76
2018-09-07 12:00 | 75
2018-09-07 13:00 | 75
2018-09-07 14:00 | 75
2018-09-07 15:00 | 75
2018-09-07 16:00 | 73
2018-09-07 17:00 | 74
2018-09-07 18:00 | 73
2018-09-07 19:00 | 73
2018-09-07 20:00 | 72
2018-09-07 21:00 | 72
2018-09-07 22:00 | 72
2018-09-07 23:00 | 72
2018-09-08 | 72
2018-09-08 01:00 | 72
2018-09-08 02:00 | 72
2018-09-08 03:00 | 72
2018-09-08 04:00 | 72
2018-09-08 05:00 | 71
2018-09-08 06:00 | 72
2018-09-08 07:00 | 70
2018-09-08 08:00 | 69
2018-09-08 09:00 | 70
2018-09-08 10:00 | 70
2018-09-08 11:00 | 72
2018-09-08 12:00 | 72
2018-09-08 13:00 | 72
2018-09-08 14:00 | 71
2018-09-08 15:00 | 72
2018-09-08 16:00 | 68
2018-09-08 17:00 | 68
2018-09-08 18:00 | 66
2018-09-08 19:00 | 64
2018-09-08 20:00 | 65
2018-09-08 21:00 | 64
2018-09-08 22:00 | 64
2018-09-08 23:00 | 64
2018-09-09 | 63
2018-09-09 01:00 | 64
2018-09-09 02:00 | 64
2018-09-09 03:00 | 63
2018-09-09 04:00 | 63
2018-09-09 05:00 | 60
2018-09-09 06:00 | 59
2018-09-09 07:00 | 61
2018-09-09 08:00 | 60
2018-09-09 09:00 | 61
2018-09-09 10:00 | 61
2018-09-09 11:00 | 62
2018-09-09 12:00 | 63
2018-09-09 13:00 | 63
2018-09-09 14:00 | 63
2018-09-09 15:00 | 64
2018-09-09 16:00 | 65
2018-09-09 17:00 | 64
2018-09-09 18:00 | 65
2018-09-09 19:00 | 62
2018-09-09 20:00 | 62
2018-09-09 21:00 | 62
2018-09-09 22:00 | 62
2018-09-09 23:00 | 60
2018-09-10 | 59
2018-09-10 01:00 | 59
2018-09-10 02:00 | 59
2018-09-10 03:00 | 59
2018-09-10 04:00 | 59
2018-09-10 05:00 | 59
2018-09-10 06:00 | 60
2018-09-10 07:00 | 62
2018-09-10 08:00 | 62
2018-09-10 09:00 | 63
2018-09-10 10:00 | 63
2018-09-10 11:00 | 64
2018-09-10 12:00 | 64
2018-09-10 13:00 | 63
2018-09-10 14:00 | 63
2018-09-10 15:00 | 63
2018-09-10 16:00 | 64
2018-09-10 17:00 | 63
2018-09-10 18:00 | 63
2018-09-10 19:00 | 64
2018-09-10 20:00 | 64
2018-09-10 21:00 | 66
2018-09-10 22:00 | 66
2018-09-10 23:00 | 65
2018-09-11 | 66
2018-09-11 01:00 | 65
2018-09-11 02:00 | 64
2018-09-11 03:00 | 64
2018-09-11 04:00 | 64
2018-09-11 05:00 | 64
2018-09-11 06:00 | 64
2018-09-11 07:00 | 64
2018-09-11 08:00 | 65
2018-09-11 09:00 | 64
2018-09-11 10:00 | 66
2018-09-11 11:00 | 68
2018-09-11 12:00 | 70
2018-09-11 13:00 | 72
2018-09-11 14:00 | 72
2018-09-11 15:00 | 72
2018-09-11 16:00 | 73
2018-09-11 17:00 | 75
2018-09-11 18:00 | 73
2018-09-11 19:00 | 73
2018-09-11 20:00 | 74
2018-09-11 21:00 | 73
2018-09-11 22:00 | 73
2018-09-11 23:00 | 73
2018-09-12 | 73
2018-09-12 01:00 | 73
2018-09-12 02:00 | 73
2018-09-12 03:00 | 73
2018-09-12 04:00 | 72
2018-09-12 05:00 | 72
2018-09-12 06:00 | 72
2018-09-12 07:00 | 72
2018-09-12 08:00 | 73
2018-09-12 09:00 | 73
2018-09-12 10:00 | 73
2018-09-12 11:00 | 74
2018-09-12 12:00 | 73
2018-09-12 13:00 | 75
2018-09-12 14:00 | 75
2018-09-12 15:00 | 77
2018-09-12 16:00 | 77
2018-09-12 17:00 | 76
2018-09-12 18:00 | 75
2018-09-12 19:00 | 73
2018-09-12 20:00 | 74
2018-09-12 21:00 | 75
2018-09-12 22:00 | 73
2018-09-12 23:00 | 73
2018-09-13 | 72
2018-09-13 01:00 | 72
2018-09-13 02:00 | 72
2018-09-13 03:00 | 72
2018-09-13 04:00 | 72
2018-09-13 05:00 | 71
2018-09-13 06:00 | 72
2018-09-13 07:00 | 72
2018-09-13 08:00 | 72
2018-09-13 09:00 | 72
2018-09-13 10:00 | 72
2018-09-13 11:00 | 72
2018-09-13 12:00 | 73
2018-09-13 13:00 | 75
2018-09-13 14:00 | 76
2018-09-13 15:00 | 75
2018-09-13 16:00 | 75
2018-09-13 17:00 | 76
2018-09-13 18:00 | 75
2018-09-13 19:00 | 75
2018-09-13 20:00 | 74
2018-09-13 21:00 | 73
2018-09-13 22:00 | 73
2018-09-13 23:00 | 72
2018-09-14 | 72
2018-09-14 01:00 | 72
2018-09-14 02:00 | 71
2018-09-14 03:00 | 72
2018-09-14 04:00 | 72
2018-09-14 05:00 | 71
2018-09-14 06:00 | 72
2018-09-14 07:00 | 72
2018-09-14 08:00 | 72
2018-09-14 09:00 | 72
2018-09-14 10:00 | 73
2018-09-14 11:00 | 73
2018-09-14 12:00 | 73
2018-09-14 13:00 | 75
2018-09-14 14:00 | 75
2018-09-14 15:00 | 73
2018-09-14 16:00 | 73
2018-09-14 17:00 | 74
2018-09-14 18:00 | 75
2018-09-14 19:00 | 75
2018-09-14 20:00 | 74
2018-09-14 21:00 | 73
2018-09-14 22:00 | 73
2018-09-14 23:00 | 73
2018-09-15 | 73
2018-09-15 01:00 | 72
2018-09-15 02:00 | 71
2018-09-15 03:00 | 70
2018-09-15 04:00 | 70
2018-09-15 05:00 | 69
2018-09-15 06:00 | 70
2018-09-15 07:00 | 70
2018-09-15 08:00 | 71
2018-09-15 09:00 | 72
2018-09-15 10:00 | 73
2018-09-15 11:00 | 76
2018-09-15 12:00 | 77
2018-09-15 13:00 | 79
2018-09-15 14:00 | 81
2018-09-15 15:00 | 81
2018-09-15 16:00 | 81
2018-09-15 17:00 | 80
2018-09-15 18:00 | 79
2018-09-15 19:00 | 75
2018-09-15 20:00 | 73
2018-09-15 21:00 | 73
2018-09-15 22:00 | 72
2018-09-15 23:00 | 72
2018-09-16 | 72
2018-09-16 01:00 | 71
2018-09-16 02:00 | 71
2018-09-16 03:00 | 72
2018-09-16 04:00 | 72
2018-09-16 05:00 | 71
2018-09-16 06:00 | 70
2018-09-16 07:00 | 70
2018-09-16 08:00 | 72
2018-09-16 09:00 | 75
2018-09-16 10:00 | 77
2018-09-16 11:00 | 80
2018-09-16 12:00 | 81
2018-09-16 13:00 | 82
2018-09-16 14:00 | 85
2018-09-16 15:00 | 84
2018-09-16 16:00 | 82
2018-09-16 17:00 | 83
2018-09-16 18:00 | 81
2018-09-16 19:00 | 77
2018-09-16 20:00 | 76
2018-09-16 21:00 | 75
2018-09-16 22:00 | 75
2018-09-16 23:00 | 74
2018-09-17 | 73
2018-09-17 01:00 | 74
2018-09-17 02:00 | 73
2018-09-17 03:00 | 72
2018-09-17 04:00 | 72
2018-09-17 05:00 | 72
2018-09-17 06:00 | 72
2018-09-17 07:00 | 72
2018-09-17 08:00 | 72
2018-09-17 09:00 | 73
2018-09-17 10:00 | 75
2018-09-17 11:00 | 76
2018-09-17 12:00 | 79
2018-09-17 13:00 | 75
2018-09-17 14:00 | 79
2018-09-17 15:00 | 79
2018-09-17 16:00 | 79
2018-09-17 17:00 | 77
2018-09-17 18:00 | 79
2018-09-17 19:00 | 77
2018-09-17 20:00 | 77
2018-09-17 21:00 | 77
2018-09-17 22:00 | 77
2018-09-17 23:00 | 77
2018-09-18 | 77
2018-09-18 01:00 | 76
2018-09-18 02:00 | 76
2018-09-18 03:00 | 77
2018-09-18 04:00 | 77
2018-09-18 05:00 | 77
2018-09-18 06:00 | 77
2018-09-18 07:00 | 77
2018-09-18 08:00 | 78
2018-09-18 09:00 | 79
2018-09-18 10:00 | 79
2018-09-18 11:00 | 83
2018-09-18 12:00 | 82
2018-09-18 13:00 | 79
2018-09-18 14:00 | 76
2018-09-18 15:00 | 73
2018-09-18 16:00 | 73
2018-09-18 17:00 | 72
2018-09-18 18:00 | 73
2018-09-18 19:00 | 74
2018-09-18 20:00 | 73
2018-09-18 21:00 | 73
2018-09-18 22:00 | 74
2018-09-18 23:00 | 74
2018-09-19 | 73
2018-09-19 01:00 | 74
2018-09-19 02:00 | 74
2018-09-19 03:00 | 74
2018-09-19 04:00 | 73
2018-09-19 05:00 | 73
2018-09-19 06:00 | 72
2018-09-19 07:00 | 72
2018-09-19 08:00 | 73
2018-09-19 09:00 | 74
2018-09-19 10:00 | 76
2018-09-19 11:00 | 78
2018-09-19 12:00 | 80
2018-09-19 13:00 | 80
2018-09-19 14:00 | 80
2018-09-19 15:00 | 82
2018-09-19 16:00 | 80
2018-09-19 17:00 | 79
2018-09-19 18:00 | 78
2018-09-19 19:00 | 76
2018-09-19 20:00 | 74
2018-09-19 21:00 | 73
2018-09-19 22:00 | 73
2018-09-19 23:00 | 72
2018-09-20 | 71
2018-09-20 01:00 | 69
2018-09-20 02:00 | 68
2018-09-20 03:00 | 67
2018-09-20 04:00 | 67
2018-09-20 05:00 | 66
2018-09-20 06:00 | 66
2018-09-20 07:00 | 66
2018-09-20 08:00 | 66
2018-09-20 09:00 | 67
2018-09-20 10:00 | 67
2018-09-20 11:00 | 69
2018-09-20 12:00 | 68
2018-09-20 13:00 | 70
2018-09-20 14:00 | 71
2018-09-20 15:00 | 71
2018-09-20 16:00 | 73
2018-09-20 17:00 | 72
2018-09-20 18:00 | 71
2018-09-20 19:00 | 70
2018-09-20 20:00 | 69
2018-09-20 21:00 | 69
2018-09-20 22:00 | 69
2018-09-20 23:00 | 69
2018-09-21 | 69
2018-09-21 01:00 | 69
2018-09-21 02:00 | 69
2018-09-21 03:00 | 69
2018-09-21 04:00 | 69
2018-09-21 05:00 | 69
2018-09-21 06:00 | 69
2018-09-21 07:00 | 69
2018-09-21 08:00 | 70
2018-09-21 09:00 | 70
2018-09-21 10:00 | 71
2018-09-21 11:00 | 72
2018-09-21 12:00 | 73
2018-09-21 13:00 | 72
2018-09-21 14:00 | 72
2018-09-21 15:00 | 73
2018-09-21 16:00 | 73
2018-09-21 17:00 | 74
2018-09-21 18:00 | 74
2018-09-21 19:00 | 74
2018-09-21 20:00 | 73
2018-09-21 21:00 | 74
2018-09-21 22:00 | 74
2018-09-21 23:00 | 73
2018-09-22 | 73
2018-09-22 01:00 | 73
2018-09-22 02:00 | 74
2018-09-22 03:00 | 75
2018-09-22 04:00 | 76
2018-09-22 05:00 | 76
2018-09-22 06:00 | 76
2018-09-22 07:00 | 75
2018-09-22 08:00 | 73
2018-09-22 09:00 | 72
2018-09-22 10:00 | 72
2018-09-22 11:00 | 72
2018-09-22 12:00 | 73
2018-09-22 13:00 | 71
2018-09-22 14:00 | 71
2018-09-22 15:00 | 71
2018-09-22 16:00 | 70
2018-09-22 17:00 | 69
2018-09-22 18:00 | 69
2018-09-22 19:00 | 68
2018-09-22 20:00 | 68
2018-09-22 21:00 | 67
2018-09-22 22:00 | 66
2018-09-22 23:00 | 65
2018-09-23 | 64
2018-09-23 01:00 | 64
2018-09-23 02:00 | 63
2018-09-23 03:00 | 63
2018-09-23 04:00 | 63
2018-09-23 05:00 | 62
2018-09-23 06:00 | 62
2018-09-23 07:00 | 62
2018-09-23 08:00 | 62
2018-09-23 09:00 | 63
2018-09-23 10:00 | 62
2018-09-23 11:00 | 63
2018-09-23 12:00 | 65
2018-09-23 13:00 | 66
2018-09-23 14:00 | 67
2018-09-23 15:00 | 67
2018-09-23 16:00 | 67
2018-09-23 17:00 | 67
2018-09-23 18:00 | 67
2018-09-23 19:00 | 66
2018-09-23 20:00 | 66
2018-09-23 21:00 | 66
2018-09-23 22:00 | 66
2018-09-23 23:00 | 66
2018-09-24 | 66
2018-09-24 01:00 | 65
2018-09-24 02:00 | 64
2018-09-24 03:00 | 64
2018-09-24 04:00 | 63
2018-09-24 05:00 | 61
2018-09-24 06:00 | 60
2018-09-24 07:00 | 60
2018-09-24 08:00 | 60
2018-09-24 09:00 | 62
2018-09-24 10:00 | 63
2018-09-24 11:00 | 63
2018-09-24 12:00 | 67
2018-09-24 13:00 | 69
2018-09-24 14:00 | 71
2018-09-24 15:00 | 69
2018-09-24 16:00 | 69
2018-09-24 17:00 | 68
2018-09-24 18:00 | 66
2018-09-24 19:00 | 64
2018-09-24 20:00 | 63
2018-09-24 21:00 | 62
2018-09-24 22:00 | 62
2018-09-24 23:00 | 62
2018-09-25 | 62
2018-09-25 01:00 | 62
2018-09-25 02:00 | 61
2018-09-25 03:00 | 61
2018-09-25 04:00 | 61
2018-09-25 05:00 | 61
2018-09-25 06:00 | 60
2018-09-25 07:00 | 61
2018-09-25 08:00 | 61
2018-09-25 09:00 | 63
2018-09-25 10:00 | 70
2018-09-25 11:00 | 71
2018-09-25 12:00 | 71
2018-09-25 13:00 | 73
2018-09-25 14:00 | 73
2018-09-25 15:00 | 75
2018-09-25 16:00 | 75
2018-09-25 17:00 | 76
2018-09-25 18:00 | 73
2018-09-25 19:00 | 73
2018-09-25 20:00 | 74
2018-09-25 21:00 | 73
2018-09-25 22:00 | 73
2018-09-25 23:00 | 73
2018-09-26 | 73
2018-09-26 01:00 | 73
2018-09-26 02:00 | 74
2018-09-26 03:00 | 73
2018-09-26 04:00 | 73
2018-09-26 05:00 | 74
2018-09-26 06:00 | 73
2018-09-26 07:00 | 73
2018-09-26 08:00 | 74
2018-09-26 09:00 | 73
2018-09-26 10:00 | 75
2018-09-26 11:00 | 78
2018-09-26 12:00 | 81
2018-09-26 13:00 | 82
2018-09-26 14:00 | 80
2018-09-26 15:00 | 82
2018-09-26 16:00 | 82
2018-09-26 17:00 | 83
2018-09-26 18:00 | 79
2018-09-26 19:00 | 77
2018-09-26 20:00 | 75
2018-09-26 21:00 | 76
2018-09-26 22:00 | 76
2018-09-26 23:00 | 74
2018-09-27 | 74
2018-09-27 01:00 | 72
2018-09-27 02:00 | 70
2018-09-27 03:00 | 69
2018-09-27 04:00 | 66
2018-09-27 05:00 | 65
2018-09-27 06:00 | 65
2018-09-27 07:00 | 63
2018-09-27 08:00 | 63
2018-09-27 09:00 | 63
2018-09-27 10:00 | 65
2018-09-27 11:00 | 68
2018-09-27 12:00 | 70
2018-09-27 13:00 | 72
2018-09-27 14:00 | 72
2018-09-27 15:00 | 73
2018-09-27 16:00 | 73
2018-09-27 17:00 | 72
2018-09-27 18:00 | 71
2018-09-27 19:00 | 70
2018-09-27 20:00 | 70
2018-09-27 21:00 | 69
2018-09-27 22:00 | 68
2018-09-27 23:00 | 68
2018-09-28 | 68
2018-09-28 01:00 | 65
2018-09-28 02:00 | 65
2018-09-28 03:00 | 65
2018-09-28 04:00 | 64
2018-09-28 05:00 | 63
2018-09-28 06:00 | 64
2018-09-28 07:00 | 63
2018-09-28 08:00 | 60
2018-09-28 09:00 | 60
2018-09-28 10:00 | 59
2018-09-28 11:00 | 58
2018-09-28 12:00 | 61
2018-09-28 13:00 | 57
2018-09-28 14:00 | 59
2018-09-28 15:00 | 63
2018-09-28 16:00 | 63
2018-09-28 17:00 | 64
2018-09-28 18:00 | 64
2018-09-28 19:00 | 64
2018-09-28 20:00 | 64
2018-09-28 21:00 | 63
2018-09-28 22:00 | 63
2018-09-28 23:00 | 62
2018-09-29 | 63
2018-09-29 01:00 | 63
2018-09-29 02:00 | 62
2018-09-29 03:00 | 61
2018-09-29 04:00 | 61
2018-09-29 05:00 | 60
2018-09-29 06:00 | 61
2018-09-29 07:00 | 61
2018-09-29 08:00 | 62
2018-09-29 09:00 | 64
2018-09-29 10:00 | 66
2018-09-29 11:00 | 68
2018-09-29 12:00 | 70
2018-09-29 13:00 | 72
2018-09-29 14:00 | 74
2018-09-29 15:00 | 75
2018-09-29 16:00 | 73
2018-09-29 17:00 | 75
2018-09-29 18:00 | 72
2018-09-29 19:00 | 70
2018-09-29 20:00 | 68
2018-09-29 21:00 | 68
2018-09-29 22:00 | 66
2018-09-29 23:00 | 66
2018-09-30 | 64
2018-09-30 01:00 | 64
2018-09-30 02:00 | 63
2018-09-30 03:00 | 63
2018-09-30 04:00 | 61
2018-09-30 05:00 | 60
2018-09-30 06:00 | 57
2018-09-30 07:00 | 57
2018-09-30 08:00 | 59
2018-09-30 09:00 | 61
2018-09-30 10:00 | 64
2018-09-30 11:00 | 65
2018-09-30 12:00 | 66
2018-09-30 13:00 | 70
2018-09-30 14:00 | 70
2018-09-30 15:00 | 72
2018-09-30 16:00 | 72
2018-09-30 17:00 | 70
2018-09-30 18:00 | 68
2018-09-30 19:00 | 66
2018-09-30 20:00 | 67
2018-09-30 21:00 | 66
2018-09-30 22:00 | 66
2018-09-30 23:00 | 68
2018-10-01 | 66
2018-10-01 01:00 | 67
2018-10-01 02:00 | 67
2018-10-01 03:00 | 66
2018-10-01 04:00 | 64
2018-10-01 05:00 | 65
2018-10-01 06:00 | 66
2018-10-01 07:00 | 66
2018-10-01 08:00 | 68
2018-10-01 09:00 | 70
2018-10-01 10:00 | 70
2018-10-01 11:00 | 73
2018-10-01 12:00 | 75
2018-10-01 13:00 | 75
2018-10-01 14:00 | 76
2018-10-01 15:00 | 75
2018-10-01 16:00 | 75
2018-10-01 17:00 | 78
2018-10-01 18:00 | 75
2018-10-01 19:00 | 73
2018-10-01 20:00 | 72
2018-10-01 21:00 | 73
2018-10-01 22:00 | 73
2018-10-01 23:00 | 72.5
2018-10-02 | 72
2018-10-02 01:00 | 71
2018-10-02 02:00 | 71
2018-10-02 03:00 | 68
2018-10-02 04:00 | 66
2018-10-02 05:00 | 67
2018-10-02 06:00 | 66
2018-10-02 07:00 | 66
2018-10-02 08:00 | 68
2018-10-02 09:00 | 72
2018-10-02 10:00 | 75
2018-10-02 11:00 | 76
2018-10-02 12:00 | 77
2018-10-02 13:00 | 77
2018-10-02 14:00 | 78
2018-10-02 15:00 | 79
2018-10-02 16:00 | 77
2018-10-02 17:00 | 77
2018-10-02 18:00 | 77
2018-10-02 19:00 | 75
2018-10-02 20:00 | 76
2018-10-02 21:00 | 75
2018-10-02 22:00 | 75
2018-10-02 23:00 | 68
2018-10-03 | 68
2018-10-03 01:00 | 67
2018-10-03 02:00 | 67
2018-10-03 03:00 | 68
2018-10-03 04:00 | 66
2018-10-03 05:00 | 67
2018-10-03 06:00 | 66
2018-10-03 07:00 | 66
2018-10-03 08:00 | 69
2018-10-03 09:00 | 70
2018-10-03 10:00 | 72
2018-10-03 11:00 | 72
2018-10-03 12:00 | 73
2018-10-03 13:00 | 73
2018-10-03 14:00 | 74
2018-10-03 15:00 | 77
2018-10-03 16:00 | 75
2018-10-03 17:00 | 75
2018-10-03 18:00 | 75
2018-10-03 19:00 | 73
2018-10-03 20:00 | 71
2018-10-03 21:00 | 70
2018-10-03 22:00 | 70
2018-10-03 23:00 | 68
2018-10-04 | 66
2018-10-04 01:00 | 66
2018-10-04 02:00 | 66
2018-10-04 03:00 | 64
2018-10-04 04:00 | 64
2018-10-04 05:00 | 65
2018-10-04 06:00 | 64
2018-10-04 07:00 | 64
2018-10-04 08:00 | 66
2018-10-04 09:00 | 68
2018-10-04 10:00 | 72
2018-10-04 11:00 | 73
2018-10-04 12:00 | 77
2018-10-04 13:00 | 79
2018-10-04 14:00 | 77
2018-10-04 15:00 | 75
2018-10-04 16:00 | 75
2018-10-04 17:00 | 76
2018-10-04 18:00 | 75
2018-10-04 19:00 | 75
2018-10-04 20:00 | 76
2018-10-04 21:00 | 76
2018-10-04 22:00 | 76
2018-10-04 23:00 | 74
2018-10-05 | 74
2018-10-05 01:00 | 73
2018-10-05 02:00 | 71
2018-10-05 03:00 | 68
2018-10-05 04:00 | 66
2018-10-05 05:00 | 64
2018-10-05 06:00 | 63
2018-10-05 07:00 | 61
2018-10-05 08:00 | 63
2018-10-05 09:00 | 63
2018-10-05 10:00 | 64
2018-10-05 11:00 | 65
2018-10-05 12:00 | 66
2018-10-05 13:00 | 67
2018-10-05 14:00 | 68
2018-10-05 15:00 | 69
2018-10-05 16:00 | 70
2018-10-05 17:00 | 69
2018-10-05 18:00 | 69
2018-10-05 19:00 | 68
2018-10-05 20:00 | 66
2018-10-05 21:00 | 66
2018-10-05 22:00 | 66
2018-10-05 23:00 | 65
2018-10-06 | 65
2018-10-06 01:00 | 65
2018-10-06 02:00 | 65
2018-10-06 03:00 | 65
2018-10-06 04:00 | 65
2018-10-06 05:00 | 65
2018-10-06 06:00 | 65
2018-10-06 07:00 | 65
2018-10-06 08:00 | 65
2018-10-06 09:00 | 66
2018-10-06 10:00 | 64
2018-10-06 11:00 | 66
2018-10-06 12:00 | 67
2018-10-06 13:00 | 67
2018-10-06 14:00 | 67
2018-10-06 15:00 | 67
2018-10-06 16:00 | 66
2018-10-06 17:00 | 67
2018-10-06 18:00 | 67
2018-10-06 19:00 | 67
2018-10-06 20:00 | 67
2018-10-06 21:00 | 67
2018-10-06 22:00 | 68
2018-10-06 23:00 | 69
2018-10-07 | 69
2018-10-07 01:00 | 70
2018-10-07 02:00 | 70
2018-10-07 03:00 | 70
2018-10-07 04:00 | 70
2018-10-07 05:00 | 70
2018-10-07 06:00 | 70
2018-10-07 07:00 | 71
2018-10-07 08:00 | 71
2018-10-07 09:00 | 72
2018-10-07 10:00 | 72
2018-10-07 11:00 | 73
2018-10-07 12:00 | 75
2018-10-07 13:00 | 77
2018-10-07 14:00 | 79
2018-10-07 15:00 | 80
2018-10-07 16:00 | 81
2018-10-07 17:00 | 81
2018-10-07 18:00 | 80
2018-10-07 19:00 | 80
2018-10-07 20:00 | 79
2018-10-07 21:00 | 79
2018-10-07 22:00 | 77
2018-10-07 23:00 | 76
2018-10-08 | 73
2018-10-08 01:00 | 72
2018-10-08 02:00 | 73
2018-10-08 03:00 | 72
2018-10-08 04:00 | 72
2018-10-08 05:00 | 70
2018-10-08 06:00 | 68
2018-10-08 07:00 | 68
2018-10-08 08:00 | 67
2018-10-08 09:00 | 66
2018-10-08 10:00 | 66
2018-10-08 11:00 | 67
2018-10-08 12:00 | 66
2018-10-08 13:00 | 66
2018-10-08 14:00 | 67
2018-10-08 15:00 | 66
2018-10-08 16:00 | 66
2018-10-08 17:00 | 66
2018-10-08 18:00 | 64
2018-10-08 19:00 | 66
2018-10-08 20:00 | 65
2018-10-08 21:00 | 66
2018-10-08 22:00 | 66
2018-10-08 23:00 | 66
2018-10-09 | 66
2018-10-09 01:00 | 67
2018-10-09 02:00 | 68
2018-10-09 03:00 | 70
2018-10-09 04:00 | 70
2018-10-09 05:00 | 69
2018-10-09 06:00 | 70
2018-10-09 07:00 | 72
2018-10-09 08:00 | 71
2018-10-09 09:00 | 72
2018-10-09 10:00 | 73
2018-10-09 11:00 | 74
2018-10-09 12:00 | 75
2018-10-09 13:00 | 77
2018-10-09 14:00 | 77
2018-10-09 15:00 | 77
2018-10-09 16:00 | 77
2018-10-09 17:00 | 76
2018-10-09 18:00 | 73
2018-10-09 19:00 | 73
2018-10-09 20:00 | 74
2018-10-09 21:00 | 73
2018-10-09 22:00 | 73
2018-10-09 23:00 | 74
2018-10-10 | 73
2018-10-10 01:00 | 74
2018-10-10 02:00 | 73
2018-10-10 03:00 | 72
2018-10-10 04:00 | 72
2018-10-10 05:00 | 71
2018-10-10 06:00 | 72
2018-10-10 07:00 | 72
2018-10-10 08:00 | 73
2018-10-10 09:00 | 73
2018-10-10 10:00 | 75
2018-10-10 11:00 | 77
2018-10-10 12:00 | 77
2018-10-10 13:00 | 79
2018-10-10 14:00 | 81
2018-10-10 15:00 | 82
2018-10-10 16:00 | 77
2018-10-10 17:00 | 79
2018-10-10 18:00 | 75
2018-10-10 19:00 | 73
2018-10-10 20:00 | 74
2018-10-10 21:00 | 75
2018-10-10 22:00 | 73
2018-10-10 23:00 | 74
2018-10-11 | 73
2018-10-11 01:00 | 74
2018-10-11 02:00 | 73.5
2018-10-11 03:00 | 73
2018-10-11 04:00 | 73
2018-10-11 05:00 | 73
2018-10-11 06:00 | 73
2018-10-11 07:00 | 73
2018-10-11 08:00 | 74
2018-10-11 09:00 | 75
2018-10-11 10:00 | 75
2018-10-11 11:00 | 76
2018-10-11 12:00 | 73
2018-10-11 13:00 | 73
2018-10-11 14:00 | 77
2018-10-11 15:00 | 79
2018-10-11 16:00 | 73
2018-10-11 17:00 | 73
2018-10-11 18:00 | 72
2018-10-11 19:00 | 72
2018-10-11 20:00 | 73
2018-10-11 21:00 | 72
2018-10-11 22:00 | 72
2018-10-11 23:00 | 72
2018-10-12 | 72
2018-10-12 01:00 | 71
2018-10-12 02:00 | 70
2018-10-12 03:00 | 68
2018-10-12 04:00 | 66
2018-10-12 05:00 | 64
2018-10-12 06:00 | 63
2018-10-12 07:00 | 62
2018-10-12 08:00 | 61
2018-10-12 09:00 | 61
2018-10-12 10:00 | 62
2018-10-12 11:00 | 61
2018-10-12 12:00 | 61
2018-10-12 13:00 | 63
2018-10-12 14:00 | 62
2018-10-12 15:00 | 63
2018-10-12 16:00 | 63
2018-10-12 17:00 | 62
2018-10-12 18:00 | 61
2018-10-12 19:00 | 57
2018-10-12 20:00 | 57
2018-10-12 21:00 | 55
2018-10-12 22:00 | 55
2018-10-12 23:00 | 54
2018-10-13 | 54
2018-10-13 01:00 | 54
2018-10-13 02:00 | 54
2018-10-13 03:00 | 54
2018-10-13 04:00 | 54
2018-10-13 05:00 | 53
2018-10-13 06:00 | 54
2018-10-13 07:00 | 54
2018-10-13 08:00 | 50
2018-10-13 09:00 | 50
2018-10-13 10:00 | 48
2018-10-13 11:00 | 50
2018-10-13 12:00 | 52
2018-10-13 13:00 | 54
2018-10-13 14:00 | 56
2018-10-13 15:00 | 57
2018-10-13 16:00 | 57
2018-10-13 17:00 | 58
2018-10-13 18:00 | 57
2018-10-13 19:00 | 57
2018-10-13 20:00 | 56
2018-10-13 21:00 | 55
2018-10-13 22:00 | 54
2018-10-13 23:00 | 54
2018-10-14 | 54
2018-10-14 01:00 | 54
2018-10-14 02:00 | 53
2018-10-14 03:00 | 52
2018-10-14 04:00 | 52
2018-10-14 05:00 | 52
2018-10-14 06:00 | 54
2018-10-14 07:00 | 52
2018-10-14 08:00 | 52
2018-10-14 09:00 | 54
2018-10-14 10:00 | 54
2018-10-14 11:00 | 56
2018-10-14 12:00 | 59
2018-10-14 13:00 | 59
2018-10-14 14:00 | 59
2018-10-14 15:00 | 61
2018-10-14 16:00 | 59
2018-10-14 17:00 | 59
2018-10-14 18:00 | 57
2018-10-14 19:00 | 57
2018-10-14 20:00 | 58
2018-10-14 21:00 | 57
2018-10-14 22:00 | 57
2018-10-14 23:00 | 56
2018-10-15 | 55
2018-10-15 01:00 | 55
2018-10-15 02:00 | 56
2018-10-15 03:00 | 57
2018-10-15 04:00 | 57
2018-10-15 05:00 | 57
2018-10-15 06:00 | 57
2018-10-15 07:00 | 58
2018-10-15 08:00 | 59
2018-10-15 09:00 | 60
2018-10-15 10:00 | 62
2018-10-15 11:00 | 63
2018-10-15 12:00 | 63
2018-10-15 13:00 | 64
2018-10-15 14:00 | 65
2018-10-15 15:00 | 66
2018-10-15 16:00 | 67
2018-10-15 17:00 | 67
2018-10-15 18:00 | 67
2018-10-15 19:00 | 67
2018-10-15 20:00 | 68
2018-10-15 21:00 | 69
2018-10-15 22:00 | 69
2018-10-15 23:00 | 70
2018-10-16 | 66
2018-10-16 01:00 | 63
2018-10-16 02:00 | 62
2018-10-16 03:00 | 60
2018-10-16 04:00 | 58
2018-10-16 05:00 | 54
2018-10-16 06:00 | 52
2018-10-16 07:00 | 50
2018-10-16 08:00 | 49
2018-10-16 09:00 | 49
2018-10-16 10:00 | 50
2018-10-16 11:00 | 51
2018-10-16 12:00 | 54
2018-10-16 13:00 | 54
2018-10-16 14:00 | 56
2018-10-16 15:00 | 55
2018-10-16 16:00 | 57
2018-10-16 17:00 | 57
2018-10-16 18:00 | 55
2018-10-16 19:00 | 55
2018-10-16 20:00 | 54
2018-10-16 21:00 | 54
2018-10-16 22:00 | 54
2018-10-16 23:00 | 54
2018-10-17 | 54
2018-10-17 01:00 | 54
2018-10-17 02:00 | 53
2018-10-17 03:00 | 53
2018-10-17 04:00 | 52
2018-10-17 05:00 | 53
2018-10-17 06:00 | 51
2018-10-17 07:00 | 51
2018-10-17 08:00 | 51
2018-10-17 09:00 | 53
2018-10-17 10:00 | 54
2018-10-17 11:00 | 56
2018-10-17 12:00 | 57
2018-10-17 13:00 | 63
2018-10-17 14:00 | 63
2018-10-17 15:00 | 63
2018-10-17 16:00 | 63
2018-10-17 17:00 | 63
2018-10-17 18:00 | 59
2018-10-17 19:00 | 57
2018-10-17 20:00 | 57
2018-10-17 21:00 | 55
2018-10-17 22:00 | 54
2018-10-17 23:00 | 52
2018-10-18 | 50
2018-10-18 01:00 | 49
2018-10-18 02:00 | 48
2018-10-18 03:00 | 48
2018-10-18 04:00 | 47
2018-10-18 05:00 | 46
2018-10-18 06:00 | 45
2018-10-18 07:00 | 44
2018-10-18 08:00 | 44
2018-10-18 09:00 | 45
2018-10-18 10:00 | 45
2018-10-18 11:00 | 47
2018-10-18 12:00 | 48
2018-10-18 13:00 | 50
2018-10-18 14:00 | 51
2018-10-18 15:00 | 52
2018-10-18 16:00 | 52
2018-10-18 17:00 | 52
2018-10-18 18:00 | 52
2018-10-18 19:00 | 52
2018-10-18 20:00 | 50
2018-10-18 21:00 | 50
2018-10-18 22:00 | 48
2018-10-18 23:00 | 48
2018-10-19 | 52
2018-10-19 01:00 | 48
2018-10-19 02:00 | 47
2018-10-19 03:00 | 46
2018-10-19 04:00 | 46
2018-10-19 05:00 | 47
2018-10-19 06:00 | 46
2018-10-19 07:00 | 46
2018-10-19 08:00 | 47
2018-10-19 09:00 | 50
2018-10-19 10:00 | 52
2018-10-19 11:00 | 53
2018-10-19 12:00 | 57
2018-10-19 13:00 | 59
2018-10-19 14:00 | 60
2018-10-19 15:00 | 63
2018-10-19 16:00 | 63
2018-10-19 17:00 | 61
2018-10-19 18:00 | 59
2018-10-19 19:00 | 59
2018-10-19 20:00 | 58
2018-10-19 21:00 | 57
2018-10-19 22:00 | 57
2018-10-19 23:00 | 59
2018-10-20 | 59
2018-10-20 01:00 | 58
2018-10-20 02:00 | 58
2018-10-20 03:00 | 57
2018-10-20 04:00 | 55
2018-10-20 05:00 | 56
2018-10-20 06:00 | 55
2018-10-20 07:00 | 55
2018-10-20 08:00 | 57
2018-10-20 09:00 | 57
2018-10-20 10:00 | 57
2018-10-20 11:00 | 59
2018-10-20 12:00 | 61
2018-10-20 13:00 | 61
2018-10-20 14:00 | 62
2018-10-20 15:00 | 63
2018-10-20 16:00 | 64
2018-10-20 17:00 | 65
2018-10-20 18:00 | 63
2018-10-20 19:00 | 63
2018-10-20 20:00 | 61
2018-10-20 21:00 | 63
2018-10-20 22:00 | 57
2018-10-20 23:00 | 56
2018-10-21 | 55
2018-10-21 01:00 | 54
2018-10-21 02:00 | 52
2018-10-21 03:00 | 52
2018-10-21 04:00 | 52
2018-10-21 05:00 | 50
2018-10-21 06:00 | 50
2018-10-21 07:00 | 50
2018-10-21 08:00 | 50
2018-10-21 09:00 | 48
2018-10-21 10:00 | 48
2018-10-21 11:00 | 48
2018-10-21 12:00 | 46
2018-10-21 13:00 | 48
2018-10-21 14:00 | 49
2018-10-21 15:00 | 48
2018-10-21 16:00 | 48
2018-10-21 17:00 | 48
2018-10-21 18:00 | 46
2018-10-21 19:00 | 45
2018-10-21 20:00 | 45
2018-10-21 21:00 | 45
2018-10-21 22:00 | 45
2018-10-21 23:00 | 43
2018-10-22 | 43
2018-10-22 01:00 | 43
2018-10-22 02:00 | 44
2018-10-22 03:00 | 43
2018-10-22 04:00 | 43
2018-10-22 05:00 | 43
2018-10-22 06:00 | 45
2018-10-22 07:00 | 45
2018-10-22 08:00 | 46
2018-10-22 09:00 | 46
2018-10-22 10:00 | 48
2018-10-22 11:00 | 50
2018-10-22 12:00 | 50
2018-10-22 13:00 | 52
2018-10-22 14:00 | 52
2018-10-22 15:00 | 52
2018-10-22 16:00 | 52
2018-10-22 17:00 | 52
2018-10-22 18:00 | 52
2018-10-22 19:00 | 52
2018-10-22 20:00 | 51
2018-10-22 21:00 | 52
2018-10-22 22:00 | 50
2018-10-22 23:00 | 49
2018-10-23 | 48
2018-10-23 01:00 | 49
2018-10-23 02:00 | 47
2018-10-23 03:00 | 47
2018-10-23 04:00 | 47
2018-10-23 05:00 | 48
2018-10-23 06:00 | 48
2018-10-23 07:00 | 48
2018-10-23 08:00 | 52
2018-10-23 09:00 | 53
2018-10-23 10:00 | 57
2018-10-23 11:00 | 57
2018-10-23 12:00 | 61
2018-10-23 13:00 | 64
2018-10-23 14:00 | 65
2018-10-23 15:00 | 67
2018-10-23 16:00 | 65
2018-10-23 17:00 | 65
2018-10-23 18:00 | 64
2018-10-23 19:00 | 59
2018-10-23 20:00 | 56
2018-10-23 21:00 | 55
2018-10-23 22:00 | 54
2018-10-23 23:00 | 53
2018-10-24 | 52
2018-10-24 01:00 | 51
2018-10-24 02:00 | 50
2018-10-24 03:00 | 50
2018-10-24 04:00 | 49
2018-10-24 05:00 | 48
2018-10-24 06:00 | 49
2018-10-24 07:00 | 48
2018-10-24 08:00 | 48
2018-10-24 09:00 | 48
2018-10-24 10:00 | 50
2018-10-24 11:00 | 51
2018-10-24 12:00 | 54
2018-10-24 13:00 | 54
2018-10-24 14:00 | 54
2018-10-24 15:00 | 55
2018-10-24 16:00 | 54
2018-10-24 17:00 | 55
2018-10-24 18:00 | 54
2018-10-24 19:00 | 54
2018-10-24 20:00 | 52
2018-10-24 21:00 | 50
2018-10-24 22:00 | 48
2018-10-24 23:00 | 48
2018-10-25 | 46
2018-10-25 01:00 | 47
2018-10-25 02:00 | 46
2018-10-25 03:00 | 46
2018-10-25 04:00 | 45
2018-10-25 05:00 | 45
2018-10-25 06:00 | 45
2018-10-25 07:00 | 45
2018-10-25 08:00 | 44
2018-10-25 09:00 | 45
2018-10-25 10:00 | 46
2018-10-25 11:00 | 47
2018-10-25 12:00 | 48
2018-10-25 13:00 | 50
2018-10-25 14:00 | 51
2018-10-25 15:00 | 52
2018-10-25 16:00 | 52
2018-10-25 17:00 | 51
2018-10-25 18:00 | 50
2018-10-25 19:00 | 48
2018-10-25 20:00 | 46
2018-10-25 21:00 | 46
2018-10-25 22:00 | 45
2018-10-25 23:00 | 44
2018-10-26 | 43
2018-10-26 01:00 | 43
2018-10-26 02:00 | 42
2018-10-26 03:00 | 43
2018-10-26 04:00 | 43
2018-10-26 05:00 | 42
2018-10-26 06:00 | 43
2018-10-26 07:00 | 43
2018-10-26 08:00 | 43
2018-10-26 09:00 | 45
2018-10-26 10:00 | 45
2018-10-26 11:00 | 45
2018-10-26 12:00 | 46
2018-10-26 13:00 | 46
2018-10-26 14:00 | 48
2018-10-26 15:00 | 48
2018-10-26 16:00 | 50
2018-10-26 17:00 | 50
2018-10-26 18:00 | 48
2018-10-26 19:00 | 48
2018-10-26 20:00 | 48
2018-10-26 21:00 | 48
2018-10-26 22:00 | 48
2018-10-26 23:00 | 48
2018-10-27 | 48
2018-10-27 01:00 | 47
2018-10-27 02:00 | 45
2018-10-27 03:00 | 45
2018-10-27 04:00 | 46
2018-10-27 05:00 | 47
2018-10-27 06:00 | 46
2018-10-27 07:00 | 48
2018-10-27 08:00 | 49
2018-10-27 09:00 | 50
2018-10-27 10:00 | 48
2018-10-27 11:00 | 49
2018-10-27 12:00 | 50
2018-10-27 13:00 | 50
2018-10-27 14:00 | 51
2018-10-27 15:00 | 50
2018-10-27 16:00 | 52
2018-10-27 17:00 | 52
2018-10-27 18:00 | 52
2018-10-27 19:00 | 52
2018-10-27 20:00 | 52
2018-10-27 21:00 | 52
2018-10-27 22:00 | 52
2018-10-27 23:00 | 51
2018-10-28 | 50
2018-10-28 01:00 | 48
2018-10-28 02:00 | 48
2018-10-28 03:00 | 46
2018-10-28 04:00 | 46
2018-10-28 05:00 | 48
2018-10-28 06:00 | 48
2018-10-28 07:00 | 48
2018-10-28 08:00 | 48
2018-10-28 09:00 | 48
2018-10-28 10:00 | 48
2018-10-28 11:00 | 50
2018-10-28 12:00 | 52
2018-10-28 13:00 | 52
2018-10-28 14:00 | 53
2018-10-28 15:00 | 54
2018-10-28 16:00 | 54
2018-10-28 17:00 | 53
2018-10-28 18:00 | 54
2018-10-28 19:00 | 54
2018-10-28 20:00 | 53
2018-10-28 21:00 | 54
2018-10-28 22:00 | 52
2018-10-28 23:00 | 51
2018-10-29 | 52
2018-10-29 01:00 | 50
2018-10-29 02:00 | 50
2018-10-29 03:00 | 50
2018-10-29 04:00 | 52
2018-10-29 05:00 | 54
2018-10-29 06:00 | 54
2018-10-29 07:00 | 52
2018-10-29 08:00 | 52
2018-10-29 09:00 | 52
2018-10-29 10:00 | 52
2018-10-29 11:00 | 53
2018-10-29 12:00 | 54
2018-10-29 13:00 | 55
2018-10-29 14:00 | 57
2018-10-29 15:00 | 57
2018-10-29 16:00 | 57
2018-10-29 17:00 | 57
2018-10-29 18:00 | 55
2018-10-29 19:00 | 54
2018-10-29 20:00 | 54
2018-10-29 21:00 | 54
2018-10-29 22:00 | 52
2018-10-29 23:00 | 50
2018-10-30 | 48
2018-10-30 01:00 | 49
2018-10-30 02:00 | 49
2018-10-30 03:00 | 48
2018-10-30 04:00 | 46
2018-10-30 05:00 | 47
2018-10-30 06:00 | 46
2018-10-30 07:00 | 46
2018-10-30 08:00 | 45
2018-10-30 09:00 | 46
2018-10-30 10:00 | 46
2018-10-30 11:00 | 49
2018-10-30 12:00 | 50
2018-10-30 13:00 | 52
2018-10-30 14:00 | 54
2018-10-30 15:00 | 55
2018-10-30 16:00 | 55
2018-10-30 17:00 | 57
2018-10-30 18:00 | 55
2018-10-30 19:00 | 55
2018-10-30 20:00 | 55
2018-10-30 21:00 | 54
2018-10-30 22:00 | 54
2018-10-30 23:00 | 52
2018-10-31 | 52
2018-10-31 01:00 | 50
2018-10-31 02:00 | 49
2018-10-31 03:00 | 50
2018-10-31 04:00 | 48
2018-10-31 05:00 | 47
2018-10-31 06:00 | 46
2018-10-31 07:00 | 46
2018-10-31 08:00 | 49
2018-10-31 09:00 | 52
2018-10-31 10:00 | 54
2018-10-31 11:00 | 57
2018-10-31 12:00 | 61
2018-10-31 13:00 | 63
2018-10-31 14:00 | 64
2018-10-31 15:00 | 64
2018-10-31 16:00 | 63
2018-10-31 17:00 | 63
2018-10-31 18:00 | 61
2018-10-31 19:00 | 61
2018-10-31 20:00 | 60
2018-10-31 21:00 | 61
2018-10-31 22:00 | 61
2018-10-31 23:00 | 61
2018-11-01 | 61
2018-11-01 01:00 | 61
2018-11-01 02:00 | 60
2018-11-01 03:00 | 57
2018-11-01 04:00 | 59
2018-11-01 05:00 | 60
2018-11-01 06:00 | 59
2018-11-01 07:00 | 57
2018-11-01 08:00 | 59
2018-11-01 09:00 | 59
2018-11-01 10:00 | 63
2018-11-01 11:00 | 63
2018-11-01 12:00 | 66
2018-11-01 13:00 | 70
2018-11-01 14:00 | 68
2018-11-01 15:00 | 66
2018-11-01 16:00 | 66
2018-11-01 17:00 | 67
2018-11-01 18:00 | 66
2018-11-01 19:00 | 64
2018-11-01 20:00 | 64
2018-11-01 21:00 | 63
2018-11-01 22:00 | 63
2018-11-01 23:00 | 63
2018-11-02 | 63
2018-11-02 01:00 | 63
2018-11-02 02:00 | 63
2018-11-02 03:00 | 66
2018-11-02 04:00 | 66
2018-11-02 05:00 | 68
2018-11-02 06:00 | 66
2018-11-02 07:00 | 64
2018-11-02 08:00 | 65
2018-11-02 09:00 | 64
2018-11-02 10:00 | 66
2018-11-02 11:00 | 68
2018-11-02 12:00 | 66
2018-11-02 13:00 | 66
2018-11-02 14:00 | 68
2018-11-02 15:00 | 68
2018-11-02 16:00 | 66
2018-11-02 17:00 | 66
2018-11-02 18:00 | 64
2018-11-02 19:00 | 64
2018-11-02 20:00 | 65
2018-11-02 21:00 | 64
2018-11-02 22:00 | 64
2018-11-02 23:00 | 66
2018-11-03 | 66
2018-11-03 01:00 | 66
2018-11-03 02:00 | 66
2018-11-03 03:00 | 59
2018-11-03 04:00 | 59
2018-11-03 05:00 | 58
2018-11-03 06:00 | 59
2018-11-03 07:00 | 59
2018-11-03 08:00 | 60
2018-11-03 09:00 | 61
2018-11-03 10:00 | 57
2018-11-03 11:00 | 55
2018-11-03 12:00 | 55
2018-11-03 13:00 | 55
2018-11-03 14:00 | 58
2018-11-03 15:00 | 59
2018-11-03 16:00 | 57
2018-11-03 17:00 | 57
2018-11-03 18:00 | 55
2018-11-03 19:00 | 55
2018-11-03 20:00 | 54
2018-11-03 21:00 | 54
2018-11-03 22:00 | 54
2018-11-03 23:00 | 52
2018-11-04 | 52
2018-11-04 01:00 | 50
2018-11-04 01:00 | 51
2018-11-04 02:00 | 48
2018-11-04 03:00 | 48
2018-11-04 04:00 | 47
2018-11-04 05:00 | 46
2018-11-04 06:00 | 46
2018-11-04 07:00 | 47
2018-11-04 08:00 | 46
2018-11-04 09:00 | 48
2018-11-04 10:00 | 50
2018-11-04 11:00 | 52
2018-11-04 12:00 | 54
2018-11-04 13:00 | 55
2018-11-04 14:00 | 55
2018-11-04 15:00 | 55
2018-11-04 16:00 | 56
2018-11-04 17:00 | 52
2018-11-04 18:00 | 52
2018-11-04 19:00 | 51
2018-11-04 20:00 | 52
2018-11-04 21:00 | 50
2018-11-04 22:00 | 49
2018-11-04 23:00 | 50
2018-11-05 | 49
2018-11-05 01:00 | 49
2018-11-05 02:00 | 48
2018-11-05 03:00 | 48
2018-11-05 04:00 | 50
2018-11-05 05:00 | 50
2018-11-05 06:00 | 50
2018-11-05 07:00 | 51
2018-11-05 08:00 | 52
2018-11-05 09:00 | 50
2018-11-05 10:00 | 52
2018-11-05 11:00 | 52
2018-11-05 12:00 | 52
2018-11-05 13:00 | 54
2018-11-05 14:00 | 54
2018-11-05 15:00 | 54
2018-11-05 16:00 | 54
2018-11-05 17:00 | 54
2018-11-05 18:00 | 54
2018-11-05 19:00 | 53
2018-11-05 20:00 | 54
2018-11-05 21:00 | 54
2018-11-05 22:00 | 52
2018-11-05 23:00 | 52
2018-11-06 | 51
2018-11-06 01:00 | 51
2018-11-06 02:00 | 50
2018-11-06 03:00 | 50
2018-11-06 04:00 | 50
2018-11-06 05:00 | 50
2018-11-06 06:00 | 52
2018-11-06 07:00 | 51
2018-11-06 08:00 | 52
2018-11-06 09:00 | 54
2018-11-06 10:00 | 56
2018-11-06 11:00 | 55
2018-11-06 12:00 | 55
2018-11-06 13:00 | 60
2018-11-06 14:00 | 57
2018-11-06 15:00 | 59
2018-11-06 16:00 | 61
2018-11-06 17:00 | 61
2018-11-06 18:00 | 59
2018-11-06 19:00 | 59
2018-11-06 20:00 | 59
2018-11-06 21:00 | 57
2018-11-06 22:00 | 59
2018-11-06 23:00 | 57
2018-11-07 | 58
2018-11-07 01:00 | 58
2018-11-07 02:00 | 57
2018-11-07 03:00 | 59
2018-11-07 04:00 | 57
2018-11-07 05:00 | 55
2018-11-07 06:00 | 55
2018-11-07 07:00 | 53
2018-11-07 08:00 | 55
2018-11-07 09:00 | 55
2018-11-07 10:00 | 57
2018-11-07 11:00 | 59
2018-11-07 12:00 | 63
2018-11-07 13:00 | 63
2018-11-07 14:00 | 63
2018-11-07 15:00 | 64
2018-11-07 16:00 | 63
2018-11-07 17:00 | 63
2018-11-07 18:00 | 61
2018-11-07 19:00 | 61
2018-11-07 20:00 | 61
2018-11-07 21:00 | 61
2018-11-07 22:00 | 60
2018-11-07 23:00 | 61
2018-11-08 | 59
2018-11-08 01:00 | 57
2018-11-08 02:00 | 55
2018-11-08 03:00 | 52
2018-11-08 04:00 | 50
2018-11-08 05:00 | 48
2018-11-08 06:00 | 48
2018-11-08 07:00 | 48
2018-11-08 08:00 | 48
2018-11-08 09:00 | 48
2018-11-08 10:00 | 50
2018-11-08 11:00 | 52
2018-11-08 12:00 | 54
2018-11-08 13:00 | 55
2018-11-08 14:00 | 55
2018-11-08 15:00 | 55
2018-11-08 16:00 | 56
2018-11-08 17:00 | 54
2018-11-08 18:00 | 54
2018-11-08 19:00 | 51
2018-11-08 20:00 | 50
2018-11-08 21:00 | 48
2018-11-08 22:00 | 48
2018-11-08 23:00 | 46
2018-11-09 | 46
2018-11-09 01:00 | 45
2018-11-09 02:00 | 45
2018-11-09 03:00 | 45
2018-11-09 04:00 | 44
2018-11-09 05:00 | 43
2018-11-09 06:00 | 43
2018-11-09 07:00 | 44
2018-11-09 08:00 | 46
2018-11-09 09:00 | 48
2018-11-09 10:00 | 51
2018-11-09 11:00 | 50
2018-11-09 12:00 | 52
2018-11-09 13:00 | 52
2018-11-09 14:00 | 52
2018-11-09 15:00 | 52
2018-11-09 16:00 | 52
2018-11-09 17:00 | 52
2018-11-09 18:00 | 51.5
2018-11-09 19:00 | 51
2018-11-09 20:00 | 54
2018-11-09 21:00 | 54
2018-11-09 22:00 | 54
2018-11-09 23:00 | 54
2018-11-10 | 51
2018-11-10 01:00 | 50
2018-11-10 02:00 | 50
2018-11-10 03:00 | 48
2018-11-10 04:00 | 47
2018-11-10 05:00 | 46
2018-11-10 06:00 | 46
2018-11-10 07:00 | 47
2018-11-10 08:00 | 46
2018-11-10 09:00 | 46
2018-11-10 10:00 | 47
2018-11-10 11:00 | 45
2018-11-10 12:00 | 46
2018-11-10 13:00 | 46
2018-11-10 14:00 | 45
2018-11-10 15:00 | 46
2018-11-10 16:00 | 44
2018-11-10 17:00 | 43
2018-11-10 18:00 | 41
2018-11-10 19:00 | 40
2018-11-10 20:00 | 39
2018-11-10 21:00 | 39
2018-11-10 22:00 | 39
2018-11-10 23:00 | 37
2018-11-11 | 38
2018-11-11 01:00 | 38
2018-11-11 02:00 | 37
2018-11-11 03:00 | 37
2018-11-11 04:00 | 36
2018-11-11 05:00 | 37
2018-11-11 06:00 | 37
2018-11-11 07:00 | 37
2018-11-11 08:00 | 37
2018-11-11 09:00 | 37
2018-11-11 10:00 | 41
2018-11-11 11:00 | 43
2018-11-11 12:00 | 45
2018-11-11 13:00 | 46
2018-11-11 14:00 | 46
2018-11-11 15:00 | 46
2018-11-11 16:00 | 47
2018-11-11 17:00 | 46
2018-11-11 18:00 | 46
2018-11-11 19:00 | 45
2018-11-11 20:00 | 45
2018-11-11 21:00 | 45
2018-11-11 22:00 | 44
2018-11-11 23:00 | 43
2018-11-12 | 43
2018-11-12 01:00 | 40
2018-11-12 02:00 | 43
2018-11-12 03:00 | 39
2018-11-12 04:00 | 39
2018-11-12 05:00 | 39
2018-11-12 06:00 | 39
2018-11-12 07:00 | 40
2018-11-12 08:00 | 41
2018-11-12 09:00 | 45
2018-11-12 10:00 | 47
2018-11-12 11:00 | 48
2018-11-12 12:00 | 48
2018-11-12 13:00 | 49
2018-11-12 14:00 | 48
2018-11-12 15:00 | 48
2018-11-12 16:00 | 48
2018-11-12 17:00 | 46
2018-11-12 18:00 | 46
2018-11-12 19:00 | 48
2018-11-12 20:00 | 46
2018-11-12 21:00 | 48
2018-11-12 22:00 | 48
2018-11-12 23:00 | 46
2018-11-13 | 47
2018-11-13 01:00 | 46
2018-11-13 02:00 | 46
2018-11-13 03:00 | 46
2018-11-13 04:00 | 48
2018-11-13 05:00 | 50
2018-11-13 06:00 | 50
2018-11-13 07:00 | 50
2018-11-13 08:00 | 54
2018-11-13 09:00 | 52
2018-11-13 10:00 | 50
2018-11-13 11:00 | 50
2018-11-13 12:00 | 46
2018-11-13 13:00 | 48
2018-11-13 14:00 | 48
2018-11-13 15:00 | 48
2018-11-13 16:00 | 49
2018-11-13 17:00 | 46
2018-11-13 18:00 | 46
2018-11-13 19:00 | 46
2018-11-13 20:00 | 46
2018-11-13 21:00 | 45
2018-11-13 22:00 | 45
2018-11-13 23:00 | 45
2018-11-14 | 44
2018-11-14 01:00 | 43
2018-11-14 02:00 | 41
2018-11-14 03:00 | 39
2018-11-14 04:00 | 39
2018-11-14 05:00 | 37
2018-11-14 06:00 | 39
2018-11-14 07:00 | 38
2018-11-14 08:00 | 37
2018-11-14 09:00 | 37
2018-11-14 10:00 | 38
2018-11-14 11:00 | 39
2018-11-14 12:00 | 39
2018-11-14 13:00 | 39
2018-11-14 14:00 | 39
2018-11-14 15:00 | 39
2018-11-14 16:00 | 38
2018-11-14 17:00 | 37
2018-11-14 18:00 | 37
2018-11-14 19:00 | 36
2018-11-14 20:00 | 36
2018-11-14 21:00 | 34
2018-11-14 22:00 | 34
2018-11-14 23:00 | 34
2018-11-15 | 33
2018-11-15 01:00 | 33
2018-11-15 02:00 | 32
2018-11-15 03:00 | 31
2018-11-15 04:00 | 31
2018-11-15 05:00 | 31
2018-11-15 06:00 | 31
2018-11-15 07:00 | 32
2018-11-15 08:00 | 32
2018-11-15 09:00 | 32
2018-11-15 10:00 | 34
2018-11-15 11:00 | 34
2018-11-15 12:00 | 36
2018-11-15 13:00 | 36
2018-11-15 14:00 | 34
2018-11-15 15:00 | 34
2018-11-15 16:00 | 34
2018-11-15 17:00 | 30
2018-11-15 18:00 | 30
2018-11-15 19:00 | 33
2018-11-15 20:00 | 35
2018-11-15 21:00 | 36
2018-11-15 22:00 | 38
2018-11-15 23:00 | 39
2018-11-16 | 40
2018-11-16 01:00 | 40
2018-11-16 02:00 | 41
2018-11-16 03:00 | 41
2018-11-16 04:00 | 42
2018-11-16 05:00 | 41
2018-11-16 06:00 | 38
2018-11-16 07:00 | 38
2018-11-16 08:00 | 37
2018-11-16 09:00 | 39
2018-11-16 10:00 | 41
2018-11-16 11:00 | 43
2018-11-16 12:00 | 45
2018-11-16 13:00 | 45
2018-11-16 14:00 | 46
2018-11-16 15:00 | 46
2018-11-16 16:00 | 45
2018-11-16 17:00 | 45
2018-11-16 18:00 | 43
2018-11-16 19:00 | 43
2018-11-16 20:00 | 43
2018-11-16 21:00 | 41
2018-11-16 22:00 | 41
2018-11-16 23:00 | 39
2018-11-17 | 40
2018-11-17 01:00 | 40
2018-11-17 02:00 | 39
2018-11-17 03:00 | 41
2018-11-17 04:00 | 41
2018-11-17 05:00 | 41
2018-11-17 06:00 | 43
2018-11-17 07:00 | 42
2018-11-17 08:00 | 43
2018-11-17 09:00 | 45
2018-11-17 10:00 | 46
2018-11-17 11:00 | 48
2018-11-17 12:00 | 46
2018-11-17 13:00 | 47
2018-11-17 14:00 | 48
2018-11-17 15:00 | 48
2018-11-17 16:00 | 47
2018-11-17 17:00 | 46
2018-11-17 18:00 | 46
2018-11-17 19:00 | 46
2018-11-17 20:00 | 46
2018-11-17 21:00 | 46
2018-11-17 22:00 | 45
2018-11-17 23:00 | 45
2018-11-18 | 44
2018-11-18 01:00 | 44
2018-11-18 02:00 | 43
2018-11-18 03:00 | 43
2018-11-18 04:00 | 41
2018-11-18 05:00 | 41
2018-11-18 06:00 | 41
2018-11-18 07:00 | 40
2018-11-18 08:00 | 41
2018-11-18 09:00 | 41
2018-11-18 10:00 | 41
2018-11-18 11:00 | 41
2018-11-18 12:00 | 43
2018-11-18 13:00 | 43
2018-11-18 14:00 | 43
2018-11-18 15:00 | 45
2018-11-18 16:00 | 44
2018-11-18 17:00 | 45
2018-11-18 18:00 | 43
2018-11-18 19:00 | 44
2018-11-18 20:00 | 45
2018-11-18 21:00 | 43
2018-11-18 22:00 | 43
2018-11-18 23:00 | 43
2018-11-19 | 42
2018-11-19 01:00 | 42
2018-11-19 02:00 | 41
2018-11-19 03:00 | 41
2018-11-19 04:00 | 42
2018-11-19 05:00 | 43
2018-11-19 06:00 | 45
2018-11-19 07:00 | 47
2018-11-19 08:00 | 48
2018-11-19 09:00 | 46
2018-11-19 10:00 | 48
2018-11-19 11:00 | 46
2018-11-19 12:00 | 48
2018-11-19 13:00 | 51
2018-11-19 14:00 | 50
2018-11-19 15:00 | 50
2018-11-19 16:00 | 49
2018-11-19 17:00 | 48
2018-11-19 18:00 | 50
2018-11-19 19:00 | 49
2018-11-19 20:00 | 48
2018-11-19 21:00 | 48
2018-11-19 22:00 | 48
2018-11-19 23:00 | 48
2018-11-20 | 47
2018-11-20 01:00 | 47
2018-11-20 02:00 | 46
2018-11-20 03:00 | 46
2018-11-20 04:00 | 46
2018-11-20 05:00 | 46
2018-11-20 06:00 | 46
2018-11-20 07:00 | 45
2018-11-20 08:00 | 45
2018-11-20 09:00 | 43
2018-11-20 10:00 | 42
2018-11-20 11:00 | 43
2018-11-20 12:00 | 45
2018-11-20 13:00 | 46
2018-11-20 14:00 | 46
2018-11-20 15:00 | 46
2018-11-20 16:00 | 47
2018-11-20 17:00 | 46
2018-11-20 18:00 | 45
2018-11-20 19:00 | 45
2018-11-20 20:00 | 45
2018-11-20 21:00 | 45
2018-11-20 22:00 | 43
2018-11-20 23:00 | 43
2018-11-21 | 41
2018-11-21 01:00 | 40
2018-11-21 02:00 | 39
2018-11-21 03:00 | 39
2018-11-21 04:00 | 39
2018-11-21 05:00 | 39
2018-11-21 06:00 | 37
2018-11-21 07:00 | 38
2018-11-21 08:00 | 39
2018-11-21 09:00 | 39
2018-11-21 10:00 | 41
2018-11-21 11:00 | 43
2018-11-21 12:00 | 43
2018-11-21 13:00 | 44
2018-11-21 14:00 | 45
2018-11-21 15:00 | 45
2018-11-21 16:00 | 45
2018-11-21 17:00 | 45
2018-11-21 18:00 | 43
2018-11-21 19:00 | 38
2018-11-21 20:00 | 37
2018-11-21 21:00 | 36
2018-11-21 22:00 | 34
2018-11-21 23:00 | 30
2018-11-22 | 29
2018-11-22 01:00 | 27
2018-11-22 02:00 | 27
2018-11-22 03:00 | 25
2018-11-22 04:00 | 24
2018-11-22 05:00 | 25
2018-11-22 06:00 | 21
2018-11-22 07:00 | 21
2018-11-22 08:00 | 21
2018-11-22 09:00 | 21
2018-11-22 10:00 | 23
2018-11-22 11:00 | 25
2018-11-22 12:00 | 27
2018-11-22 13:00 | 27
2018-11-22 14:00 | 28
2018-11-22 15:00 | 28
2018-11-22 16:00 | 28
2018-11-22 17:00 | 27
2018-11-22 18:00 | 25
2018-11-22 19:00 | 24
2018-11-22 20:00 | 21
2018-11-22 21:00 | 21
2018-11-22 22:00 | 21
2018-11-22 23:00 | 19
2018-11-23 | 19
2018-11-23 01:00 | 19
2018-11-23 02:00 | 19
2018-11-23 03:00 | 18
2018-11-23 04:00 | 18
2018-11-23 05:00 | 18
2018-11-23 06:00 | 18
2018-11-23 07:00 | 17
2018-11-23 08:00 | 19
2018-11-23 09:00 | 23
2018-11-23 10:00 | 22
2018-11-23 11:00 | 27
2018-11-23 12:00 | 28
2018-11-23 13:00 | 31
2018-11-23 14:00 | 30
2018-11-23 15:00 | 30
2018-11-23 16:00 | 32
2018-11-23 17:00 | 32
2018-11-23 18:00 | 32
2018-11-23 19:00 | 32
2018-11-23 20:00 | 32
2018-11-23 21:00 | 32
2018-11-23 22:00 | 32
2018-11-23 23:00 | 32
2018-11-24 | 32
2018-11-24 01:00 | 32
2018-11-24 02:00 | 32
2018-11-24 03:00 | 32
2018-11-24 04:00 | 32
2018-11-24 05:00 | 32
2018-11-24 06:00 | 34
2018-11-24 07:00 | 34
2018-11-24 08:00 | 36
2018-11-24 09:00 | 36
2018-11-24 10:00 | 38
2018-11-24 11:00 | 39
2018-11-24 12:00 | 39
2018-11-24 13:00 | 42
2018-11-24 14:00 | 43
2018-11-24 15:00 | 45
2018-11-24 16:00 | 46
2018-11-24 17:00 | 46
2018-11-24 18:00 | 46
2018-11-24 19:00 | 48
2018-11-24 20:00 | 46
2018-11-24 21:00 | 48
2018-11-24 22:00 | 48
2018-11-24 23:00 | 48
2018-11-25 | 49
2018-11-25 01:00 | 50
2018-11-25 02:00 | 46
2018-11-25 03:00 | 48
2018-11-25 04:00 | 47
2018-11-25 05:00 | 46
2018-11-25 06:00 | 46
2018-11-25 07:00 | 47
2018-11-25 08:00 | 46
2018-11-25 09:00 | 48
2018-11-25 10:00 | 50
2018-11-25 11:00 | 52
2018-11-25 12:00 | 54
2018-11-25 13:00 | 54
2018-11-25 14:00 | 54
2018-11-25 15:00 | 54
2018-11-25 16:00 | 54
2018-11-25 17:00 | 54
2018-11-25 18:00 | 52
2018-11-25 19:00 | 53
2018-11-25 20:00 | 54
2018-11-25 21:00 | 52
2018-11-25 22:00 | 52
2018-11-25 23:00 | 50
2018-11-26 | 49
2018-11-26 01:00 | 45
2018-11-26 02:00 | 46
2018-11-26 03:00 | 45
2018-11-26 04:00 | 45
2018-11-26 05:00 | 45
2018-11-26 06:00 | 45
2018-11-26 07:00 | 47
2018-11-26 08:00 | 48
2018-11-26 09:00 | 50
2018-11-26 10:00 | 51
2018-11-26 11:00 | 54
2018-11-26 12:00 | 54
2018-11-26 13:00 | 53
2018-11-26 14:00 | 54
2018-11-26 15:00 | 52
2018-11-26 16:00 | 50
2018-11-26 17:00 | 48
2018-11-26 18:00 | 48
2018-11-26 19:00 | 49
2018-11-26 20:00 | 48
2018-11-26 21:00 | 48
2018-11-26 22:00 | 48
2018-11-26 23:00 | 46
2018-11-27 | 47
2018-11-27 01:00 | 45
2018-11-27 02:00 | 45
2018-11-27 03:00 | 43
2018-11-27 04:00 | 43
2018-11-27 05:00 | 43
2018-11-27 06:00 | 43
2018-11-27 07:00 | 42
2018-11-27 08:00 | 43
2018-11-27 09:00 | 43
2018-11-27 10:00 | 44
2018-11-27 11:00 | 45
2018-11-27 12:00 | 46
2018-11-27 13:00 | 45
2018-11-27 14:00 | 45
2018-11-27 15:00 | 45
2018-11-27 16:00 | 43
2018-11-27 17:00 | 43
2018-11-27 18:00 | 43
2018-11-27 19:00 | 42
2018-11-27 20:00 | 41
2018-11-27 21:00 | 39
2018-11-27 22:00 | 39
2018-11-27 23:00 | 39
2018-11-28 | 38
2018-11-28 01:00 | 38
2018-11-28 02:00 | 37
2018-11-28 03:00 | 39
2018-11-28 04:00 | 39
2018-11-28 05:00 | 37
2018-11-28 06:00 | 37
2018-11-28 07:00 | 38
2018-11-28 08:00 | 37
2018-11-28 09:00 | 37
2018-11-28 10:00 | 39
2018-11-28 11:00 | 39
2018-11-28 12:00 | 41
2018-11-28 13:00 | 41
2018-11-28 14:00 | 43
2018-11-28 15:00 | 43
2018-11-28 16:00 | 42
2018-11-28 17:00 | 43
2018-11-28 18:00 | 43
2018-11-28 19:00 | 42
2018-11-28 20:00 | 43
2018-11-28 21:00 | 43
2018-11-28 22:00 | 42
2018-11-28 23:00 | 43
2018-11-29 | 42
2018-11-29 01:00 | 41
2018-11-29 02:00 | 43
2018-11-29 03:00 | 41
2018-11-29 04:00 | 41
2018-11-29 05:00 | 41
2018-11-29 06:00 | 41
2018-11-29 07:00 | 42
2018-11-29 08:00 | 43
2018-11-29 09:00 | 43
2018-11-29 10:00 | 43
2018-11-29 11:00 | 45
2018-11-29 12:00 | 45
2018-11-29 13:00 | 45
2018-11-29 14:00 | 46
2018-11-29 15:00 | 45
2018-11-29 16:00 | 44
2018-11-29 17:00 | 43
2018-11-29 18:00 | 43
2018-11-29 19:00 | 42
2018-11-29 20:00 | 43
2018-11-29 21:00 | 41
2018-11-29 22:00 | 41
2018-11-29 23:00 | 39
2018-11-30 | 40
2018-11-30 01:00 | 40
2018-11-30 02:00 | 39
2018-11-30 03:00 | 39
2018-11-30 04:00 | 39
2018-11-30 05:00 | 39
2018-11-30 06:00 | 39
2018-11-30 07:00 | 39
2018-11-30 08:00 | 39
2018-11-30 09:00 | 39
2018-11-30 10:00 | 40
2018-11-30 11:00 | 41
2018-11-30 12:00 | 43
2018-11-30 13:00 | 43
2018-11-30 14:00 | 43
2018-11-30 15:00 | 43
2018-11-30 16:00 | 41
2018-11-30 17:00 | 39
2018-11-30 18:00 | 39
2018-11-30 19:00 | 40
2018-11-30 20:00 | 39
2018-11-30 21:00 | 41
2018-11-30 22:00 | 41
2018-11-30 23:00 | 41
2018-12-01 | 41
2018-12-01 01:00 | 41
2018-12-01 02:00 | 41
2018-12-01 03:00 | 39
2018-12-01 04:00 | 40
2018-12-01 05:00 | 39
2018-12-01 06:00 | 37
2018-12-01 07:00 | 38
2018-12-01 08:00 | 39
2018-12-01 09:00 | 41
2018-12-01 10:00 | 42
2018-12-01 11:00 | 43
2018-12-01 12:00 | 43
2018-12-01 13:00 | 44
2018-12-01 14:00 | 45
2018-12-01 15:00 | 45
2018-12-01 16:00 | 45
2018-12-01 17:00 | 45
2018-12-01 18:00 | 45
2018-12-01 19:00 | 44
2018-12-01 20:00 | 43
2018-12-01 21:00 | 43
2018-12-01 22:00 | 42
2018-12-01 23:00 | 43
2018-12-02 | 42
2018-12-02 01:00 | 43
2018-12-02 02:00 | 45
2018-12-02 03:00 | 43
2018-12-02 04:00 | 44
2018-12-02 05:00 | 45
2018-12-02 06:00 | 45
2018-12-02 07:00 | 46
2018-12-02 08:00 | 46
2018-12-02 09:00 | 46
2018-12-02 10:00 | 47
2018-12-02 11:00 | 48
2018-12-02 12:00 | 48
2018-12-02 13:00 | 50
2018-12-02 14:00 | 52
2018-12-02 15:00 | 52
2018-12-02 16:00 | 51
2018-12-02 17:00 | 54
2018-12-02 18:00 | 52
2018-12-02 19:00 | 52
2018-12-02 20:00 | 52
2018-12-02 21:00 | 54
2018-12-02 22:00 | 52
2018-12-02 23:00 | 55
2018-12-03 | 57
2018-12-03 01:00 | 55
2018-12-03 02:00 | 55
2018-12-03 03:00 | 55
2018-12-03 04:00 | 55
2018-12-03 05:00 | 55
2018-12-03 06:00 | 55
2018-12-03 07:00 | 55
2018-12-03 08:00 | 55
2018-12-03 09:00 | 55
2018-12-03 10:00 | 55
2018-12-03 11:00 | 55
2018-12-03 12:00 | 54
2018-12-03 13:00 | 54
2018-12-03 14:00 | 54
2018-12-03 15:00 | 54
2018-12-03 16:00 | 53
2018-12-03 17:00 | 52
2018-12-03 18:00 | 52
2018-12-03 19:00 | 50
2018-12-03 20:00 | 50
2018-12-03 21:00 | 48
2018-12-03 22:00 | 48
2018-12-03 23:00 | 46
2018-12-04 | 46
2018-12-04 01:00 | 43
2018-12-04 02:00 | 43
2018-12-04 03:00 | 39
2018-12-04 04:00 | 39
2018-12-04 05:00 | 39
2018-12-04 06:00 | 39
2018-12-04 07:00 | 38
2018-12-04 08:00 | 37
2018-12-04 09:00 | 39
2018-12-04 10:00 | 40
2018-12-04 11:00 | 39
2018-12-04 12:00 | 41
2018-12-04 13:00 | 42
2018-12-04 14:00 | 41
2018-12-04 15:00 | 41
2018-12-04 16:00 | 40
2018-12-04 17:00 | 39
2018-12-04 18:00 | 37
2018-12-04 19:00 | 37
2018-12-04 20:00 | 36
2018-12-04 21:00 | 34
2018-12-04 22:00 | 33
2018-12-04 23:00 | 32
2018-12-05 | 32
2018-12-05 01:00 | 31
2018-12-05 02:00 | 30
2018-12-05 03:00 | 30
2018-12-05 04:00 | 30
2018-12-05 05:00 | 30
2018-12-05 06:00 | 28
2018-12-05 07:00 | 29
2018-12-05 08:00 | 30
2018-12-05 09:00 | 30
2018-12-05 10:00 | 32
2018-12-05 11:00 | 34
2018-12-05 12:00 | 34
2018-12-05 13:00 | 36
2018-12-05 14:00 | 36
2018-12-05 15:00 | 37
2018-12-05 16:00 | 37
2018-12-05 17:00 | 38
2018-12-05 18:00 | 38
2018-12-05 19:00 | 36
2018-12-05 20:00 | 36
2018-12-05 21:00 | 36
2018-12-05 22:00 | 36
2018-12-05 23:00 | 35
2018-12-06 | 35
2018-12-06 01:00 | 34
2018-12-06 02:00 | 34
2018-12-06 03:00 | 33
2018-12-06 04:00 | 33
2018-12-06 05:00 | 33
2018-12-06 06:00 | 32
2018-12-06 07:00 | 33
2018-12-06 08:00 | 33
2018-12-06 09:00 | 34
2018-12-06 10:00 | 36
2018-12-06 11:00 | 37
2018-12-06 12:00 | 37
2018-12-06 13:00 | 39
2018-12-06 14:00 | 39
2018-12-06 15:00 | 39
2018-12-06 16:00 | 40
2018-12-06 17:00 | 39
2018-12-06 18:00 | 39
2018-12-06 19:00 | 39
2018-12-06 20:00 | 39
2018-12-06 21:00 | 39
2018-12-06 22:00 | 39
2018-12-06 23:00 | 39
2018-12-07 | 40
2018-12-07 01:00 | 40
2018-12-07 02:00 | 39
2018-12-07 03:00 | 39
2018-12-07 04:00 | 39
2018-12-07 05:00 | 37
2018-12-07 06:00 | 37
2018-12-07 07:00 | 36
2018-12-07 08:00 | 36
2018-12-07 09:00 | 36
2018-12-07 10:00 | 37
2018-12-07 11:00 | 37
2018-12-07 12:00 | 37
2018-12-07 13:00 | 38
2018-12-07 14:00 | 39
2018-12-07 15:00 | 37
2018-12-07 16:00 | 37
2018-12-07 17:00 | 36
2018-12-07 18:00 | 34
2018-12-07 19:00 | 33
2018-12-07 20:00 | 32
2018-12-07 21:00 | 30
2018-12-07 22:00 | 30
2018-12-07 23:00 | 30
2018-12-08 | 29
2018-12-08 01:00 | 29
2018-12-08 02:00 | 28
2018-12-08 03:00 | 28
2018-12-08 04:00 | 28
2018-12-08 05:00 | 27
2018-12-08 06:00 | 27
2018-12-08 07:00 | 26
2018-12-08 08:00 | 27
2018-12-08 09:00 | 28
2018-12-08 10:00 | 30
2018-12-08 11:00 | 32
2018-12-08 12:00 | 34
2018-12-08 13:00 | 34
2018-12-08 14:00 | 36
2018-12-08 15:00 | 36
2018-12-08 16:00 | 35
2018-12-08 17:00 | 34
2018-12-08 18:00 | 34
2018-12-08 19:00 | 34
2018-12-08 20:00 | 34
2018-12-08 21:00 | 34
2018-12-08 22:00 | 34
2018-12-08 23:00 | 34
2018-12-09 | 33
2018-12-09 01:00 | 32
2018-12-09 02:00 | 32
2018-12-09 03:00 | 30
2018-12-09 04:00 | 31
2018-12-09 05:00 | 30
2018-12-09 06:00 | 30
2018-12-09 07:00 | 30
2018-12-09 08:00 | 30
2018-12-09 09:00 | 32
2018-12-09 10:00 | 33
2018-12-09 11:00 | 34
2018-12-09 12:00 | 36
2018-12-09 13:00 | 36
2018-12-09 14:00 | 36
2018-12-09 15:00 | 36
2018-12-09 16:00 | 36
2018-12-09 17:00 | 36
2018-12-09 18:00 | 36
2018-12-09 19:00 | 35
2018-12-09 20:00 | 36
2018-12-09 21:00 | 36
2018-12-09 22:00 | 34
2018-12-09 23:00 | 34
2018-12-10 | 33
2018-12-10 01:00 | 32
2018-12-10 02:00 | 32
2018-12-10 03:00 | 30
2018-12-10 04:00 | 31
2018-12-10 05:00 | 30
2018-12-10 06:00 | 30
2018-12-10 07:00 | 30
2018-12-10 08:00 | 30
2018-12-10 09:00 | 34
2018-12-10 10:00 | 37
2018-12-10 11:00 | 37
2018-12-10 12:00 | 39
2018-12-10 13:00 | 38
2018-12-10 14:00 | 39
2018-12-10 15:00 | 39
2018-12-10 16:00 | 39
2018-12-10 17:00 | 37
2018-12-10 18:00 | 37
2018-12-10 19:00 | 37
2018-12-10 20:00 | 37
2018-12-10 21:00 | 37
2018-12-10 22:00 | 35
2018-12-10 23:00 | 34
2018-12-11 | 32
2018-12-11 01:00 | 32
2018-12-11 02:00 | 32
2018-12-11 03:00 | 30
2018-12-11 04:00 | 31
2018-12-11 05:00 | 30
2018-12-11 06:00 | 30
2018-12-11 07:00 | 30
2018-12-11 08:00 | 30
2018-12-11 09:00 | 34
2018-12-11 10:00 | 35
2018-12-11 11:00 | 36
2018-12-11 12:00 | 39
2018-12-11 13:00 | 40
2018-12-11 14:00 | 39
2018-12-11 15:00 | 39
2018-12-11 16:00 | 40
2018-12-11 17:00 | 37
2018-12-11 18:00 | 37
2018-12-11 19:00 | 38
2018-12-11 20:00 | 37
2018-12-11 21:00 | 37
2018-12-11 22:00 | 36
2018-12-11 23:00 | 36
2018-12-12 | 35
2018-12-12 01:00 | 35
2018-12-12 02:00 | 36
2018-12-12 03:00 | 36
2018-12-12 04:00 | 35
2018-12-12 05:00 | 34
2018-12-12 06:00 | 34
2018-12-12 07:00 | 34
2018-12-12 08:00 | 36
2018-12-12 09:00 | 36
2018-12-12 10:00 | 38
2018-12-12 11:00 | 39
2018-12-12 12:00 | 39
2018-12-12 13:00 | 40
2018-12-12 14:00 | 39
2018-12-12 15:00 | 39
2018-12-12 16:00 | 39
2018-12-12 17:00 | 39
2018-12-12 18:00 | 39
2018-12-12 19:00 | 39
2018-12-12 20:00 | 37
2018-12-12 21:00 | 37
2018-12-12 22:00 | 37
2018-12-12 23:00 | 36
2018-12-13 | 36
2018-12-13 01:00 | 36
2018-12-13 02:00 | 36
2018-12-13 03:00 | 34
2018-12-13 04:00 | 34
2018-12-13 05:00 | 34
2018-12-13 06:00 | 34
2018-12-13 07:00 | 34
2018-12-13 08:00 | 34
2018-12-13 09:00 | 36
2018-12-13 10:00 | 36
2018-12-13 11:00 | 36
2018-12-13 12:00 | 36
2018-12-13 13:00 | 38
2018-12-13 14:00 | 37
2018-12-13 15:00 | 37
2018-12-13 16:00 | 37
2018-12-13 17:00 | 37
2018-12-13 18:00 | 40
2018-12-13 19:00 | 40
2018-12-13 20:00 | 41
2018-12-13 21:00 | 41
2018-12-13 22:00 | 42
2018-12-13 23:00 | 40
2018-12-14 | 40
2018-12-14 01:00 | 40
2018-12-14 02:00 | 40
2018-12-14 03:00 | 41
2018-12-14 04:00 | 41
2018-12-14 05:00 | 41
2018-12-14 06:00 | 42
2018-12-14 07:00 | 42
2018-12-14 08:00 | 43
2018-12-14 09:00 | 46
2018-12-14 10:00 | 49
2018-12-14 11:00 | 45
2018-12-14 12:00 | 45
2018-12-14 13:00 | 45
2018-12-14 14:00 | 45
2018-12-14 15:00 | 45
2018-12-14 16:00 | 50
2018-12-14 17:00 | 52
2018-12-14 18:00 | 50
2018-12-14 19:00 | 51
2018-12-14 20:00 | 50
2018-12-14 21:00 | 50
2018-12-14 22:00 | 50
2018-12-14 23:00 | 50
2018-12-15 | 50
2018-12-15 01:00 | 48
2018-12-15 02:00 | 46
2018-12-15 03:00 | 46
2018-12-15 04:00 | 46
2018-12-15 05:00 | 46
2018-12-15 06:00 | 46
2018-12-15 07:00 | 47
2018-12-15 08:00 | 46
2018-12-15 09:00 | 46
2018-12-15 10:00 | 47
2018-12-15 11:00 | 46
2018-12-15 12:00 | 46
2018-12-15 13:00 | 48
2018-12-15 14:00 | 48
2018-12-15 15:00 | 48
2018-12-15 16:00 | 48
2018-12-15 17:00 | 48
2018-12-15 18:00 | 46
2018-12-15 19:00 | 47
2018-12-15 20:00 | 46
2018-12-15 21:00 | 46
2018-12-15 22:00 | 47
2018-12-15 23:00 | 46
2018-12-16 | 46
2018-12-16 01:00 | 45
2018-12-16 02:00 | 45
2018-12-16 03:00 | 45
2018-12-16 04:00 | 42
2018-12-16 05:00 | 41
2018-12-16 06:00 | 39
2018-12-16 07:00 | 40
2018-12-16 08:00 | 39
2018-12-16 09:00 | 39
2018-12-16 10:00 | 40
2018-12-16 11:00 | 39
2018-12-16 12:00 | 41
2018-12-16 13:00 | 41
2018-12-16 14:00 | 43
2018-12-16 15:00 | 41
2018-12-16 16:00 | 40
2018-12-16 17:00 | 39
2018-12-16 18:00 | 39
2018-12-16 19:00 | 40
2018-12-16 20:00 | 37
2018-12-16 21:00 | 37
2018-12-16 22:00 | 38
2018-12-16 23:00 | 37
2018-12-17 | 39
2018-12-17 01:00 | 39
2018-12-17 02:00 | 37
2018-12-17 03:00 | 37
2018-12-17 04:00 | 39
2018-12-17 05:00 | 39
2018-12-17 06:00 | 39
2018-12-17 07:00 | 40
2018-12-17 08:00 | 39
2018-12-17 09:00 | 41
2018-12-17 10:00 | 43
2018-12-17 11:00 | 45
2018-12-17 12:00 | 46
2018-12-17 13:00 | 45
2018-12-17 14:00 | 45
2018-12-17 15:00 | 45
2018-12-17 16:00 | 44
2018-12-17 17:00 | 43
2018-12-17 18:00 | 43
2018-12-17 19:00 | 43
2018-12-17 20:00 | 43
2018-12-17 21:00 | 43
2018-12-17 22:00 | 42
2018-12-17 23:00 | 41
2018-12-18 | 41
2018-12-18 01:00 | 40
2018-12-18 02:00 | 37
2018-12-18 03:00 | 37
2018-12-18 04:00 | 36
2018-12-18 05:00 | 36
2018-12-18 06:00 | 34
2018-12-18 07:00 | 33
2018-12-18 08:00 | 32
2018-12-18 09:00 | 32
2018-12-18 10:00 | 32
2018-12-18 11:00 | 32
2018-12-18 12:00 | 34
2018-12-18 13:00 | 34
2018-12-18 14:00 | 36
2018-12-18 15:00 | 36
2018-12-18 16:00 | 36
2018-12-18 17:00 | 36
2018-12-18 18:00 | 34
2018-12-18 19:00 | 33
2018-12-18 20:00 | 32
2018-12-18 21:00 | 30
2018-12-18 22:00 | 30
2018-12-18 23:00 | 28
2018-12-19 | 29
2018-12-19 01:00 | 28
2018-12-19 02:00 | 28
2018-12-19 03:00 | 27
2018-12-19 04:00 | 27
2018-12-19 05:00 | 27
2018-12-19 06:00 | 27
2018-12-19 07:00 | 28
2018-12-19 08:00 | 28
2018-12-19 09:00 | 30
2018-12-19 10:00 | 32
2018-12-19 11:00 | 34
2018-12-19 12:00 | 37
2018-12-19 13:00 | 38
2018-12-19 14:00 | 41
2018-12-19 15:00 | 41
2018-12-19 16:00 | 42
2018-12-19 17:00 | 43
2018-12-19 18:00 | 41
2018-12-19 19:00 | 40
2018-12-19 20:00 | 41
2018-12-19 21:00 | 41
2018-12-19 22:00 | 40
2018-12-19 23:00 | 39
2018-12-20 | 39
2018-12-20 01:00 | 40
2018-12-20 02:00 | 39
2018-12-20 03:00 | 37
2018-12-20 04:00 | 38
2018-12-20 05:00 | 37
2018-12-20 06:00 | 37
2018-12-20 07:00 | 38
2018-12-20 08:00 | 37
2018-12-20 09:00 | 41
2018-12-20 10:00 | 41
2018-12-20 11:00 | 41
2018-12-20 12:00 | 43
2018-12-20 13:00 | 42
2018-12-20 14:00 | 43
2018-12-20 15:00 | 41
2018-12-20 16:00 | 42
2018-12-20 17:00 | 43
2018-12-20 18:00 | 43
2018-12-20 19:00 | 43
2018-12-20 20:00 | 43
2018-12-20 21:00 | 43
2018-12-20 22:00 | 44
2018-12-20 23:00 | 43
2018-12-21 | 46
2018-12-21 01:00 | 56
2018-12-21 02:00 | 55
2018-12-21 03:00 | 57
2018-12-21 04:00 | 57
2018-12-21 05:00 | 57
2018-12-21 06:00 | 59
2018-12-21 07:00 | 61
2018-12-21 08:00 | 58
2018-12-21 09:00 | 61
2018-12-21 10:00 | 58
2018-12-21 11:00 | 57
2018-12-21 12:00 | 57
2018-12-21 13:00 | 57
2018-12-21 14:00 | 56
2018-12-21 15:00 | 56
2018-12-21 16:00 | 56
2018-12-21 17:00 | 55
2018-12-21 18:00 | 58
2018-12-21 19:00 | 56
2018-12-21 20:00 | 58
2018-12-21 21:00 | 56
2018-12-21 22:00 | 54
2018-12-21 23:00 | 53
2018-12-22 | 52
2018-12-22 01:00 | 51
2018-12-22 02:00 | 51
2018-12-22 03:00 | 51
2018-12-22 04:00 | 52
2018-12-22 05:00 | 52
2018-12-22 06:00 | 52
2018-12-22 07:00 | 49
2018-12-22 08:00 | 44
2018-12-22 09:00 | 43
2018-12-22 10:00 | 43
2018-12-22 11:00 | 43
2018-12-22 12:00 | 43
2018-12-22 13:00 | 43
2018-12-22 14:00 | 43
2018-12-22 15:00 | 43
2018-12-22 16:00 | 44
2018-12-22 17:00 | 43
2018-12-22 18:00 | 43
2018-12-22 19:00 | 42
2018-12-22 20:00 | 42
2018-12-22 21:00 | 42
2018-12-22 22:00 | 42
2018-12-22 23:00 | 41
2018-12-23 | 41
2018-12-23 01:00 | 40
2018-12-23 02:00 | 39
2018-12-23 03:00 | 39
2018-12-23 04:00 | 39
2018-12-23 05:00 | 38
2018-12-23 06:00 | 37
2018-12-23 07:00 | 37
2018-12-23 08:00 | 37
2018-12-23 09:00 | 38
2018-12-23 10:00 | 38
2018-12-23 11:00 | 39
2018-12-23 12:00 | 41
2018-12-23 13:00 | 42
2018-12-23 14:00 | 43
2018-12-23 15:00 | 43
2018-12-23 16:00 | 43
2018-12-23 17:00 | 42
2018-12-23 18:00 | 42
2018-12-23 19:00 | 42
2018-12-23 20:00 | 40
2018-12-23 21:00 | 40
2018-12-23 22:00 | 40
2018-12-23 23:00 | 39
2018-12-24 | 40
2018-12-24 01:00 | 36
2018-12-24 02:00 | 37
2018-12-24 03:00 | 36
2018-12-24 04:00 | 36
2018-12-24 05:00 | 36
2018-12-24 06:00 | 36
2018-12-24 07:00 | 37
2018-12-24 08:00 | 37
2018-12-24 09:00 | 38
2018-12-24 10:00 | 39
2018-12-24 11:00 | 39
2018-12-24 12:00 | 40
2018-12-24 13:00 | 43
2018-12-24 14:00 | 43
2018-12-24 15:00 | 43
2018-12-24 16:00 | 42
2018-12-24 17:00 | 42
2018-12-24 18:00 | 41
2018-12-24 19:00 | 40
2018-12-24 20:00 | 39
2018-12-24 21:00 | 39
2018-12-24 22:00 | 38
2018-12-24 23:00 | 38
2018-12-25 | 37
2018-12-25 01:00 | 37
2018-12-25 02:00 | 36
2018-12-25 03:00 | 36
2018-12-25 04:00 | 35
2018-12-25 05:00 | 35
2018-12-25 06:00 | 35
2018-12-25 07:00 | 35
2018-12-25 08:00 | 35
2018-12-25 09:00 | 36
2018-12-25 10:00 | 38
2018-12-25 11:00 | 39
2018-12-25 12:00 | 39
2018-12-25 13:00 | 40
2018-12-25 14:00 | 40
2018-12-25 15:00 | 40
2018-12-25 16:00 | 39
2018-12-25 17:00 | 37
2018-12-25 18:00 | 37
2018-12-25 19:00 | 37
2018-12-25 20:00 | 37
2018-12-25 21:00 | 36
2018-12-25 22:00 | 35
2018-12-25 23:00 | 35
2018-12-26 | 34
2018-12-26 01:00 | 34
2018-12-26 02:00 | 34
2018-12-26 03:00 | 33
2018-12-26 04:00 | 33
2018-12-26 05:00 | 34
2018-12-26 06:00 | 34
2018-12-26 07:00 | 35
2018-12-26 08:00 | 35
2018-12-26 09:00 | 36
2018-12-26 10:00 | 38
2018-12-26 11:00 | 38
2018-12-26 12:00 | 39
2018-12-26 13:00 | 41
2018-12-26 14:00 | 41
2018-12-26 15:00 | 43
2018-12-26 16:00 | 43
2018-12-26 17:00 | 43
2018-12-26 18:00 | 43
2018-12-26 19:00 | 42
2018-12-26 20:00 | 43
2018-12-26 21:00 | 41
2018-12-26 22:00 | 40
2018-12-26 23:00 | 41
2018-12-27 | 42
2018-12-27 01:00 | 42
2018-12-27 02:00 | 43
2018-12-27 03:00 | 41
2018-12-27 04:00 | 41
2018-12-27 05:00 | 41
2018-12-27 06:00 | 39
2018-12-27 07:00 | 39
2018-12-27 08:00 | 39
2018-12-27 09:00 | 39
2018-12-27 10:00 | 41
2018-12-27 11:00 | 41
2018-12-27 12:00 | 41
2018-12-27 13:00 | 42
2018-12-27 14:00 | 43
2018-12-27 15:00 | 43
2018-12-27 16:00 | 42
2018-12-27 17:00 | 39
2018-12-27 18:00 | 39
2018-12-27 19:00 | 40
2018-12-27 20:00 | 39
2018-12-27 21:00 | 39
2018-12-27 22:00 | 40
2018-12-27 23:00 | 41
2018-12-28 | 43
2018-12-28 01:00 | 44
2018-12-28 02:00 | 45
2018-12-28 03:00 | 45
2018-12-28 04:00 | 44
2018-12-28 05:00 | 45
2018-12-28 06:00 | 45
2018-12-28 07:00 | 46
2018-12-28 08:00 | 46
2018-12-28 09:00 | 48
2018-12-28 10:00 | 53
2018-12-28 11:00 | 52
2018-12-28 12:00 | 52
2018-12-28 13:00 | 53
2018-12-28 14:00 | 54
2018-12-28 15:00 | 54
2018-12-28 16:00 | 53
2018-12-28 17:00 | 54
2018-12-28 18:00 | 55
2018-12-28 19:00 | 58
2018-12-28 20:00 | 57
2018-12-28 21:00 | 57
2018-12-28 22:00 | 58
2018-12-28 23:00 | 57
2018-12-29 | 56
2018-12-29 01:00 | 56
2018-12-29 02:00 | 55
2018-12-29 03:00 | 54
2018-12-29 04:00 | 54
2018-12-29 05:00 | 55
2018-12-29 06:00 | 55
2018-12-29 07:00 | 54
2018-12-29 08:00 | 52
2018-12-29 09:00 | 52
2018-12-29 10:00 | 50
2018-12-29 11:00 | 48
2018-12-29 12:00 | 46
2018-12-29 13:00 | 48
2018-12-29 14:00 | 46
2018-12-29 15:00 | 46
2018-12-29 16:00 | 47
2018-12-29 17:00 | 46
2018-12-29 18:00 | 45
2018-12-29 19:00 | 44
2018-12-29 20:00 | 43
2018-12-29 21:00 | 43
2018-12-29 22:00 | 41
2018-12-29 23:00 | 39
2018-12-30 | 40
2018-12-30 01:00 | 39
2018-12-30 02:00 | 37
2018-12-30 03:00 | 37
2018-12-30 04:00 | 36
2018-12-30 05:00 | 36
2018-12-30 06:00 | 36
2018-12-30 07:00 | 35
2018-12-30 08:00 | 36
2018-12-30 09:00 | 34
2018-12-30 10:00 | 33
2018-12-30 11:00 | 34
2018-12-30 12:00 | 34
2018-12-30 13:00 | 35
2018-12-30 14:00 | 37
2018-12-30 15:00 | 38
2018-12-30 16:00 | 38
2018-12-30 17:00 | 38
2018-12-30 18:00 | 38
2018-12-30 19:00 | 38
2018-12-30 20:00 | 39
2018-12-30 21:00 | 39
2018-12-30 22:00 | 39
2018-12-30 23:00 | 39
2018-12-31 | 39
2018-12-31 01:00 | 40
2018-12-31 02:00 | 39
2018-12-31 03:00 | 39
2018-12-31 04:00 | 38
2018-12-31 05:00 | 37
2018-12-31 06:00 | 36
2018-12-31 07:00 | 36
2018-12-31 08:00 | 37
2018-12-31 09:00 | 38
2018-12-31 10:00 | 42
2018-12-31 11:00 | 45
2018-12-31 12:00 | 45
2018-12-31 13:00 | 45
2018-12-31 14:00 | 45
2018-12-31 15:00 | 45
2018-12-31 16:00 | 44
2018-12-31 17:00 | 45
2018-12-31 18:00 | 45
2018-12-31 19:00 | 44
2018-12-31 20:00 | 45
2018-12-31 21:00 | 45
2018-12-31 22:00 | 46
2018-12-31 23:00 | 46

## Step 2. Aggregate Data
Supply Fan Datetime | Supply Fan RMS Power (kW) | Supply Fan OAT (F) | Return Fan Datetime | Return Fan RMS Power (kW) | Return Fan OAT (F) | Supply Fan |  |  |  |  | Return Fan
2022-03-11 09:00 | 12.0351 | 44 | 2022-03-11 09:00 | 4.0959 | 44 |  |  |  | Sorted | 403 |  |  |  | Sorted |  | 352
2022-03-11 10:00 | 12.0351 | 46 | 2022-03-11 10:00 | 4.0959 | 46 | Date-Time | true RMS power (kW) | OAT (F) |  |  | Date-Time | true RMS power (kW) | OAT (F) | Date-Time | true RMS power (kW) | OAT (F)
2022-03-11 11:00 | 12.0351 | 49 | 2022-03-11 11:00 | 4.0959 | 49 | 2022-03-11 09:00 | 12.0351 | 49 |  |  | 2022-03-11 09:00 | 4.0959 | 49 | 2022-03-11 09:00 | 4.0959 | 49
2022-03-11 12:00 | 12.0351 | 49 | 2022-03-11 12:00 | 4.0959 | 49 | 2022-03-11 10:00 | 12.0351 | 49 |  |  | 2022-03-11 10:00 | 4.0959 | 49 | 2022-03-11 10:00 | 4.0959 | 49
2022-03-11 13:00 | 12.0351 | 48 | 2022-03-11 13:00 | 4.0959 | 48 | 2022-03-11 11:00 | 12.0351 | 49 |  |  | 2022-03-11 11:00 | 4.0959 | 49 | 2022-03-11 11:00 | 4.0959 | 49
2022-03-11 14:00 | 12.0351 | 48 | 2022-03-11 14:00 | 4.0959 | 48 | 2022-03-11 12:00 | 12.0351 | 49 |  |  | 2022-03-11 12:00 | 4.0959 | 49 | 2022-03-11 12:00 | 4.0959 | 49
2022-03-11 15:00 | 12.0351 | 48 | 2022-03-11 15:00 | 4.0959 | 48 | 2022-03-11 13:00 | 12.0351 | 49 |  |  | 2022-03-11 13:00 | 4.0959 | 49 | 2022-03-11 13:00 | 4.0959 | 49
2022-03-11 16:00 | 12.0351 | 46 | 2022-03-11 16:00 | 4.0959 | 46 | 2022-03-11 14:00 | 12.0351 | 50 |  |  | 2022-03-11 14:00 | 4.0959 | 50 | 2022-03-11 14:00 | 4.0959 | 50
2022-03-11 17:00 | 12.0351 | 45 | 2022-03-11 17:00 | 4.0959 | 45 | 2022-03-11 15:00 | 12.0351 | 50 |  |  | 2022-03-11 15:00 | 4.0959 | 50 | 2022-03-11 15:00 | 4.0959 | 50
2022-03-11 18:00 | 12.0351 | 43 | 2022-03-11 18:00 | 4.0959 | 43 | 2022-03-11 16:00 | 12.0351 | 50 |  |  | 2022-03-11 16:00 | 4.0959 | 50 | 2022-03-11 16:00 | 4.0959 | 50
2022-03-11 19:00 | 6.2229 | 42 | 2022-03-11 19:00 | 4.0959 | 42 | 2022-03-11 17:00 | 12.0351 | 51 |  |  | 2022-03-11 17:00 | 4.0959 | 51 | 2022-03-11 17:00 | 4.0959 | 51
2022-03-11 20:00 | 4.8652 | 43 | 2022-03-11 20:00 | 2.9296 | 43 | 2022-03-11 18:00 | 12.0351 | 51 |  |  | 2022-03-11 18:00 | 4.0959 | 51 | 2022-03-11 18:00 | 4.0959 | 51
2022-03-11 21:00 | 4.8438 | 44 | 2022-03-11 21:00 | 2.9127 | 44 | 2022-03-11 19:00 | 6.2229 | 50 |  |  | 2022-03-11 19:00 | 4.0959 | 50 | 2022-03-11 19:00 | 4.0959 | 50
2022-03-11 22:00 | 4.8389 | 45 | 2022-03-11 22:00 | 2.9089 | 45 | 2022-03-11 20:00 | 4.8652 | 50 |  |  | 2022-03-11 20:00 | 2.9296 | 50 | 2022-03-14 05:00 | 4.0959 | 26
2022-03-11 23:00 | 4.8331 | 45 | 2022-03-11 23:00 | 2.9044 | 45 | 2022-03-11 21:00 | 4.8438 | 51 |  |  | 2022-03-11 21:00 | 2.9127 | 51 | 2022-03-14 06:00 | 4.0959 | 25
2022-03-12 | 4.7958 | 45 | 2022-03-12 | 2.8768 | 45 | 2022-03-11 22:00 | 4.8389 | 51 |  |  | 2022-03-11 22:00 | 2.9089 | 51 | 2022-03-14 07:00 | 4.0959 | 24
2022-03-12 01:00 | 4.8291 | 46 | 2022-03-12 01:00 | 2.9014 | 46 | 2022-03-11 23:00 | 4.8331 | 52 |  |  | 2022-03-11 23:00 | 2.9044 | 52 | 2022-03-14 08:00 | 4.0959 | 23
2022-03-12 02:00 | 4.8662 | 44 | 2022-03-12 02:00 | 2.9304 | 44 | 2022-03-12 | 4.7958 | 53 |  |  | 2022-03-12 | 2.8768 | 53 | 2022-03-14 09:00 | 4.0959 | 22
2022-03-12 03:00 | 4.9003 | 45 | 2022-03-12 03:00 | 2.9586 | 45 | 2022-03-12 01:00 | 4.8291 | 52 |  |  | 2022-03-12 01:00 | 2.9014 | 52 | 2022-03-14 10:00 | 4.0959 | 22
2022-03-12 04:00 | 4.8983 | 45 | 2022-03-12 04:00 | 2.9569 | 45 | 2022-03-12 02:00 | 4.8662 | 51 |  |  | 2022-03-12 02:00 | 2.9304 | 51 | 2022-03-14 11:00 | 4.0959 | 22
2022-03-12 05:00 | 4.8983 | 45 | 2022-03-12 05:00 | 2.9569 | 45 | 2022-03-12 03:00 | 4.9003 | 52 |  |  | 2022-03-12 03:00 | 2.9586 | 52 | 2022-03-14 12:00 | 4.0959 | 21
2022-03-12 06:00 | 4.906 | 45 | 2022-03-12 06:00 | 2.9635 | 45 | 2022-03-12 04:00 | 4.8983 | 51 |  |  | 2022-03-12 04:00 | 2.9569 | 51 | 2022-03-14 13:00 | 4.0959 | 21
2022-03-12 07:00 | 4.8954 | 45 | 2022-03-12 07:00 | 2.9545 | 45 | 2022-03-12 05:00 | 4.8983 | 52 |  |  | 2022-03-12 05:00 | 2.9569 | 52 | 2022-03-14 14:00 | 4.0959 | 20
2022-03-12 08:00 | 4.8964 | 45 | 2022-03-12 08:00 | 2.9553 | 45 | 2022-03-12 06:00 | 4.906 | 52 |  |  | 2022-03-12 06:00 | 2.9635 | 52 | 2022-03-14 15:00 | 4.0959 | 20
2022-03-12 09:00 | 4.8643 | 46 | 2022-03-12 09:00 | 2.9288 | 46 | 2022-03-12 07:00 | 4.8954 | 52 |  |  | 2022-03-12 07:00 | 2.9545 | 52 | 2022-03-14 16:00 | 4.0959 | 20
2022-03-12 10:00 | 4.908 | 45 | 2022-03-12 10:00 | 2.9652 | 45 | 2022-03-12 08:00 | 4.8964 | 53 |  |  | 2022-03-12 08:00 | 2.9553 | 53 | 2022-03-14 17:00 | 4.0959 | 20
2022-03-12 11:00 | 4.8604 | 36 | 2022-03-12 11:00 | 2.9257 | 36 | 2022-03-12 09:00 | 4.8643 | 53 |  |  | 2022-03-12 09:00 | 2.9288 | 53 | 2022-03-14 18:00 | 4.0959 | 23
2022-03-12 12:00 | 4.8007 | 35 | 2022-03-12 12:00 | 2.8803 | 35 | 2022-03-12 10:00 | 4.908 | 53 |  |  | 2022-03-12 10:00 | 2.9652 | 53 | 2022-03-15 06:00 | 4.0959 | 32
2022-03-12 13:00 | 4.8164 | 33 | 2022-03-12 13:00 | 2.8918 | 33 | 2022-03-12 11:00 | 4.8604 | 53 |  |  | 2022-03-12 11:00 | 2.9257 | 53 | 2022-03-15 07:00 | 4.0959 | 32
2022-03-12 14:00 | 4.832 | 32 | 2022-03-12 14:00 | 2.9036 | 32 | 2022-03-12 12:00 | 4.8007 | 53 |  |  | 2022-03-12 12:00 | 2.8803 | 53 | 2022-03-15 08:00 | 4.0959 | 31
2022-03-12 15:00 | 4.8379 | 32 | 2022-03-12 15:00 | 2.9081 | 32 | 2022-03-12 13:00 | 4.8164 | 51 |  |  | 2022-03-12 13:00 | 2.8918 | 51 | 2022-03-15 09:00 | 4.0959 | 32
2022-03-12 16:00 | 4.8457 | 31 | 2022-03-12 16:00 | 2.9142 | 31 | 2022-03-12 14:00 | 4.832 | 52 |  |  | 2022-03-12 14:00 | 2.9036 | 52 | 2022-03-15 10:00 | 4.0959 | 32
2022-03-12 17:00 | 4.8428 | 27 | 2022-03-12 17:00 | 2.9119 | 27 | 2022-03-12 15:00 | 4.8379 | 52 |  |  | 2022-03-12 15:00 | 2.9081 | 52 | 2022-03-15 11:00 | 4.0959 | 30
2022-03-12 18:00 | 4.9022 | 24 | 2022-03-12 18:00 | 2.9602 | 24 | 2022-03-12 16:00 | 4.8457 | 51 |  |  | 2022-03-12 16:00 | 2.9142 | 51 | 2022-03-15 12:00 | 4.0959 | 32
2022-03-12 19:00 | 4.9408 | 26 | 2022-03-12 19:00 | 2.9943 | 26 | 2022-03-12 17:00 | 4.8428 | 51 |  |  | 2022-03-12 17:00 | 2.9119 | 51 | 2022-03-15 13:00 | 4.0959 | 34
2022-03-12 20:00 | 4.9225 | 27 | 2022-03-12 20:00 | 2.9779 | 27 | 2022-03-12 18:00 | 4.9022 | 52 |  |  | 2022-03-12 18:00 | 2.9602 | 52 | 2022-03-15 14:00 | 4.0959 | 34
2022-03-12 21:00 | 4.9031 | 26 | 2022-03-12 21:00 | 2.961 | 26 | 2022-03-12 19:00 | 4.9408 | 52 |  |  | 2022-03-12 19:00 | 2.9943 | 52 | 2022-03-15 15:00 | 4.0959 | 34
2022-03-12 22:00 | 4.9486 | 26 | 2022-03-12 22:00 | 3.0014 | 26 | 2022-03-12 20:00 | 4.9225 | 53 |  |  | 2022-03-12 20:00 | 2.9779 | 53 | 2022-03-15 16:00 | 4.0959 | 34
2022-03-12 23:00 | 4.9303 | 25 | 2022-03-12 23:00 | 2.9848 | 25 | 2022-03-12 21:00 | 4.9031 | 53 |  |  | 2022-03-12 21:00 | 2.961 | 53 | 2022-03-15 17:00 | 4.0959 | 35
2022-03-13 | 4.9283 | 24 | 2022-03-13 | 2.983 | 24 | 2022-03-12 22:00 | 4.9486 | 54 |  |  | 2022-03-12 22:00 | 3.0014 | 54 | 2022-03-16 06:00 | 4.0959 | 43
2022-03-13 01:00 | 4.9755 | 23 | 2022-03-13 01:00 | 3.0267 | 23 | 2022-03-12 23:00 | 4.9303 | 57 |  |  | 2022-03-12 23:00 | 2.9848 | 57 | 2022-03-16 07:00 | 4.0959 | 42
2022-03-13 02:00 | 4.9745 | 23 | 2022-03-13 02:00 | 3.0257 | 23 | 2022-03-13 | 4.9283 | 58 |  |  | 2022-03-13 | 2.983 | 58 | 2022-03-16 08:00 | 4.0959 | 42
2022-03-13 03:00 | 5.0215 | 23 | 2022-03-13 03:00 | 3.0725 | 23 | 2022-03-13 01:00 | 4.9755 | 53 |  |  | 2022-03-13 01:00 | 3.0267 | 53 | 2022-03-16 09:00 | 4.0959 | 41
2022-03-13 04:00 | 5.0224 | 23 | 2022-03-13 04:00 | 3.0734 | 23 | 2022-03-13 02:00 | 4.9745 | 50 |  |  | 2022-03-13 02:00 | 3.0257 | 50 | 2022-03-16 10:00 | 4.0959 | 40
2022-03-13 05:00 | 5.0424 | 23 | 2022-03-13 05:00 | 3.0945 | 23 | 2022-03-13 03:00 | 5.0215 | 50 |  |  | 2022-03-13 03:00 | 3.0725 | 50 | 2022-03-16 11:00 | 4.0959 | 39
2022-03-13 06:00 | 5.0138 | 23 | 2022-03-13 06:00 | 3.0646 | 23 | 2022-03-13 04:00 | 5.0224 | 48 |  |  | 2022-03-13 04:00 | 3.0734 | 48 | 2022-03-16 12:00 | 4.0959 | 38
2022-03-13 07:00 | 5.0596 | 23 | 2022-03-13 07:00 | 3.1131 | 23 | 2022-03-13 05:00 | 5.0424 | 44 |  |  | 2022-03-13 05:00 | 3.0945 | 44 | 2022-03-16 13:00 | 4.0959 | 36
2022-03-13 08:00 | 5.1304 | 24 | 2022-03-13 08:00 | 3.1956 | 24 | 2022-03-13 06:00 | 5.0138 | 40 |  |  | 2022-03-13 06:00 | 3.0646 | 40 | 2022-03-16 14:00 | 4.0959 | 35
2022-03-13 09:00 | 5.0785 | 26 | 2022-03-13 09:00 | 3.1343 | 26 | 2022-03-13 07:00 | 5.0596 | 39 |  |  | 2022-03-13 07:00 | 3.1131 | 39 | 2022-03-16 15:00 | 4.0959 | 37
2022-03-13 10:00 | 5.0794 | 28 | 2022-03-13 10:00 | 3.1353 | 28 | 2022-03-13 08:00 | 5.1304 | 39 |  |  | 2022-03-13 08:00 | 3.1956 | 39 | 2022-03-16 16:00 | 4.0959 | 39
2022-03-13 11:00 | 5.087 | 30 | 2022-03-13 11:00 | 3.144 | 30 | 2022-03-13 09:00 | 5.0785 | 39 |  |  | 2022-03-13 09:00 | 3.1343 | 39 | 2022-03-16 17:00 | 4.0959 | 38
2022-03-13 12:00 | 5.0243 | 32 | 2022-03-13 12:00 | 3.0754 | 32 | 2022-03-13 10:00 | 5.0794 | 38 |  |  | 2022-03-13 10:00 | 3.1353 | 38 | 2022-03-17 06:00 | 4.0959 | 35
2022-03-13 13:00 | 4.9697 | 32 | 2022-03-13 13:00 | 3.0211 | 32 | 2022-03-13 11:00 | 5.087 | 38 |  |  | 2022-03-13 11:00 | 3.144 | 38 | 2022-03-17 07:00 | 4.0959 | 35
2022-03-13 14:00 | 4.9621 | 33 | 2022-03-13 14:00 | 3.0139 | 33 | 2022-03-13 12:00 | 5.0243 | 37 |  |  | 2022-03-13 12:00 | 3.0754 | 37 | 2022-03-17 08:00 | 4.0959 | 34
2022-03-13 15:00 | 4.9573 | 34 | 2022-03-13 15:00 | 3.0094 | 34 | 2022-03-13 13:00 | 4.9697 | 35 |  |  | 2022-03-13 13:00 | 3.0211 | 35 | 2022-03-17 09:00 | 4.0959 | 35
2022-03-13 16:00 | 4.9582 | 35 | 2022-03-13 16:00 | 3.0103 | 35 | 2022-03-13 14:00 | 4.9621 | 34 |  |  | 2022-03-13 14:00 | 3.0139 | 34 | 2022-03-17 10:00 | 4.0959 | 34
2022-03-13 17:00 | 4.9659 | 34 | 2022-03-13 17:00 | 3.0175 | 34 | 2022-03-13 15:00 | 4.9573 | 33 |  |  | 2022-03-13 15:00 | 3.0094 | 33 | 2022-03-17 11:00 | 4.0959 | 32
2022-03-13 18:00 | 4.9745 | 34 | 2022-03-13 18:00 | 3.0257 | 34 | 2022-03-13 16:00 | 4.9582 | 32 |  |  | 2022-03-13 16:00 | 3.0103 | 32 | 2022-03-17 12:00 | 4.0959 | 30
2022-03-13 19:00 | 4.9899 | 32 | 2022-03-13 19:00 | 3.0407 | 32 | 2022-03-13 17:00 | 4.9659 | 31 |  |  | 2022-03-13 17:00 | 3.0175 | 31 | 2022-03-17 13:00 | 4.0959 | 30
2022-03-13 20:00 | 5.0138 | 28 | 2022-03-13 20:00 | 3.0646 | 28 | 2022-03-13 18:00 | 4.9745 | 31 |  |  | 2022-03-13 18:00 | 3.0257 | 31 | 2022-03-17 14:00 | 4.0959 | 30
2022-03-13 21:00 | 5.0081 | 30 | 2022-03-13 21:00 | 3.0588 | 30 | 2022-03-13 19:00 | 4.9899 | 30 |  |  | 2022-03-13 19:00 | 3.0407 | 30 | 2022-03-17 15:00 | 4.0959 | 29
2022-03-13 22:00 | 4.9745 | 31 | 2022-03-13 22:00 | 3.0257 | 31 | 2022-03-13 20:00 | 5.0138 | 30 |  |  | 2022-03-13 20:00 | 3.0646 | 30 | 2022-03-17 16:00 | 4.0959 | 29
2022-03-13 23:00 | 5.0434 | 31 | 2022-03-13 23:00 | 3.0955 | 31 | 2022-03-13 21:00 | 5.0081 | 29 |  |  | 2022-03-13 21:00 | 3.0588 | 29 | 2022-03-17 17:00 | 4.0959 | 29
2022-03-14 | 5.0282 | 32 | 2022-03-14 | 3.0794 | 32 | 2022-03-13 22:00 | 4.9745 | 29 |  |  | 2022-03-13 22:00 | 3.0257 | 29 | 2022-03-18 06:00 | 4.0959 | 27
2022-03-14 01:00 | 5.0879 | 34 | 2022-03-14 01:00 | 3.145 | 34 | 2022-03-13 23:00 | 5.0434 | 30 |  |  | 2022-03-13 23:00 | 3.0955 | 30 | 2022-03-18 07:00 | 4.0959 | 27
2022-03-14 02:00 | 5.0917 | 36 | 2022-03-14 02:00 | 3.1494 | 36 | 2022-03-14 | 5.0282 | 29 |  |  | 2022-03-14 | 3.0794 | 29 | 2022-03-18 08:00 | 4.0959 | 26
2022-03-14 03:00 | 5.0596 | 36 | 2022-03-14 03:00 | 3.1131 | 36 | 2022-03-14 01:00 | 5.0879 | 29 |  |  | 2022-03-14 01:00 | 3.145 | 29 | 2022-03-18 09:00 | 4.0959 | 26
2022-03-14 04:00 | 5.0538 | 37 | 2022-03-14 04:00 | 3.1068 | 37 | 2022-03-14 02:00 | 5.0917 | 27 |  |  | 2022-03-14 02:00 | 3.1494 | 27 | 2022-03-18 10:00 | 4.0959 | 25
2022-03-14 05:00 | 6.4743 | 37 | 2022-03-14 05:00 | 4.0959 | 37 | 2022-03-14 03:00 | 5.0596 | 27 |  |  | 2022-03-14 03:00 | 3.1131 | 27 | 2022-03-18 11:00 | 4.0959 | 24
2022-03-14 06:00 | 12.0351 | 37 | 2022-03-14 06:00 | 4.0959 | 37 | 2022-03-14 04:00 | 5.0538 | 27 |  |  | 2022-03-14 04:00 | 3.1068 | 27 | 2022-03-18 12:00 | 4.0959 | 23
2022-03-14 07:00 | 12.0351 | 37 | 2022-03-14 07:00 | 4.0959 | 37 | 2022-03-14 05:00 | 6.4743 | 26 |  |  | 2022-03-14 05:00 | 4.0959 | 26 | 2022-03-18 13:00 | 4.0959 | 22
2022-03-14 08:00 | 12.0351 | 37 | 2022-03-14 08:00 | 4.0959 | 37 | 2022-03-14 06:00 | 12.0351 | 25 |  |  | 2022-03-14 06:00 | 4.0959 | 25 | 2022-03-18 14:00 | 4.0959 | 22
2022-03-14 09:00 | 12.0351 | 41 | 2022-03-14 09:00 | 4.0959 | 41 | 2022-03-14 07:00 | 12.0351 | 24 |  |  | 2022-03-14 07:00 | 4.0959 | 24 | 2022-03-18 15:00 | 4.0959 | 22
2022-03-14 10:00 | 12.0351 | 45 | 2022-03-14 10:00 | 4.0959 | 45 | 2022-03-14 08:00 | 12.0351 | 23 |  |  | 2022-03-14 08:00 | 4.0959 | 23 | 2022-03-18 16:00 | 4.0959 | 21
2022-03-14 11:00 | 12.0351 | 47 | 2022-03-14 11:00 | 4.0959 | 47 | 2022-03-14 09:00 | 12.0351 | 22 |  |  | 2022-03-14 09:00 | 4.0959 | 22 | 2022-03-18 17:00 | 4.0959 | 21
2022-03-14 12:00 | 12.0351 | 51 | 2022-03-14 12:00 | 4.0959 | 51 | 2022-03-14 10:00 | 12.0351 | 22 |  |  | 2022-03-14 10:00 | 4.0959 | 22 | 2022-03-18 18:00 | 4.0959 | 22
2022-03-14 13:00 | 12.0351 | 53 | 2022-03-14 13:00 | 4.0959 | 53 | 2022-03-14 11:00 | 12.0351 | 22 |  |  | 2022-03-14 11:00 | 4.0959 | 22 | 2022-03-21 05:00 | 4.0959 | 0
2022-03-14 14:00 | 12.0351 | 54 | 2022-03-14 14:00 | 4.0959 | 54 | 2022-03-14 12:00 | 12.0351 | 21 |  |  | 2022-03-14 12:00 | 4.0959 | 21 | 2022-03-21 06:00 | 4.0959 | 0
2022-03-14 15:00 | 12.0351 | 52 | 2022-03-14 15:00 | 4.0959 | 52 | 2022-03-14 13:00 | 12.0351 | 21 |  |  | 2022-03-14 13:00 | 4.0959 | 21 | 2022-03-21 07:00 | 4.0959 | 0
2022-03-14 16:00 | 12.0351 | 50 | 2022-03-14 16:00 | 4.0959 | 50 | 2022-03-14 14:00 | 12.0351 | 20 |  |  | 2022-03-14 14:00 | 4.0959 | 20 | 2022-03-21 08:00 | 4.0959 | 0
2022-03-14 17:00 | 12.0351 | 48 | 2022-03-14 17:00 | 4.0959 | 48 | 2022-03-14 15:00 | 12.0351 | 20 |  |  | 2022-03-14 15:00 | 4.0959 | 20 | 2022-03-21 09:00 | 4.0959 | 0
2022-03-14 18:00 | 12.0351 | 47 | 2022-03-14 18:00 | 4.0959 | 47 | 2022-03-14 16:00 | 12.0351 | 20 |  |  | 2022-03-14 16:00 | 4.0959 | 20 | 2022-03-21 10:00 | 4.0959 | 0
2022-03-14 19:00 | 4.8808 | 45 | 2022-03-14 19:00 | 2.9423 | 45 | 2022-03-14 17:00 | 12.0351 | 20 |  |  | 2022-03-14 17:00 | 4.0959 | 20 | 2022-03-21 11:00 | 4.0959 | 0
2022-03-14 20:00 | 4.834 | 45 | 2022-03-14 20:00 | 2.9051 | 45 | 2022-03-14 18:00 | 12.0351 | 23 |  |  | 2022-03-14 18:00 | 4.0959 | 23 | 2022-03-21 12:00 | 4.0959 | 0
2022-03-14 21:00 | 4.8457 | 45 | 2022-03-14 21:00 | 2.9142 | 45 | 2022-03-14 19:00 | 4.8808 | 25 |  |  | 2022-03-14 19:00 | 2.9423 | 25 | 2022-03-21 13:00 | 4.0959 | 0
2022-03-14 22:00 | 4.873 | 47 | 2022-03-14 22:00 | 2.9359 | 47 | 2022-03-14 20:00 | 4.834 | 28 |  |  | 2022-03-14 20:00 | 2.9051 | 28 | 2022-03-21 14:00 | 4.0959 | 0
2022-03-14 23:00 | 4.9899 | 46 | 2022-03-14 23:00 | 3.0407 | 46 | 2022-03-14 21:00 | 4.8457 | 29 |  |  | 2022-03-14 21:00 | 2.9142 | 29 | 2022-03-21 15:00 | 4.0959 | 0
2022-03-15 | 5.0004 | 45 | 2022-03-15 | 3.0511 | 45 | 2022-03-14 22:00 | 4.873 | 31 |  |  | 2022-03-14 22:00 | 2.9359 | 31 | 2022-03-21 16:00 | 4.0959 | 0
2022-03-15 01:00 | 5.0424 | 44 | 2022-03-15 01:00 | 3.0945 | 44 | 2022-03-14 23:00 | 4.9899 | 32 |  |  | 2022-03-14 23:00 | 3.0407 | 32 | 2022-03-21 17:00 | 4.0959 | 0
2022-03-15 02:00 | 5.0596 | 44 | 2022-03-15 02:00 | 3.1131 | 44 | 2022-03-15 | 5.0004 | 32 |  |  | 2022-03-15 | 3.0511 | 32 | 2022-03-22 06:00 | 4.0959 | 0
2022-03-15 03:00 | 5.0908 | 43 | 2022-03-15 03:00 | 3.1483 | 43 | 2022-03-15 01:00 | 5.0424 | 32 |  |  | 2022-03-15 01:00 | 3.0945 | 32 | 2022-03-22 07:00 | 4.0959 | 0
2022-03-15 04:00 | 5.0794 | 42 | 2022-03-15 04:00 | 3.1353 | 42 | 2022-03-15 02:00 | 5.0596 | 29 |  |  | 2022-03-15 02:00 | 3.1131 | 29 | 2022-03-22 08:00 | 4.0959 | 0
2022-03-15 05:00 | 5.1191 | 40 | 2022-03-15 05:00 | 3.1818 | 40 | 2022-03-15 03:00 | 5.0908 | 31 |  |  | 2022-03-15 03:00 | 3.1483 | 31 | 2022-03-22 09:00 | 4.0959 | 0
2022-03-15 06:00 | 12.0351 | 40 | 2022-03-15 06:00 | 4.0959 | 40 | 2022-03-15 04:00 | 5.0794 | 32 |  |  | 2022-03-15 04:00 | 3.1353 | 32 | 2022-03-22 10:00 | 4.0959 | 0
2022-03-15 07:00 | 12.0351 | 40 | 2022-03-15 07:00 | 4.0959 | 40 | 2022-03-15 05:00 | 5.1191 | 32 |  |  | 2022-03-15 05:00 | 3.1818 | 32 | 2022-03-22 11:00 | 4.0959 | 0
2022-03-15 08:00 | 12.0351 | 42 | 2022-03-15 08:00 | 4.0959 | 42 | 2022-03-15 06:00 | 12.0351 | 32 |  |  | 2022-03-15 06:00 | 4.0959 | 32 | 2022-03-22 12:00 | 4.0959 | 0
2022-03-15 09:00 | 12.0351 | 46 | 2022-03-15 09:00 | 4.0959 | 46 | 2022-03-15 07:00 | 12.0351 | 32 |  |  | 2022-03-15 07:00 | 4.0959 | 32 | 2022-03-22 13:00 | 4.0959 | 0
2022-03-15 10:00 | 12.0351 | 49 | 2022-03-15 10:00 | 4.0959 | 49 | 2022-03-15 08:00 | 12.0351 | 31 |  |  | 2022-03-15 08:00 | 4.0959 | 31 | 2022-03-22 14:00 | 4.0959 | 0
2022-03-15 11:00 | 12.0351 | 50 | 2022-03-15 11:00 | 4.0959 | 50 | 2022-03-15 09:00 | 12.0351 | 32 |  |  | 2022-03-15 09:00 | 4.0959 | 32 | 2022-03-22 15:00 | 4.0959 | 0
2022-03-15 12:00 | 12.0351 | 52 | 2022-03-15 12:00 | 4.0959 | 52 | 2022-03-15 10:00 | 12.0351 | 32 |  |  | 2022-03-15 10:00 | 4.0959 | 32 | 2022-03-22 16:00 | 4.0959 | 0
2022-03-15 13:00 | 12.0351 | 55 | 2022-03-15 13:00 | 4.0959 | 55 | 2022-03-15 11:00 | 12.0351 | 30 |  |  | 2022-03-15 11:00 | 4.0959 | 30 | 2022-03-22 17:00 | 4.0959 | 0
2022-03-15 14:00 | 12.0351 | 56 | 2022-03-15 14:00 | 4.0959 | 56 | 2022-03-15 12:00 | 12.0351 | 32 |  |  | 2022-03-15 12:00 | 4.0959 | 32 | 2022-03-23 06:00 | 4.0959 | 0
2022-03-15 15:00 | 12.0351 | 55 | 2022-03-15 15:00 | 4.0959 | 55 | 2022-03-15 13:00 | 12.0351 | 34 |  |  | 2022-03-15 13:00 | 4.0959 | 34 | 2022-03-23 07:00 | 4.0959 | 0
2022-03-15 16:00 | 12.0351 | 54 | 2022-03-15 16:00 | 4.0959 | 54 | 2022-03-15 14:00 | 12.0351 | 34 |  |  | 2022-03-15 14:00 | 4.0959 | 34 | 2022-03-23 08:00 | 4.0959 | 0
2022-03-15 17:00 | 12.0351 | 53 | 2022-03-15 17:00 | 4.0959 | 53 | 2022-03-15 15:00 | 12.0351 | 34 |  |  | 2022-03-15 15:00 | 4.0959 | 34 | 2022-03-23 09:00 | 4.0959 | 0
2022-03-15 18:00 | 0.87619 | 51 | 2022-03-15 18:00 | 0.80309 | 51 | 2022-03-15 16:00 | 12.0351 | 34 |  |  | 2022-03-15 16:00 | 4.0959 | 34 | 2022-03-23 10:00 | 4.0959 | 0
2022-03-15 19:00 | 0.91252 | 48 | 2022-03-15 19:00 | 0.84074 | 48 | 2022-03-15 17:00 | 12.0351 | 35 |  |  | 2022-03-15 17:00 | 4.0959 | 35 | 2022-03-23 11:00 | 4.0959 | 0
2022-03-15 20:00 | 0.90861 | 48 | 2022-03-15 20:00 | 0.83667 | 48 | 2022-03-15 18:00 | 0.87619 | 37 |  |  | 2022-03-15 18:00 | 0.80309 | 37 | 2022-03-23 12:00 | 4.0959 | 0
2022-03-15 21:00 | 0.89784 | 48 | 2022-03-15 21:00 | 0.82546 | 48 | 2022-03-15 19:00 | 0.91252 | 39 |  |  | 2022-03-15 19:00 | 0.84074 | 39 | 2022-03-23 13:00 | 4.0959 | 0
2022-03-15 22:00 | 0.89096 | 51 | 2022-03-15 22:00 | 0.81833 | 51 | 2022-03-15 20:00 | 0.90861 | 40 |  |  | 2022-03-15 20:00 | 0.83667 | 40 | 2022-03-23 14:00 | 4.0959 | 0
2022-03-15 23:00 | 0.88606 | 58 | 2022-03-15 23:00 | 0.81327 | 58 | 2022-03-15 21:00 | 0.89784 | 40 |  |  | 2022-03-15 21:00 | 0.82546 | 40 | 2022-03-23 15:00 | 4.0959 | 0
2022-03-16 | 0.9047 | 51 | 2022-03-16 | 0.8326 | 51 | 2022-03-15 22:00 | 0.89096 | 41 |  |  | 2022-03-15 22:00 | 0.81833 | 41 | 2022-03-23 16:00 | 4.0959 | 0
2022-03-16 01:00 | 0.92325 | 50 | 2022-03-16 01:00 | 0.85197 | 50 | 2022-03-15 23:00 | 0.88606 | 43 |  |  | 2022-03-15 23:00 | 0.81327 | 43 | 2022-03-23 17:00 | 4.0959 | 0
2022-03-16 02:00 | 0.90567 | 50 | 2022-03-16 02:00 | 0.8336 | 50 | 2022-03-16 | 0.9047 | 45 |  |  | 2022-03-16 | 0.8326 | 45 | 2022-03-24 06:00 | 4.0959 | 0
2022-03-16 03:00 | 0.90175 | 47 | 2022-03-16 03:00 | 0.82953 | 47 | 2022-03-16 01:00 | 0.92325 | 46 |  |  | 2022-03-16 01:00 | 0.85197 | 46 | 2022-03-24 07:00 | 4.0959 | 0
2022-03-16 04:00 | 0.92905 | 44 | 2022-03-16 04:00 | 0.85806 | 44 | 2022-03-16 02:00 | 0.90567 | 45 |  |  | 2022-03-16 02:00 | 0.8336 | 45 | 2022-03-24 08:00 | 4.0959 | 0
2022-03-16 05:00 | 0.93198 | 44 | 2022-03-16 05:00 | 0.86114 | 44 | 2022-03-16 03:00 | 0.90175 | 45 |  |  | 2022-03-16 03:00 | 0.82953 | 45 | 2022-03-24 09:00 | 4.0959 | 0
2022-03-16 06:00 | 11.5343 | 45 | 2022-03-16 06:00 | 4.0959 | 45 | 2022-03-16 04:00 | 0.92905 | 45 |  |  | 2022-03-16 04:00 | 0.85806 | 45 | 2022-03-24 10:00 | 4.0959 | 0
2022-03-16 07:00 | 12.0351 | 44 | 2022-03-16 07:00 | 4.0959 | 44 | 2022-03-16 05:00 | 0.93198 | 43 |  |  | 2022-03-16 05:00 | 0.86114 | 43 | 2022-03-24 11:00 | 4.0959 | 0
2022-03-16 08:00 | 12.0351 | 47 | 2022-03-16 08:00 | 4.0959 | 47 | 2022-03-16 06:00 | 11.5343 | 43 |  |  | 2022-03-16 06:00 | 4.0959 | 43 | 2022-03-24 12:00 | 4.0959 | 0
2022-03-16 09:00 | 12.0351 | 56 | 2022-03-16 09:00 | 4.0959 | 56 | 2022-03-16 07:00 | 12.0351 | 42 |  |  | 2022-03-16 07:00 | 4.0959 | 42 | 2022-03-24 13:00 | 4.0959 | 0
2022-03-16 10:00 | 12.0351 | 58 | 2022-03-16 10:00 | 4.0959 | 58 | 2022-03-16 08:00 | 12.0351 | 42 |  |  | 2022-03-16 08:00 | 4.0959 | 42 | 2022-03-24 14:00 | 4.0959 | 0
2022-03-16 11:00 | 12.0351 | 60 | 2022-03-16 11:00 | 4.0959 | 60 | 2022-03-16 09:00 | 12.0351 | 41 |  |  | 2022-03-16 09:00 | 4.0959 | 41 | 2022-03-24 15:00 | 4.0959 | 0
2022-03-16 12:00 | 12.0351 | 62 | 2022-03-16 12:00 | 4.0959 | 62 | 2022-03-16 10:00 | 12.0351 | 40 |  |  | 2022-03-16 10:00 | 4.0959 | 40 | 2022-03-24 16:00 | 4.0959 | 0
2022-03-16 13:00 | 12.0351 | 60 | 2022-03-16 13:00 | 4.0959 | 60 | 2022-03-16 11:00 | 12.0351 | 39 |  |  | 2022-03-16 11:00 | 4.0959 | 39 | 2022-03-24 17:00 | 4.0959 | 0
2022-03-16 14:00 | 12.0351 | 58 | 2022-03-16 14:00 | 4.0959 | 58 | 2022-03-16 12:00 | 12.0351 | 38 |  |  | 2022-03-16 12:00 | 4.0959 | 38 | 2022-03-25 08:00 | 4.0959 | 0
2022-03-16 15:00 | 12.0351 | 55 | 2022-03-16 15:00 | 4.0959 | 55 | 2022-03-16 13:00 | 12.0351 | 36 |  |  | 2022-03-16 13:00 | 4.0959 | 36 | 2022-03-25 09:00 | 4.0959 | 0
2022-03-16 16:00 | 12.0351 | 54 | 2022-03-16 16:00 | 4.0959 | 54 | 2022-03-16 14:00 | 12.0351 | 35 |  |  | 2022-03-16 14:00 | 4.0959 | 35 | 2022-03-25 10:00 | 4.0959 | 0
2022-03-16 17:00 | 7.7985 | 54 | 2022-03-16 17:00 | 4.0959 | 54 | 2022-03-16 15:00 | 12.0351 | 37 |  |  | 2022-03-16 15:00 | 4.0959 | 37 | 2022-03-25 11:00 | 4.0959 | 0
2022-03-16 18:00 | 4.7958 | 51 | 2022-03-16 18:00 | 2.8768 | 51 | 2022-03-16 16:00 | 12.0351 | 39 |  |  | 2022-03-16 16:00 | 4.0959 | 39 | 2022-03-25 12:00 | 4.0959 | 0
2022-03-16 19:00 | 4.8545 | 48 | 2022-03-16 19:00 | 2.9211 | 48 | 2022-03-16 17:00 | 7.7985 | 38 |  |  | 2022-03-16 17:00 | 4.0959 | 38 | 2022-03-25 13:00 | 4.0959 | 0
2022-03-16 20:00 | 4.8613 | 48 | 2022-03-16 20:00 | 2.9265 | 48 | 2022-03-16 18:00 | 4.7958 | 37 |  |  | 2022-03-16 18:00 | 2.8768 | 37 | 2022-03-25 14:00 | 4.0959 | 0
2022-03-16 21:00 | 4.8311 | 47 | 2022-03-16 21:00 | 2.9029 | 47 | 2022-03-16 19:00 | 4.8545 | 37 |  |  | 2022-03-16 19:00 | 2.9211 | 37 | 2022-03-25 15:00 | 4.0959 | 0
2022-03-16 22:00 | 4.8935 | 46 | 2022-03-16 22:00 | 2.9528 | 46 | 2022-03-16 20:00 | 4.8613 | 38 |  |  | 2022-03-16 20:00 | 2.9265 | 38 | 2022-03-25 16:00 | 4.0959 | 0
2022-03-16 23:00 | 4.9428 | 46 | 2022-03-16 23:00 | 2.9961 | 46 | 2022-03-16 21:00 | 4.8311 | 38 |  |  | 2022-03-16 21:00 | 2.9029 | 38 | 2022-03-25 17:00 | 4.0959 | 0
2022-03-17 | 4.9012 | 46 | 2022-03-17 | 2.9594 | 46 | 2022-03-16 22:00 | 4.8935 | 39 |  |  | 2022-03-16 22:00 | 2.9528 | 39 | 2022-03-13 08:00 | 3.1956 | 39
2022-03-17 01:00 | 4.9515 | 45 | 2022-03-17 01:00 | 3.004 | 45 | 2022-03-16 23:00 | 4.9428 | 39 |  |  | 2022-03-16 23:00 | 2.9961 | 39 | 2022-03-15 05:00 | 3.1818 | 32
2022-03-17 02:00 | 4.988 | 45 | 2022-03-17 02:00 | 3.0388 | 45 | 2022-03-17 | 4.9012 | 40 |  |  | 2022-03-17 | 2.9594 | 40 | 2022-03-14 02:00 | 3.1494 | 27
2022-03-17 03:00 | 4.987 | 47 | 2022-03-17 03:00 | 3.0378 | 47 | 2022-03-17 01:00 | 4.9515 | 37 |  |  | 2022-03-17 01:00 | 3.004 | 37 | 2022-03-15 03:00 | 3.1483 | 31
2022-03-17 04:00 | 5.0158 | 47 | 2022-03-17 04:00 | 3.0666 | 47 | 2022-03-17 02:00 | 4.988 | 36 |  |  | 2022-03-17 02:00 | 3.0388 | 36 | 2022-03-14 01:00 | 3.145 | 29
2022-03-17 05:00 | 4.9947 | 49 | 2022-03-17 05:00 | 3.0454 | 49 | 2022-03-17 03:00 | 4.987 | 36 |  |  | 2022-03-17 03:00 | 3.0378 | 36 | 2022-03-13 11:00 | 3.144 | 38
2022-03-17 06:00 | 12.0351 | 50 | 2022-03-17 06:00 | 4.0959 | 50 | 2022-03-17 04:00 | 5.0158 | 36 |  |  | 2022-03-17 04:00 | 3.0666 | 36 | 2022-03-13 10:00 | 3.1353 | 38
2022-03-17 07:00 | 12.0351 | 47 | 2022-03-17 07:00 | 4.0959 | 47 | 2022-03-17 05:00 | 4.9947 | 35 |  |  | 2022-03-17 05:00 | 3.0454 | 35 | 2022-03-15 04:00 | 3.1353 | 32
2022-03-17 08:00 | 12.0351 | 47 | 2022-03-17 08:00 | 4.0959 | 47 | 2022-03-17 06:00 | 12.0351 | 35 |  |  | 2022-03-17 06:00 | 4.0959 | 35 | 2022-03-13 09:00 | 3.1343 | 39
2022-03-17 09:00 | 12.0351 | 47 | 2022-03-17 09:00 | 4.0959 | 47 | 2022-03-17 07:00 | 12.0351 | 35 |  |  | 2022-03-17 07:00 | 4.0959 | 35 | 2022-03-13 07:00 | 3.1131 | 39
2022-03-17 10:00 | 12.0351 | 48 | 2022-03-17 10:00 | 4.0959 | 48 | 2022-03-17 08:00 | 12.0351 | 34 |  |  | 2022-03-17 08:00 | 4.0959 | 34 | 2022-03-14 03:00 | 3.1131 | 27
2022-03-17 11:00 | 12.0351 | 51 | 2022-03-17 11:00 | 4.0959 | 51 | 2022-03-17 09:00 | 12.0351 | 35 |  |  | 2022-03-17 09:00 | 4.0959 | 35 | 2022-03-15 02:00 | 3.1131 | 29
2022-03-17 12:00 | 12.0351 | 52 | 2022-03-17 12:00 | 4.0959 | 52 | 2022-03-17 10:00 | 12.0351 | 34 |  |  | 2022-03-17 10:00 | 4.0959 | 34 | 2022-03-14 04:00 | 3.1068 | 27
2022-03-17 13:00 | 12.0351 | 52 | 2022-03-17 13:00 | 4.0959 | 52 | 2022-03-17 11:00 | 12.0351 | 32 |  |  | 2022-03-17 11:00 | 4.0959 | 32 | 2022-03-13 23:00 | 3.0955 | 30
2022-03-17 14:00 | 12.0351 | 53 | 2022-03-17 14:00 | 4.0959 | 53 | 2022-03-17 12:00 | 12.0351 | 30 |  |  | 2022-03-17 12:00 | 4.0959 | 30 | 2022-03-13 05:00 | 3.0945 | 44
2022-03-17 15:00 | 12.0351 | 54 | 2022-03-17 15:00 | 4.0959 | 54 | 2022-03-17 13:00 | 12.0351 | 30 |  |  | 2022-03-17 13:00 | 4.0959 | 30 | 2022-03-15 01:00 | 3.0945 | 32
2022-03-17 16:00 | 12.0351 | 55 | 2022-03-17 16:00 | 4.0959 | 55 | 2022-03-17 14:00 | 12.0351 | 30 |  |  | 2022-03-17 14:00 | 4.0959 | 30 | 2022-03-14 | 3.0794 | 29
2022-03-17 17:00 | 9.9006 | 54 | 2022-03-17 17:00 | 4.0959 | 54 | 2022-03-17 15:00 | 12.0351 | 29 |  |  | 2022-03-17 15:00 | 4.0959 | 29 | 2022-03-13 12:00 | 3.0754 | 37
2022-03-17 18:00 | 4.788 | 53 | 2022-03-17 18:00 | 2.8712 | 53 | 2022-03-17 16:00 | 12.0351 | 29 |  |  | 2022-03-17 16:00 | 4.0959 | 29 | 2022-03-13 04:00 | 3.0734 | 48
2022-03-17 19:00 | 4.7948 | 53 | 2022-03-17 19:00 | 2.8761 | 53 | 2022-03-17 17:00 | 9.9006 | 29 |  |  | 2022-03-17 17:00 | 4.0959 | 29 | 2022-03-13 03:00 | 3.0725 | 50
2022-03-17 20:00 | 4.785 | 53 | 2022-03-17 20:00 | 2.8691 | 53 | 2022-03-17 18:00 | 4.788 | 29 |  |  | 2022-03-17 18:00 | 2.8712 | 29 | 2022-03-17 04:00 | 3.0666 | 36
2022-03-17 21:00 | 4.8964 | 53 | 2022-03-17 21:00 | 2.9553 | 53 | 2022-03-17 19:00 | 4.7948 | 30 |  |  | 2022-03-17 19:00 | 2.8761 | 30 | 2022-03-13 06:00 | 3.0646 | 40
2022-03-17 22:00 | 4.9109 | 53 | 2022-03-17 22:00 | 2.9677 | 53 | 2022-03-17 20:00 | 4.785 | 31 |  |  | 2022-03-17 20:00 | 2.8691 | 31 | 2022-03-13 20:00 | 3.0646 | 30
2022-03-17 23:00 | 4.9437 | 52 | 2022-03-17 23:00 | 2.9969 | 52 | 2022-03-17 21:00 | 4.8964 | 33 |  |  | 2022-03-17 21:00 | 2.9553 | 33 | 2022-03-13 21:00 | 3.0588 | 29
2022-03-18 | 4.9109 | 52 | 2022-03-18 | 2.9677 | 52 | 2022-03-17 22:00 | 4.9109 | 33 |  |  | 2022-03-17 22:00 | 2.9677 | 33 | 2022-03-15 | 3.0511 | 32
2022-03-18 01:00 | 4.9119 | 52 | 2022-03-18 01:00 | 2.9686 | 52 | 2022-03-17 23:00 | 4.9437 | 33 |  |  | 2022-03-17 23:00 | 2.9969 | 33 | 2022-03-17 05:00 | 3.0454 | 35
2022-03-18 02:00 | 4.8847 | 52 | 2022-03-18 02:00 | 2.9455 | 52 | 2022-03-18 | 4.9109 | 33 |  |  | 2022-03-18 | 2.9677 | 33 | 2022-03-13 19:00 | 3.0407 | 30
2022-03-18 03:00 | 4.9012 | 53 | 2022-03-18 03:00 | 2.9594 | 53 | 2022-03-18 01:00 | 4.9119 | 33 |  |  | 2022-03-18 01:00 | 2.9686 | 33 | 2022-03-14 23:00 | 3.0407 | 32
2022-03-18 04:00 | 4.9515 | 53 | 2022-03-18 04:00 | 3.004 | 53 | 2022-03-18 02:00 | 4.8847 | 31 |  |  | 2022-03-18 02:00 | 2.9455 | 31 | 2022-03-17 02:00 | 3.0388 | 36
2022-03-18 05:00 | 4.9823 | 53 | 2022-03-18 05:00 | 3.0332 | 53 | 2022-03-18 03:00 | 4.9012 | 30 |  |  | 2022-03-18 03:00 | 2.9594 | 30 | 2022-03-17 03:00 | 3.0378 | 36
2022-03-18 06:00 | 12.0351 | 52 | 2022-03-18 06:00 | 4.0959 | 52 | 2022-03-18 04:00 | 4.9515 | 29 |  |  | 2022-03-18 04:00 | 3.004 | 29 | 2022-03-18 05:00 | 3.0332 | 28
2022-03-18 07:00 | 12.0351 | 51 | 2022-03-18 07:00 | 4.0959 | 51 | 2022-03-18 05:00 | 4.9823 | 28 |  |  | 2022-03-18 05:00 | 3.0332 | 28 | 2022-03-13 01:00 | 3.0267 | 53
2022-03-18 08:00 | 12.0351 | 51 | 2022-03-18 08:00 | 4.0959 | 51 | 2022-03-18 06:00 | 12.0351 | 27 |  |  | 2022-03-18 06:00 | 4.0959 | 27 | 2022-03-13 02:00 | 3.0257 | 50
2022-03-18 09:00 | 12.0351 | 51 | 2022-03-18 09:00 | 4.0959 | 51 | 2022-03-18 07:00 | 12.0351 | 27 |  |  | 2022-03-18 07:00 | 4.0959 | 27 | 2022-03-13 18:00 | 3.0257 | 31
2022-03-18 10:00 | 12.0351 | 51 | 2022-03-18 10:00 | 4.0959 | 51 | 2022-03-18 08:00 | 12.0351 | 26 |  |  | 2022-03-18 08:00 | 4.0959 | 26 | 2022-03-13 22:00 | 3.0257 | 29
2022-03-18 11:00 | 12.0351 | 55 | 2022-03-18 11:00 | 4.0959 | 55 | 2022-03-18 09:00 | 12.0351 | 26 |  |  | 2022-03-18 09:00 | 4.0959 | 26 | 2022-03-13 13:00 | 3.0211 | 35
2022-03-18 12:00 | 12.0351 | 60 | 2022-03-18 12:00 | 4.0959 | 60 | 2022-03-18 10:00 | 12.0351 | 25 |  |  | 2022-03-18 10:00 | 4.0959 | 25 | 2022-03-13 17:00 | 3.0175 | 31
2022-03-18 13:00 | 12.0351 | 62 | 2022-03-18 13:00 | 4.0959 | 62 | 2022-03-18 11:00 | 12.0351 | 24 |  |  | 2022-03-18 11:00 | 4.0959 | 24 | 2022-03-13 14:00 | 3.0139 | 34
2022-03-18 14:00 | 12.0351 | 61 | 2022-03-18 14:00 | 4.0959 | 61 | 2022-03-18 12:00 | 12.0351 | 23 |  |  | 2022-03-18 12:00 | 4.0959 | 23 | 2022-03-13 16:00 | 3.0103 | 32
2022-03-18 15:00 | 12.0351 | 59 | 2022-03-18 15:00 | 4.0959 | 59 | 2022-03-18 13:00 | 12.0351 | 22 |  |  | 2022-03-18 13:00 | 4.0959 | 22 | 2022-03-13 15:00 | 3.0094 | 33
2022-03-18 16:00 | 12.0351 | 57 | 2022-03-18 16:00 | 4.0959 | 57 | 2022-03-18 14:00 | 12.0351 | 22 |  |  | 2022-03-18 14:00 | 4.0959 | 22 | 2022-03-19 | 3.0058 | 30
2022-03-18 17:00 | 12.0351 | 56 | 2022-03-18 17:00 | 4.0959 | 56 | 2022-03-18 15:00 | 12.0351 | 22 |  |  | 2022-03-18 15:00 | 4.0959 | 22 | 2022-03-17 01:00 | 3.004 | 37
2022-03-18 18:00 | 7.2438 | 52 | 2022-03-18 18:00 | 4.0959 | 52 | 2022-03-18 16:00 | 12.0351 | 21 |  |  | 2022-03-18 16:00 | 4.0959 | 21 | 2022-03-18 04:00 | 3.004 | 29
2022-03-18 19:00 | 4.8281 | 50 | 2022-03-18 19:00 | 2.9007 | 50 | 2022-03-18 17:00 | 12.0351 | 21 |  |  | 2022-03-18 17:00 | 4.0959 | 21 | 2022-03-12 22:00 | 3.0014 | 54
2022-03-18 20:00 | 4.8281 | 49 | 2022-03-18 20:00 | 2.9007 | 49 | 2022-03-18 18:00 | 7.2438 | 22 |  |  | 2022-03-18 18:00 | 4.0959 | 22 | 2022-03-19 04:00 | 2.9978 | 28
2022-03-18 21:00 | 4.8164 | 49 | 2022-03-18 21:00 | 2.8918 | 49 | 2022-03-18 19:00 | 4.8281 | 23 |  |  | 2022-03-18 19:00 | 2.9007 | 23 | 2022-03-17 23:00 | 2.9969 | 33
2022-03-18 22:00 | 4.8574 | 49 | 2022-03-18 22:00 | 2.9234 | 49 | 2022-03-18 20:00 | 4.8281 | 25 |  |  | 2022-03-18 20:00 | 2.9007 | 25 | 2022-03-19 07:00 | 2.9969 | 28
2022-03-18 23:00 | 4.908 | 49 | 2022-03-18 23:00 | 2.9652 | 49 | 2022-03-18 21:00 | 4.8164 | 26 |  |  | 2022-03-18 21:00 | 2.8918 | 26 | 2022-03-16 23:00 | 2.9961 | 39
2022-03-19 | 4.9534 | 47 | 2022-03-19 | 3.0058 | 47 | 2022-03-18 22:00 | 4.8574 | 27 |  |  | 2022-03-18 22:00 | 2.9234 | 27 | 2022-03-12 19:00 | 2.9943 | 52
2022-03-19 01:00 | 4.937 | 47 | 2022-03-19 01:00 | 2.9908 | 47 | 2022-03-18 23:00 | 4.908 | 29 |  |  | 2022-03-18 23:00 | 2.9652 | 29 | 2022-03-19 01:00 | 2.9908 | 31
2022-03-19 02:00 | 4.9341 | 46 | 2022-03-19 02:00 | 2.9882 | 46 | 2022-03-19 | 4.9534 | 30 |  |  | 2022-03-19 | 3.0058 | 30 | 2022-03-19 02:00 | 2.9882 | 28
2022-03-19 03:00 | 4.9147 | 47 | 2022-03-19 03:00 | 2.9711 | 47 | 2022-03-19 01:00 | 4.937 | 31 |  |  | 2022-03-19 01:00 | 2.9908 | 31 | 2022-03-19 06:00 | 2.9882 | 28
2022-03-19 04:00 | 4.9447 | 48 | 2022-03-19 04:00 | 2.9978 | 48 | 2022-03-19 02:00 | 4.9341 | 28 |  |  | 2022-03-19 02:00 | 2.9882 | 28 | 2022-03-19 08:00 | 2.9856 | 29
2022-03-19 05:00 | 4.9303 | 49 | 2022-03-19 05:00 | 2.9848 | 49 | 2022-03-19 03:00 | 4.9147 | 23 |  |  | 2022-03-19 03:00 | 2.9711 | 23 | 2022-03-12 23:00 | 2.9848 | 57
2022-03-19 06:00 | 4.9341 | 50 | 2022-03-19 06:00 | 2.9882 | 50 | 2022-03-19 04:00 | 4.9447 | 28 |  |  | 2022-03-19 04:00 | 2.9978 | 28 | 2022-03-19 05:00 | 2.9848 | 25
2022-03-19 07:00 | 4.9437 | 50 | 2022-03-19 07:00 | 2.9969 | 50 | 2022-03-19 05:00 | 4.9303 | 25 |  |  | 2022-03-19 05:00 | 2.9848 | 25 | 2022-03-13 | 2.983 | 58
2022-03-19 08:00 | 4.9312 | 50 | 2022-03-19 08:00 | 2.9856 | 50 | 2022-03-19 06:00 | 4.9341 | 28 |  |  | 2022-03-19 06:00 | 2.9882 | 28 | 2022-03-12 20:00 | 2.9779 | 53
2022-03-19 09:00 | 4.8964 | 52 | 2022-03-19 09:00 | 2.9553 | 52 | 2022-03-19 07:00 | 4.9437 | 28 |  |  | 2022-03-19 07:00 | 2.9969 | 28 | 2022-03-19 03:00 | 2.9711 | 23
2022-03-19 10:00 | 4.8584 | 53 | 2022-03-19 10:00 | 2.9242 | 53 | 2022-03-19 08:00 | 4.9312 | 29 |  |  | 2022-03-19 08:00 | 2.9856 | 29 | 2022-03-22 05:00 | 2.9702 | 0
2022-03-19 11:00 | 4.8526 | 54 | 2022-03-19 11:00 | 2.9196 | 54 | 2022-03-19 09:00 | 4.8964 | 30 |  |  | 2022-03-19 09:00 | 2.9553 | 30 | 2022-03-18 01:00 | 2.9686 | 33
2022-03-19 12:00 | 4.8672 | 56 | 2022-03-19 12:00 | 2.9312 | 56 | 2022-03-19 10:00 | 4.8584 | 30 |  |  | 2022-03-19 10:00 | 2.9242 | 30 | 2022-03-17 22:00 | 2.9677 | 33
2022-03-19 13:00 | 4.8973 | 58 | 2022-03-19 13:00 | 2.9561 | 58 | 2022-03-19 11:00 | 4.8526 | 29 |  |  | 2022-03-19 11:00 | 2.9196 | 29 | 2022-03-18 | 2.9677 | 33
2022-03-19 14:00 | 4.8798 | 57 | 2022-03-19 14:00 | 2.9415 | 57 | 2022-03-19 12:00 | 4.8672 | 30 |  |  | 2022-03-19 12:00 | 2.9312 | 30 | 2022-03-12 10:00 | 2.9652 | 53
2022-03-19 15:00 | 4.8301 | 58 | 2022-03-19 15:00 | 2.9022 | 58 | 2022-03-19 13:00 | 4.8973 | 31 |  |  | 2022-03-19 13:00 | 2.9561 | 31 | 2022-03-18 23:00 | 2.9652 | 29
2022-03-19 16:00 | 4.8184 | 58 | 2022-03-19 16:00 | 2.8933 | 58 | 2022-03-19 14:00 | 4.8798 | 33 |  |  | 2022-03-19 14:00 | 2.9415 | 33 | 2022-03-12 06:00 | 2.9635 | 52
2022-03-19 17:00 | 4.834 | 58 | 2022-03-19 17:00 | 2.9051 | 58 | 2022-03-19 15:00 | 4.8301 | 34 |  |  | 2022-03-19 15:00 | 2.9022 | 34 | 2022-03-12 21:00 | 2.961 | 53
2022-03-19 18:00 | 4.7781 | 55 | 2022-03-19 18:00 | 2.8643 | 55 | 2022-03-19 16:00 | 4.8184 | 35 |  |  | 2022-03-19 16:00 | 2.8933 | 35 | 2022-03-12 18:00 | 2.9602 | 52
2022-03-19 19:00 | 4.7663 | 55 | 2022-03-19 19:00 | 2.8561 | 55 | 2022-03-19 17:00 | 4.834 | 35 |  |  | 2022-03-19 17:00 | 2.9051 | 35 | 2022-03-17 | 2.9594 | 40
2022-03-19 20:00 | 4.7762 | 53 | 2022-03-19 20:00 | 2.8629 | 53 | 2022-03-19 18:00 | 4.7781 | 36 |  |  | 2022-03-19 18:00 | 2.8643 | 36 | 2022-03-18 03:00 | 2.9594 | 30
2022-03-19 21:00 | 4.7525 | 53 | 2022-03-19 21:00 | 2.8467 | 53 | 2022-03-19 19:00 | 4.7663 | 37 |  |  | 2022-03-19 19:00 | 2.8561 | 37 | 2022-03-12 03:00 | 2.9586 | 52
2022-03-19 22:00 | 4.7584 | 52 | 2022-03-19 22:00 | 2.8507 | 52 | 2022-03-19 20:00 | 4.7762 | 37 |  |  | 2022-03-19 20:00 | 2.8629 | 37 | 2022-03-12 04:00 | 2.9569 | 51
2022-03-19 23:00 | 4.7958 | 52 | 2022-03-19 23:00 | 2.8768 | 52 | 2022-03-19 21:00 | 4.7525 | 39 |  |  | 2022-03-19 21:00 | 2.8467 | 39 | 2022-03-12 05:00 | 2.9569 | 52
2022-03-20 | 4.784 | 56 | 2022-03-20 | 2.8684 | 56 | 2022-03-19 22:00 | 4.7584 | 40 |  |  | 2022-03-19 22:00 | 2.8507 | 40 | 2022-03-19 13:00 | 2.9561 | 31
2022-03-20 01:00 | 4.8184 | 57 | 2022-03-20 01:00 | 2.8933 | 57 | 2022-03-19 23:00 | 4.7958 | 41 |  |  | 2022-03-19 23:00 | 2.8768 | 41 | 2022-03-12 08:00 | 2.9553 | 53
2022-03-20 02:00 | 4.834 | 55 | 2022-03-20 02:00 | 2.9051 | 55 | 2022-03-20 | 4.784 | 41 |  |  | 2022-03-20 | 2.8684 | 41 | 2022-03-17 21:00 | 2.9553 | 33
2022-03-20 03:00 | 4.7948 | 53 | 2022-03-20 03:00 | 2.8761 | 53 | 2022-03-20 01:00 | 4.8184 | 40 |  |  | 2022-03-20 01:00 | 2.8933 | 40 | 2022-03-19 09:00 | 2.9553 | 30
2022-03-20 04:00 | 4.7909 | 56 | 2022-03-20 04:00 | 2.8733 | 56 | 2022-03-20 02:00 | 4.834 | 39 |  |  | 2022-03-20 02:00 | 2.9051 | 39 | 2022-03-12 07:00 | 2.9545 | 52
2022-03-20 05:00 | 4.8193 | 56 | 2022-03-20 05:00 | 2.894 | 56 | 2022-03-20 03:00 | 4.7948 | 39 |  |  | 2022-03-20 03:00 | 2.8761 | 39 | 2022-03-16 22:00 | 2.9528 | 39
2022-03-20 06:00 | 4.8281 | 54 | 2022-03-20 06:00 | 2.9007 | 54 | 2022-03-20 04:00 | 4.7909 | 39 |  |  | 2022-03-20 04:00 | 2.8733 | 39 | 2022-03-24 05:00 | 2.9487 | 0
2022-03-20 07:00 | 4.8682 | 53 | 2022-03-20 07:00 | 2.932 | 53 | 2022-03-20 05:00 | 4.8193 | 39 |  |  | 2022-03-20 05:00 | 2.894 | 39 | 2022-03-18 02:00 | 2.9455 | 31
2022-03-20 08:00 | 4.8584 | 53 | 2022-03-20 08:00 | 2.9242 | 53 | 2022-03-20 06:00 | 4.8281 | 39 |  |  | 2022-03-20 06:00 | 2.9007 | 39 | 2022-03-14 19:00 | 2.9423 | 25
2022-03-20 09:00 | 4.8252 | 56 | 2022-03-20 09:00 | 2.8985 | 56 | 2022-03-20 07:00 | 4.8682 | 39 |  |  | 2022-03-20 07:00 | 2.932 | 39 | 2022-03-19 14:00 | 2.9415 | 33
2022-03-20 10:00 | 4.8438 | 58 | 2022-03-20 10:00 | 2.9127 | 58 | 2022-03-20 08:00 | 4.8584 | 39 |  |  | 2022-03-20 08:00 | 2.9242 | 39 | 2022-03-14 22:00 | 2.9359 | 31
2022-03-20 11:00 | 4.8027 | 59 | 2022-03-20 11:00 | 2.8818 | 59 | 2022-03-20 09:00 | 4.8252 | 40 |  |  | 2022-03-20 09:00 | 2.8985 | 40 | 2022-03-24 04:00 | 2.9359 | 0
2022-03-20 12:00 | 4.8076 | 59 | 2022-03-20 12:00 | 2.8854 | 59 | 2022-03-20 10:00 | 4.8438 | 40 |  |  | 2022-03-20 10:00 | 2.9127 | 40 | 2022-03-21 04:00 | 2.9336 | 0
2022-03-20 13:00 | 4.7801 | 58 | 2022-03-20 13:00 | 2.8657 | 58 | 2022-03-20 11:00 | 4.8027 | 40 |  |  | 2022-03-20 11:00 | 2.8818 | 40 | 2022-03-20 07:00 | 2.932 | 39
2022-03-20 14:00 | 4.7594 | 57 | 2022-03-20 14:00 | 2.8514 | 57 | 2022-03-20 12:00 | 4.8076 | 39 |  |  | 2022-03-20 12:00 | 2.8854 | 39 | 2022-03-19 12:00 | 2.9312 | 30
2022-03-20 15:00 | 4.7466 | 58 | 2022-03-20 15:00 | 2.8428 | 58 | 2022-03-20 13:00 | 4.7801 | 36 |  |  | 2022-03-20 13:00 | 2.8657 | 36 | 2022-03-22 04:00 | 2.9312 | 0
2022-03-20 16:00 | 4.7771 | 58 | 2022-03-20 16:00 | 2.8636 | 58 | 2022-03-20 14:00 | 4.7594 | 34 |  |  | 2022-03-20 14:00 | 2.8514 | 34 | 2022-03-12 02:00 | 2.9304 | 51
2022-03-20 17:00 | 4.7396 | 55 | 2022-03-20 17:00 | 2.8382 | 55 | 2022-03-20 15:00 | 4.7466 | 32 |  |  | 2022-03-20 15:00 | 2.8428 | 32 | 2022-03-11 20:00 | 2.9296 | 50
2022-03-20 18:00 | 4.7545 | 55 | 2022-03-20 18:00 | 2.8481 | 55 | 2022-03-20 16:00 | 4.7771 | 30 |  |  | 2022-03-20 16:00 | 2.8636 | 30 | 2022-03-25 06:00 | 2.9296 | 0
2022-03-20 19:00 | 4.7663 | 54 | 2022-03-20 19:00 | 2.8561 | 54 | 2022-03-20 17:00 | 4.7396 | 29 |  |  | 2022-03-20 17:00 | 2.8382 | 29 | 2022-03-12 09:00 | 2.9288 | 53
2022-03-20 20:00 | 4.787 | 53 | 2022-03-20 20:00 | 2.8705 | 53 | 2022-03-20 18:00 | 4.7545 | 29 |  |  | 2022-03-20 18:00 | 2.8481 | 29 | 2022-03-16 20:00 | 2.9265 | 38
2022-03-20 21:00 | 4.7436 | 50 | 2022-03-20 21:00 | 2.8408 | 50 | 2022-03-20 19:00 | 4.7663 | 30 |  |  | 2022-03-20 19:00 | 2.8561 | 30 | 2022-03-12 11:00 | 2.9257 | 53
2022-03-20 22:00 | 4.7396 | 48 | 2022-03-20 22:00 | 2.8382 | 48 | 2022-03-20 20:00 | 4.787 | 31 |  |  | 2022-03-20 20:00 | 2.8705 | 31 | 2022-03-19 10:00 | 2.9242 | 30
2022-03-20 23:00 | 4.7663 | 47 | 2022-03-20 23:00 | 2.8561 | 47 | 2022-03-20 21:00 | 4.7436 | 32 |  |  | 2022-03-20 21:00 | 2.8408 | 32 | 2022-03-20 08:00 | 2.9242 | 39
2022-03-21 | 4.7948 | 46 | 2022-03-21 | 2.8761 | 46 | 2022-03-20 22:00 | 4.7396 | 31 |  |  | 2022-03-20 22:00 | 2.8382 | 31 | 2022-03-18 22:00 | 2.9234 | 27
2022-03-21 01:00 | 4.8193 | 47 | 2022-03-21 01:00 | 2.894 | 47 | 2022-03-20 23:00 | 4.7663 | 32 |  |  | 2022-03-20 23:00 | 2.8561 | 32 | 2022-03-21 02:00 | 2.9226 | 0
2022-03-21 02:00 | 4.8565 | 47 | 2022-03-21 02:00 | 2.9226 | 47 | 2022-03-21 | 4.7948 | 30 |  |  | 2022-03-21 | 2.8761 | 30 | 2022-03-16 19:00 | 2.9211 | 37
2022-03-21 03:00 | 4.8242 | 46 | 2022-03-21 03:00 | 2.8977 | 46 | 2022-03-21 01:00 | 4.8193 | 29 |  |  | 2022-03-21 01:00 | 2.894 | 29 | 2022-03-24 01:00 | 2.9203 | 0
2022-03-21 04:00 | 4.8701 | 45 | 2022-03-21 04:00 | 2.9336 | 45 | [5 empty] | 2022-03-21 02:00 | 2.9226 | 0 | 2022-03-19 11:00 | 2.9196 | 29
2022-03-21 05:00 | 6.7462 | 45 | 2022-03-21 05:00 | 4.0959 | 45 | [5 empty] | 2022-03-21 03:00 | 2.8977 | 0 | 2022-03-22 03:00 | 2.9165 | 0
2022-03-21 06:00 | 12.0351 | 45 | 2022-03-21 06:00 | 4.0959 | 45 | [5 empty] | 2022-03-21 04:00 | 2.9336 | 0 | 2022-03-24 03:00 | 2.9149 | 0
2022-03-21 07:00 | 12.0351 | 45 | 2022-03-21 07:00 | 4.0959 | 45 | [5 empty] | 2022-03-21 05:00 | 4.0959 | 0 | 2022-03-12 16:00 | 2.9142 | 51
2022-03-21 08:00 | 12.0351 | 46 | 2022-03-21 08:00 | 4.0959 | 46 | [5 empty] | 2022-03-21 06:00 | 4.0959 | 0 | 2022-03-14 21:00 | 2.9142 | 29
2022-03-21 09:00 | 12.0351 | 48 | 2022-03-21 09:00 | 4.0959 | 48 | [5 empty] | 2022-03-21 07:00 | 4.0959 | 0 | 2022-03-24 02:00 | 2.9142 | 0
2022-03-21 10:00 | 12.0351 | 51 | 2022-03-21 10:00 | 4.0959 | 51 | [5 empty] | 2022-03-21 08:00 | 4.0959 | 0 | 2022-03-11 21:00 | 2.9127 | 51
2022-03-21 11:00 | 12.0351 | 53 | 2022-03-21 11:00 | 4.0959 | 53 | [5 empty] | 2022-03-21 09:00 | 4.0959 | 0 | 2022-03-20 10:00 | 2.9127 | 40
2022-03-21 12:00 | 12.0351 | 55 | 2022-03-21 12:00 | 4.0959 | 55 | [5 empty] | 2022-03-21 10:00 | 4.0959 | 0 | 2022-03-12 17:00 | 2.9119 | 51
2022-03-21 13:00 | 12.0351 | 58 | 2022-03-21 13:00 | 4.0959 | 58 | [5 empty] | 2022-03-21 11:00 | 4.0959 | 0 | 2022-03-22 01:00 | 2.9112 | 0
2022-03-21 14:00 | 12.0351 | 60 | 2022-03-21 14:00 | 4.0959 | 60 | [5 empty] | 2022-03-21 12:00 | 4.0959 | 0 | 2022-03-11 22:00 | 2.9089 | 51
2022-03-21 15:00 | 12.0351 | 62 | 2022-03-21 15:00 | 4.0959 | 62 | [5 empty] | 2022-03-21 13:00 | 4.0959 | 0 | 2022-03-12 15:00 | 2.9081 | 52
2022-03-21 16:00 | 12.0351 | 62 | 2022-03-21 16:00 | 4.0959 | 62 | [5 empty] | 2022-03-21 14:00 | 4.0959 | 0 | 2022-03-25 03:00 | 2.9074 | 0
2022-03-21 17:00 | 12.0351 | 63 | 2022-03-21 17:00 | 4.0959 | 63 | [5 empty] | 2022-03-21 15:00 | 4.0959 | 0 | 2022-03-14 20:00 | 2.9051 | 28
2022-03-21 18:00 | 4.7258 | 62 | 2022-03-21 18:00 | 2.8292 | 62 | [5 empty] | 2022-03-21 16:00 | 4.0959 | 0 | 2022-03-19 17:00 | 2.9051 | 35
2022-03-21 19:00 | 4.7938 | 60 | 2022-03-21 19:00 | 2.8754 | 60 | [5 empty] | 2022-03-21 17:00 | 4.0959 | 0 | 2022-03-20 02:00 | 2.9051 | 39
2022-03-21 20:00 | 4.711 | 58 | 2022-03-21 20:00 | 2.8198 | 58 | [5 empty] | 2022-03-21 18:00 | 2.8292 | 0 | 2022-03-11 23:00 | 2.9044 | 52
2022-03-21 21:00 | 4.6812 | 57 | 2022-03-21 21:00 | 2.8016 | 57 | [5 empty] | 2022-03-21 19:00 | 2.8754 | 0 | 2022-03-12 14:00 | 2.9036 | 52
2022-03-21 22:00 | 4.6901 | 54 | 2022-03-21 22:00 | 2.807 | 54 | [5 empty] | 2022-03-21 20:00 | 2.8198 | 0 | 2022-03-16 21:00 | 2.9029 | 38
2022-03-21 23:00 | 4.7357 | 54 | 2022-03-21 23:00 | 2.8356 | 54 | [5 empty] | 2022-03-21 21:00 | 2.8016 | 0 | 2022-03-19 15:00 | 2.9022 | 34
2022-03-22 | 4.7317 | 54 | 2022-03-22 | 2.833 | 54 | [5 empty] | 2022-03-21 22:00 | 2.807 | 0 | 2022-03-12 01:00 | 2.9014 | 52
2022-03-22 01:00 | 4.8418 | 53 | 2022-03-22 01:00 | 2.9112 | 53 | [5 empty] | 2022-03-21 23:00 | 2.8356 | 0 | 2022-03-18 19:00 | 2.9007 | 23
2022-03-22 02:00 | 4.7899 | 52 | 2022-03-22 02:00 | 2.8726 | 52 | [5 empty] | 2022-03-22 | 2.833 | 0 | 2022-03-18 20:00 | 2.9007 | 25
2022-03-22 03:00 | 4.8487 | 51 | 2022-03-22 03:00 | 2.9165 | 51 | [5 empty] | 2022-03-22 01:00 | 2.9112 | 0 | 2022-03-20 06:00 | 2.9007 | 39
2022-03-22 04:00 | 4.8672 | 51 | 2022-03-22 04:00 | 2.9312 | 51 | [5 empty] | 2022-03-22 02:00 | 2.8726 | 0 | 2022-03-20 09:00 | 2.8985 | 40
2022-03-22 05:00 | 4.9138 | 50 | 2022-03-22 05:00 | 2.9702 | 50 | [5 empty] | 2022-03-22 03:00 | 2.9165 | 0 | 2022-03-21 03:00 | 2.8977 | 0
2022-03-22 06:00 | 12.0351 | 49 | 2022-03-22 06:00 | 4.0959 | 49 | [5 empty] | 2022-03-22 04:00 | 2.9312 | 0 | 2022-03-25 05:00 | 2.8977 | 0
2022-03-22 07:00 | 12.0351 | 47 | 2022-03-22 07:00 | 4.0959 | 47 | [5 empty] | 2022-03-22 05:00 | 2.9702 | 0 | 2022-03-25 07:00 | 2.8977 | 0
2022-03-22 08:00 | 12.0351 | 46 | 2022-03-22 08:00 | 4.0959 | 46 | [5 empty] | 2022-03-22 06:00 | 4.0959 | 0 | 2022-03-20 05:00 | 2.894 | 39
2022-03-22 09:00 | 12.0351 | 47 | 2022-03-22 09:00 | 4.0959 | 47 | [5 empty] | 2022-03-22 07:00 | 4.0959 | 0 | 2022-03-21 01:00 | 2.894 | 29
2022-03-22 10:00 | 12.0351 | 48 | 2022-03-22 10:00 | 4.0959 | 48 | [5 empty] | 2022-03-22 08:00 | 4.0959 | 0 | 2022-03-24 | 2.894 | 0
2022-03-22 11:00 | 12.0351 | 50 | 2022-03-22 11:00 | 4.0959 | 50 | [5 empty] | 2022-03-22 09:00 | 4.0959 | 0 | 2022-03-19 16:00 | 2.8933 | 35
2022-03-22 12:00 | 12.0351 | 52 | 2022-03-22 12:00 | 4.0959 | 52 | [5 empty] | 2022-03-22 10:00 | 4.0959 | 0 | 2022-03-20 01:00 | 2.8933 | 40
2022-03-22 13:00 | 12.0351 | 54 | 2022-03-22 13:00 | 4.0959 | 54 | [5 empty] | 2022-03-22 11:00 | 4.0959 | 0 | 2022-03-12 13:00 | 2.8918 | 51
2022-03-22 14:00 | 12.0351 | 56 | 2022-03-22 14:00 | 4.0959 | 56 | [5 empty] | 2022-03-22 12:00 | 4.0959 | 0 | 2022-03-18 21:00 | 2.8918 | 26
2022-03-22 15:00 | 12.0351 | 59 | 2022-03-22 15:00 | 4.0959 | 59 | [5 empty] | 2022-03-22 13:00 | 4.0959 | 0 | 2022-03-20 12:00 | 2.8854 | 39
2022-03-22 16:00 | 12.0351 | 58 | 2022-03-22 16:00 | 4.0959 | 58 | [5 empty] | 2022-03-22 14:00 | 4.0959 | 0 | 2022-03-25 02:00 | 2.8846 | 0
2022-03-22 17:00 | 8.4296 | 57 | 2022-03-22 17:00 | 4.0959 | 57 | [5 empty] | 2022-03-22 15:00 | 4.0959 | 0 | 2022-03-25 01:00 | 2.8832 | 0
2022-03-22 18:00 | 2.7152 | 57 | 2022-03-22 18:00 | 2.3338 | 57 | [5 empty] | 2022-03-22 16:00 | 4.0959 | 0 | 2022-03-20 11:00 | 2.8818 | 40
2022-03-22 19:00 | 2.7661 | 55 | 2022-03-22 19:00 | 2.3491 | 55 | [5 empty] | 2022-03-22 17:00 | 4.0959 | 0 | 2022-03-12 12:00 | 2.8803 | 53
2022-03-22 20:00 | 2.7421 | 54 | 2022-03-22 20:00 | 2.342 | 54 | [5 empty] | 2022-03-22 18:00 | 2.3338 | 0 | 2022-03-25 04:00 | 2.8789 | 0
2022-03-22 21:00 | 2.7601 | 52 | 2022-03-22 21:00 | 2.3474 | 52 | [5 empty] | 2022-03-22 19:00 | 2.3491 | 0 | 2022-03-12 | 2.8768 | 53
2022-03-22 22:00 | 2.7301 | 50 | 2022-03-22 22:00 | 2.3384 | 50 | [5 empty] | 2022-03-22 20:00 | 2.342 | 0 | 2022-03-16 18:00 | 2.8768 | 37
2022-03-22 23:00 | 2.7142 | 49 | 2022-03-22 23:00 | 2.3335 | 49 | [5 empty] | 2022-03-22 21:00 | 2.3474 | 0 | 2022-03-19 23:00 | 2.8768 | 41
2022-03-23 | 2.7511 | 47 | 2022-03-23 | 2.3447 | 47 | [5 empty] | 2022-03-22 22:00 | 2.3384 | 0 | 2022-03-17 19:00 | 2.8761 | 30
2022-03-23 01:00 | 2.7972 | 46 | 2022-03-23 01:00 | 2.3579 | 46 | [5 empty] | 2022-03-22 23:00 | 2.3335 | 0 | 2022-03-20 03:00 | 2.8761 | 39
2022-03-23 02:00 | 2.7431 | 44 | 2022-03-23 02:00 | 2.3423 | 44 | [5 empty] | 2022-03-23 | 2.3447 | 0 | 2022-03-21 | 2.8761 | 30
2022-03-23 03:00 | 2.7751 | 42 | 2022-03-23 03:00 | 2.3517 | 42 | [5 empty] | 2022-03-23 01:00 | 2.3579 | 0 | 2022-03-21 19:00 | 2.8754 | 0
2022-03-23 04:00 | 2.7871 | 42 | 2022-03-23 04:00 | 2.3551 | 42 | [5 empty] | 2022-03-23 02:00 | 2.3423 | 0 | 2022-03-20 04:00 | 2.8733 | 39
2022-03-23 05:00 | 2.8042 | 41 | 2022-03-23 05:00 | 2.3599 | 41 | [5 empty] | 2022-03-23 03:00 | 2.3517 | 0 | 2022-03-22 02:00 | 2.8726 | 0
2022-03-23 06:00 | 11.4901 | 40 | 2022-03-23 06:00 | 4.0959 | 40 | [5 empty] | 2022-03-23 04:00 | 2.3551 | 0 | 2022-03-17 18:00 | 2.8712 | 29
2022-03-23 07:00 | 12.0351 | 40 | 2022-03-23 07:00 | 4.0959 | 40 | [5 empty] | 2022-03-23 05:00 | 2.3599 | 0 | 2022-03-20 20:00 | 2.8705 | 31
2022-03-23 08:00 | 12.0351 | 40 | 2022-03-23 08:00 | 4.0959 | 40 | [5 empty] | 2022-03-23 06:00 | 4.0959 | 0 | 2022-03-25 | 2.8698 | 0
2022-03-23 09:00 | 12.0351 | 42 | 2022-03-23 09:00 | 4.0959 | 42 | [5 empty] | 2022-03-23 07:00 | 4.0959 | 0 | 2022-03-17 20:00 | 2.8691 | 31
2022-03-23 10:00 | 12.0351 | 43 | 2022-03-23 10:00 | 4.0959 | 43 | [5 empty] | 2022-03-23 08:00 | 4.0959 | 0 | 2022-03-20 | 2.8684 | 41
2022-03-23 11:00 | 12.0351 | 43 | 2022-03-23 11:00 | 4.0959 | 43 | [5 empty] | 2022-03-23 09:00 | 4.0959 | 0 | 2022-03-20 13:00 | 2.8657 | 36
2022-03-23 12:00 | 12.0351 | 43 | 2022-03-23 12:00 | 4.0959 | 43 | [5 empty] | 2022-03-23 10:00 | 4.0959 | 0 | 2022-03-26 | 2.8657 | 0
2022-03-23 13:00 | 12.0351 | 45 | 2022-03-23 13:00 | 4.0959 | 45 | [5 empty] | 2022-03-23 11:00 | 4.0959 | 0 | 2022-03-19 18:00 | 2.8643 | 36
2022-03-23 14:00 | 12.0351 | 45 | 2022-03-23 14:00 | 4.0959 | 45 | [5 empty] | 2022-03-23 12:00 | 4.0959 | 0 | 2022-03-20 16:00 | 2.8636 | 30
2022-03-23 15:00 | 12.0351 | 43 | 2022-03-23 15:00 | 4.0959 | 43 | [5 empty] | 2022-03-23 13:00 | 4.0959 | 0 | 2022-03-19 20:00 | 2.8629 | 37
2022-03-23 16:00 | 12.0351 | 42 | 2022-03-23 16:00 | 4.0959 | 42 | [5 empty] | 2022-03-23 14:00 | 4.0959 | 0 | 2022-03-19 19:00 | 2.8561 | 37
2022-03-23 17:00 | 12.0351 | 41 | 2022-03-23 17:00 | 4.0959 | 41 | [5 empty] | 2022-03-23 15:00 | 4.0959 | 0 | 2022-03-20 19:00 | 2.8561 | 30
2022-03-23 18:00 | 4.7238 | 42 | 2022-03-23 18:00 | 2.828 | 42 | [5 empty] | 2022-03-23 16:00 | 4.0959 | 0 | 2022-03-20 23:00 | 2.8561 | 32
2022-03-23 19:00 | 4.7396 | 42 | 2022-03-23 19:00 | 2.8382 | 42 | [5 empty] | 2022-03-23 17:00 | 4.0959 | 0 | 2022-03-20 14:00 | 2.8514 | 34
2022-03-23 20:00 | 4.6921 | 41 | 2022-03-23 20:00 | 2.8082 | 41 | [5 empty] | 2022-03-23 18:00 | 2.828 | 0 | 2022-03-19 22:00 | 2.8507 | 40
2022-03-23 21:00 | 4.707 | 41 | 2022-03-23 21:00 | 2.8173 | 41 | [5 empty] | 2022-03-23 19:00 | 2.8382 | 0 | 2022-03-23 22:00 | 2.8507 | 0
2022-03-23 22:00 | 4.7584 | 42 | 2022-03-23 22:00 | 2.8507 | 42 | [5 empty] | 2022-03-23 20:00 | 2.8082 | 0 | 2022-03-20 18:00 | 2.8481 | 29
2022-03-23 23:00 | 4.7456 | 42 | 2022-03-23 23:00 | 2.8421 | 42 | [5 empty] | 2022-03-23 21:00 | 2.8173 | 0 | 2022-03-19 21:00 | 2.8467 | 39
2022-03-24 | 4.8193 | 40 | 2022-03-24 | 2.894 | 40 | [5 empty] | 2022-03-23 22:00 | 2.8507 | 0 | 2022-03-24 23:00 | 2.8467 | 0
2022-03-24 01:00 | 4.8535 | 41 | 2022-03-24 01:00 | 2.9203 | 41 | [5 empty] | 2022-03-23 23:00 | 2.8421 | 0 | 2022-03-20 15:00 | 2.8428 | 32
2022-03-24 02:00 | 4.8457 | 41 | 2022-03-24 02:00 | 2.9142 | 41 | [5 empty] | 2022-03-24 | 2.894 | 0 | 2022-03-23 23:00 | 2.8421 | 0
2022-03-24 03:00 | 4.8467 | 42 | 2022-03-24 03:00 | 2.9149 | 42 | [5 empty] | 2022-03-24 01:00 | 2.9203 | 0 | 2022-03-20 21:00 | 2.8408 | 32
2022-03-24 04:00 | 4.873 | 43 | 2022-03-24 04:00 | 2.9359 | 43 | [5 empty] | 2022-03-24 02:00 | 2.9142 | 0 | 2022-03-24 19:00 | 2.8408 | 0
2022-03-24 05:00 | 4.8886 | 44 | 2022-03-24 05:00 | 2.9487 | 44 | [5 empty] | 2022-03-24 03:00 | 2.9149 | 0 | 2022-03-24 22:00 | 2.8388 | 0
2022-03-24 06:00 | 10.2971 | 44 | 2022-03-24 06:00 | 4.0959 | 44 | [5 empty] | 2022-03-24 04:00 | 2.9359 | 0 | 2022-03-20 17:00 | 2.8382 | 29
2022-03-24 07:00 | 12.0351 | 44 | 2022-03-24 07:00 | 4.0959 | 44 | [5 empty] | 2022-03-24 05:00 | 2.9487 | 0 | 2022-03-20 22:00 | 2.8382 | 31
2022-03-24 08:00 | 12.0351 | 45 | 2022-03-24 08:00 | 4.0959 | 45 | [5 empty] | 2022-03-24 06:00 | 4.0959 | 0 | 2022-03-23 19:00 | 2.8382 | 0
2022-03-24 09:00 | 12.0351 | 45 | 2022-03-24 09:00 | 4.0959 | 45 | [5 empty] | 2022-03-24 07:00 | 4.0959 | 0 | 2022-03-25 23:00 | 2.8376 | 0
2022-03-24 10:00 | 12.0351 | 46 | 2022-03-24 10:00 | 4.0959 | 46 | [5 empty] | 2022-03-24 08:00 | 4.0959 | 0 | 2022-03-21 23:00 | 2.8356 | 0
2022-03-24 11:00 | 12.0351 | 47 | 2022-03-24 11:00 | 4.0959 | 47 | [5 empty] | 2022-03-24 09:00 | 4.0959 | 0 | 2022-03-22 | 2.833 | 0
2022-03-24 12:00 | 12.0351 | 46 | 2022-03-24 12:00 | 4.0959 | 46 | [5 empty] | 2022-03-24 10:00 | 4.0959 | 0 | 2022-03-21 18:00 | 2.8292 | 0
2022-03-24 13:00 | 12.0351 | 45 | 2022-03-24 13:00 | 4.0959 | 45 | [5 empty] | 2022-03-24 11:00 | 4.0959 | 0 | 2022-03-23 18:00 | 2.828 | 0
2022-03-24 14:00 | 12.0351 | 45 | 2022-03-24 14:00 | 4.0959 | 45 | [5 empty] | 2022-03-24 12:00 | 4.0959 | 0 | 2022-03-24 18:00 | 2.8204 | 0
2022-03-24 15:00 | 12.0351 | 45 | 2022-03-24 15:00 | 4.0959 | 45 | [5 empty] | 2022-03-24 13:00 | 4.0959 | 0 | 2022-03-21 20:00 | 2.8198 | 0
2022-03-24 16:00 | 12.0351 | 46 | 2022-03-24 16:00 | 4.0959 | 46 | [5 empty] | 2022-03-24 14:00 | 4.0959 | 0 | 2022-03-23 21:00 | 2.8173 | 0
2022-03-24 17:00 | 6.544 | 46 | 2022-03-24 17:00 | 4.0959 | 46 | [5 empty] | 2022-03-24 15:00 | 4.0959 | 0 | 2022-03-24 21:00 | 2.8167 | 0
2022-03-24 18:00 | 4.7119 | 46 | 2022-03-24 18:00 | 2.8204 | 46 | [5 empty] | 2022-03-24 16:00 | 4.0959 | 0 | 2022-03-25 19:00 | 2.813 | 0
2022-03-24 19:00 | 4.7436 | 46 | 2022-03-24 19:00 | 2.8408 | 46 | [5 empty] | 2022-03-24 17:00 | 4.0959 | 0 | 2022-03-25 18:00 | 2.8112 | 0
2022-03-24 20:00 | 4.6891 | 46 | 2022-03-24 20:00 | 2.8064 | 46 | [5 empty] | 2022-03-24 18:00 | 2.8204 | 0 | 2022-03-23 20:00 | 2.8082 | 0
2022-03-24 21:00 | 4.706 | 45 | 2022-03-24 21:00 | 2.8167 | 45 | [5 empty] | 2022-03-24 19:00 | 2.8408 | 0 | 2022-03-21 22:00 | 2.807 | 0
2022-03-24 22:00 | 4.7406 | 45 | 2022-03-24 22:00 | 2.8388 | 45 | [5 empty] | 2022-03-24 20:00 | 2.8064 | 0 | 2022-03-24 20:00 | 2.8064 | 0
2022-03-24 23:00 | 4.7525 | 45 | 2022-03-24 23:00 | 2.8467 | 45 | [5 empty] | 2022-03-24 21:00 | 2.8167 | 0 | 2022-03-21 21:00 | 2.8016 | 0
2022-03-25 | 4.786 | 44 | 2022-03-25 | 2.8698 | 44 | [5 empty] | 2022-03-24 22:00 | 2.8388 | 0 | 2022-03-25 20:00 | 2.791 | 0
2022-03-25 01:00 | 4.8046 | 44 | 2022-03-25 01:00 | 2.8832 | 44 | [5 empty] | 2022-03-24 23:00 | 2.8467 | 0 | 2022-03-25 22:00 | 2.7905 | 0
2022-03-25 02:00 | 4.8066 | 44 | 2022-03-25 02:00 | 2.8846 | 44 | [5 empty] | 2022-03-25 | 2.8698 | 0 | 2022-03-25 21:00 | 2.7853 | 0
2022-03-25 03:00 | 4.837 | 45 | 2022-03-25 03:00 | 2.9074 | 45 | [5 empty] | 2022-03-25 01:00 | 2.8832 | 0 | 2022-03-23 05:00 | 2.3599 | 0
2022-03-25 04:00 | 4.7988 | 45 | 2022-03-25 04:00 | 2.8789 | 45 | [5 empty] | 2022-03-25 02:00 | 2.8846 | 0 | 2022-03-23 01:00 | 2.3579 | 0
2022-03-25 05:00 | 4.8242 | 45 | 2022-03-25 05:00 | 2.8977 | 45 | [5 empty] | 2022-03-25 03:00 | 2.9074 | 0 | 2022-03-23 04:00 | 2.3551 | 0
2022-03-25 06:00 | 4.8652 | 45 | 2022-03-25 06:00 | 2.9296 | 45 | [5 empty] | 2022-03-25 04:00 | 2.8789 | 0 | 2022-03-23 03:00 | 2.3517 | 0
2022-03-25 07:00 | 4.8242 | 46 | 2022-03-25 07:00 | 2.8977 | 46 | [5 empty] | 2022-03-25 05:00 | 2.8977 | 0 | 2022-03-22 19:00 | 2.3491 | 0
2022-03-25 08:00 | 8.5391 | 47 | 2022-03-25 08:00 | 4.0959 | 47 | [5 empty] | 2022-03-25 06:00 | 2.9296 | 0 | 2022-03-22 21:00 | 2.3474 | 0
2022-03-25 09:00 | 12.0351 | 49 | 2022-03-25 09:00 | 4.0959 | 49 | [5 empty] | 2022-03-25 07:00 | 2.8977 | 0 | 2022-03-23 | 2.3447 | 0
2022-03-25 10:00 | 12.0351 | 49 | 2022-03-25 10:00 | 4.0959 | 49 | [5 empty] | 2022-03-25 08:00 | 4.0959 | 0 | 2022-03-23 02:00 | 2.3423 | 0
2022-03-25 11:00 | 12.0351 | 49 | 2022-03-25 11:00 | 4.0959 | 49 | [5 empty] | 2022-03-25 09:00 | 4.0959 | 0 | 2022-03-22 20:00 | 2.342 | 0
2022-03-25 12:00 | 12.0351 | 51 | 2022-03-25 12:00 | 4.0959 | 51 | [5 empty] | 2022-03-25 10:00 | 4.0959 | 0 | 2022-03-22 22:00 | 2.3384 | 0
2022-03-25 13:00 | 12.0351 | 55 | 2022-03-25 13:00 | 4.0959 | 55 | [5 empty] | 2022-03-25 11:00 | 4.0959 | 0 | 2022-03-22 18:00 | 2.3338 | 0
2022-03-25 14:00 | 12.0351 | 55 | 2022-03-25 14:00 | 4.0959 | 55 | [5 empty] | 2022-03-25 12:00 | 4.0959 | 0 | 2022-03-22 23:00 | 2.3335 | 0
2022-03-25 15:00 | 12.0351 | 54 | 2022-03-25 15:00 | 4.0959 | 54 | [5 empty] | 2022-03-25 13:00 | 4.0959 | 0 | 2022-03-16 05:00 | 0.86114 | 43
2022-03-25 16:00 | 12.0351 | 57 | 2022-03-25 16:00 | 4.0959 | 57 | [5 empty] | 2022-03-25 14:00 | 4.0959 | 0 | 2022-03-16 04:00 | 0.85806 | 45
2022-03-25 17:00 | 9.0628 | 56 | 2022-03-25 17:00 | 4.0959 | 56 | [5 empty] | 2022-03-25 15:00 | 4.0959 | 0 | 2022-03-16 01:00 | 0.85197 | 46
2022-03-25 18:00 | 4.6971 | 56 | 2022-03-25 18:00 | 2.8112 | 56 | [5 empty] | 2022-03-25 16:00 | 4.0959 | 0 | 2022-03-15 19:00 | 0.84074 | 39
2022-03-25 19:00 | 4.7001 | 53 | 2022-03-25 19:00 | 2.813 | 53 | [5 empty] | 2022-03-25 17:00 | 4.0959 | 0 | 2022-03-15 20:00 | 0.83667 | 40
2022-03-25 20:00 | 4.6632 | 53 | 2022-03-25 20:00 | 2.791 | 53 | [5 empty] | 2022-03-25 18:00 | 2.8112 | 0 | 2022-03-16 02:00 | 0.8336 | 45
2022-03-25 21:00 | 4.6533 | 51 | 2022-03-25 21:00 | 2.7853 | 51 | [5 empty] | 2022-03-25 19:00 | 2.813 | 0 | 2022-03-16 | 0.8326 | 45
2022-03-25 22:00 | 4.6623 | 51 | 2022-03-25 22:00 | 2.7905 | 51 | [5 empty] | 2022-03-25 20:00 | 2.791 | 0 | 2022-03-16 03:00 | 0.82953 | 45
2022-03-25 23:00 | 4.7387 | 51 | 2022-03-25 23:00 | 2.8376 | 51 | [5 empty] | 2022-03-25 21:00 | 2.7853 | 0 | 2022-03-15 21:00 | 0.82546 | 40
2022-03-26 | 4.7801 | 52 | 2022-03-26 | 2.8657 | 52 | [5 empty] | 2022-03-25 22:00 | 2.7905 | 0 | 2022-03-15 22:00 | 0.81833 | 41
2022-03-26 01:00 | 4.8154 | 51 | 2022-03-26 01:00 | 2.8911 | 51 | [5 empty] | 2022-03-25 23:00 | 2.8376 | 0 | 2022-03-15 23:00 | 0.81327 | 43
2022-03-26 02:00 | 4.8721 | 50 | 2022-03-26 02:00 | 2.9351 | 50 | [5 empty] | 2022-03-26 | 2.8657 | 0 | 2022-03-15 18:00 | 0.80309 | 37
2022-03-26 03:00 | 4.8857 | 50 | 2022-03-26 03:00 | 2.9463 | 50 | [8 empty] | 0 | 0 | 0
2022-03-26 04:00 | 4.8526 | 49 | 2022-03-26 04:00 | 2.9196 | 49 | [8 empty] | 0 | 0 | 0
2022-03-26 05:00 | 4.8721 | 49 | 2022-03-26 05:00 | 2.9351 | 49 | [8 empty] | 0 | 0 | 0
2022-03-26 06:00 | 4.8886 | 49 | 2022-03-26 06:00 | 2.9487 | 49 | [8 empty] | 0 | 0 | 0
2022-03-26 07:00 | 4.8448 | 47 | 2022-03-26 07:00 | 2.9134 | 47 | [8 empty] | 0 | 0 | 0
2022-03-26 08:00 | 4.8535 | 48 | 2022-03-26 08:00 | 2.9203 | 48 | [8 empty] | 0 | 0 | 0
2022-03-26 09:00 | 4.8584 | 49 | 2022-03-26 09:00 | 2.9242 | 49 | [8 empty] | 0 | 0 | 0
2022-03-26 10:00 | 4.8359 | 52 | 2022-03-26 10:00 | 2.9066 | 52 | [8 empty] | 0 | 0 | 0
2022-03-26 11:00 | 4.7948 | 53 | 2022-03-26 11:00 | 2.8761 | 53 | [8 empty] | 0 | 0 | 0
2022-03-26 12:00 | 4.7317 | 52 | 2022-03-26 12:00 | 2.833 | 52 | [8 empty] | 0 | 0 | 0
2022-03-26 13:00 | 4.7169 | 51 | 2022-03-26 13:00 | 2.8235 | 51 | [8 empty] | 0 | 0 | 0
2022-03-26 14:00 | 4.7119 | 53 | 2022-03-26 14:00 | 2.8204 | 53 | [8 empty] | 0 | 0 | 0
2022-03-26 15:00 | 4.698 | 47 | 2022-03-26 15:00 | 2.8118 | 47 | [8 empty] | 0 | 0 | 0
2022-03-26 16:00 | 4.704 | 48 | 2022-03-26 16:00 | 2.8155 | 48 | [8 empty] | 0 | 0 | 0
2022-03-26 17:00 | 4.7208 | 53 | 2022-03-26 17:00 | 2.826 | 53 | [8 empty] | 0 | 0 | 0
2022-03-26 18:00 | 4.7771 | 50 | 2022-03-26 18:00 | 2.8636 | 50 | [8 empty] | 0 | 0 | 0
2022-03-26 19:00 | 4.7308 | 50 | 2022-03-26 19:00 | 2.8324 | 50 | [8 empty] | 0 | 0 | 0
2022-03-26 20:00 | 4.7288 | 48 | 2022-03-26 20:00 | 2.8311 | 48 | [8 empty] | 0 | 0 | 0
2022-03-26 21:00 | 4.7495 | 47 | 2022-03-26 21:00 | 2.8448 | 47 | [8 empty] | 0 | 0 | 0
2022-03-26 22:00 | 4.7426 | 47 | 2022-03-26 22:00 | 2.8402 | 47 | [8 empty] | 0 | 0 | 0
2022-03-26 23:00 | 4.8085 | 45 | 2022-03-26 23:00 | 2.8861 | 45 | [8 empty] | 0 | 0 | 0
2022-03-27 | 4.7948 | 44 | 2022-03-27 | 2.8761 | 44 | [8 empty] | 0 | 0 | 0
2022-03-27 01:00 | 4.8604 | 42 | 2022-03-27 01:00 | 2.9257 | 42 | [8 empty] | 0 | 0 | 0
2022-03-27 02:00 | 4.8964 | 41 | 2022-03-27 02:00 | 2.9553 | 41 | [8 empty] | 0 | 0 | 0
2022-03-27 03:00 | 4.9206 | 41 | 2022-03-27 03:00 | 2.9762 | 41 | [8 empty] | 0 | 0 | 0
2022-03-27 04:00 | 4.9003 | 40 | 2022-03-27 04:00 | 2.9586 | 40 | [8 empty] | 0 | 0 | 0
2022-03-27 05:00 | 4.8886 | 41 | 2022-03-27 05:00 | 2.9487 | 41 | [8 empty] | 0 | 0 | 0
2022-03-27 06:00 | 4.908 | 39 | 2022-03-27 06:00 | 2.9652 | 39 | [8 empty] | 0 | 0 | 0
2022-03-27 07:00 | 4.9031 | 40 | 2022-03-27 07:00 | 2.961 | 40 | [8 empty] | 0 | 0 | 0
2022-03-27 08:00 | 4.9244 | 42 | 2022-03-27 08:00 | 2.9796 | 42 | [8 empty] | 0 | 0 | 0
2022-03-27 09:00 | 4.8837 | 43 | 2022-03-27 09:00 | 2.9447 | 43 | [8 empty] | 0 | 0 | 0
2022-03-27 10:00 | 4.8184 | 44 | 2022-03-27 10:00 | 2.8933 | 44 | [8 empty] | 0 | 0 | 0
2022-03-27 11:00 | 4.7909 | 46 | 2022-03-27 11:00 | 2.8733 | 46 | [8 empty] | 0 | 0 | 0
2022-03-27 12:00 | 4.788 | 45 | 2022-03-27 12:00 | 2.8712 | 45 | [8 empty] | 0 | 0 | 0
2022-03-27 13:00 | 4.786 | 45 | 2022-03-27 13:00 | 2.8698 | 45 | [8 empty] | 0 | 0 | 0
2022-03-27 14:00 | 4.7751 | 46 | 2022-03-27 14:00 | 2.8622 | 46 | [8 empty] | 0 | 0 | 0
2022-03-27 15:00 | 4.7928 | 45 | 2022-03-27 15:00 | 2.8747 | 45 | [8 empty] | 0 | 0 | 0
2022-03-27 16:00 | 4.7584 | 43 | 2022-03-27 16:00 | 2.8507 | 43 | [8 empty] | 0 | 0 | 0
2022-03-27 17:00 | 4.783 | 42 | 2022-03-27 17:00 | 2.8677 | 42 | [8 empty] | 0 | 0 | 0
2022-03-27 18:00 | 4.8115 | 39 | 2022-03-27 18:00 | 2.8882 | 39 | [8 empty] | 0 | 0 | 0
2022-03-27 19:00 | 4.8331 | 38 | 2022-03-27 19:00 | 2.9044 | 38 | [8 empty] | 0 | 0 | 0
2022-03-27 20:00 | 4.8262 | 37 | 2022-03-27 20:00 | 2.8992 | 37 | [8 empty] | 0 | 0 | 0
2022-03-27 21:00 | 4.8017 | 37 | 2022-03-27 21:00 | 2.881 | 37 | [8 empty] | 0 | 0 | 0
2022-03-27 22:00 | 4.8007 | 35 | 2022-03-27 22:00 | 2.8803 | 35 | [8 empty] | 0 | 0 | 0
2022-03-27 23:00 | 4.8213 | 33 | 2022-03-27 23:00 | 2.8955 | 33 | [8 empty] | 0 | 0 | 0
2022-03-28 | 4.8496 | 32 | 2022-03-28 | 2.9172 | 32 | [8 empty] | 0 | 0 | 0
2022-03-28 01:00 | 4.8555 | 29 | 2022-03-28 01:00 | 2.9219 | 29 | [8 empty] | 0 | 0 | 0
2022-03-28 02:00 | 4.8701 | 27 | 2022-03-28 02:00 | 2.9336 | 27 | [8 empty] | 0 | 0 | 0
2022-03-28 03:00 | 4.9031 | 26 | 2022-03-28 03:00 | 2.961 | 26 | [8 empty] | 0 | 0 | 0
2022-03-28 04:00 | 4.8867 | 25 | 2022-03-28 04:00 | 2.9471 | 25 | [8 empty] | 0 | 0 | 0
2022-03-28 05:00 | 4.9128 | 24 | 2022-03-28 05:00 | 2.9694 | 24 | [8 empty] | 0 | 0 | 0
2022-03-28 06:00 | 12.0351 | 23 | 2022-03-28 06:00 | 4.0959 | 23
2022-03-28 07:00 | 12.0351 | 23 | 2022-03-28 07:00 | 4.0959 | 23
2022-03-28 08:00 | 12.0351 | 25 | 2022-03-28 08:00 | 4.0959 | 25
2022-03-28 09:00 | 12.0351 | 26 | 2022-03-28 09:00 | 4.0959 | 26
2022-03-28 10:00 | 12.0351 | 28 | 2022-03-28 10:00 | 4.0959 | 28
2022-03-28 11:00 | 12.0351 | 31 | 2022-03-28 11:00 | 4.0959 | 31
2022-03-28 12:00 | 12.0351 | 32 | 2022-03-28 12:00 | 4.0959 | 32
2022-03-28 13:00 | 12.0351 | 32 | 2022-03-28 13:00 | 4.0959 | 32
2022-03-28 14:00 | 12.0351 | 33 | 2022-03-28 14:00 | 4.0959 | 33
2022-03-28 15:00 | 12.0351 | 32 | 2022-03-28 15:00 | 4.0959 | 32
2022-03-28 16:00 | 12.0351 | 32 | 2022-03-28 16:00 | 4.0959 | 32
2022-03-28 17:00 | 9.411 | 31 | 2022-03-28 17:00 | 4.0959 | 31
2022-03-28 18:00 | 4.6163 | 30 | 2022-03-28 18:00 | 2.7648 | 30
2022-03-28 19:00 | 4.6133 | 28 | 2022-03-28 19:00 | 2.7632 | 28
2022-03-28 20:00 | 4.6283 | 27 | 2022-03-28 20:00 | 2.7713 | 27
2022-03-28 21:00 | 4.6253 | 26 | 2022-03-28 21:00 | 2.7697 | 26
2022-03-28 22:00 | 4.6583 | 25 | 2022-03-28 22:00 | 2.7882 | 25
2022-03-28 23:00 | 4.6881 | 24 | 2022-03-28 23:00 | 2.8058 | 24
2022-03-29 | 4.7288 | 24 | 2022-03-29 | 2.8311 | 24
2022-03-29 01:00 | 4.7919 | 24 | 2022-03-29 01:00 | 2.874 | 24
2022-03-29 02:00 | 4.8867 | 24 | 2022-03-29 02:00 | 2.9471 | 24
2022-03-29 03:00 | 4.9128 | 25 | 2022-03-29 03:00 | 2.9694 | 25
2022-03-29 04:00 | 4.9525 | 25 | 2022-03-29 04:00 | 3.0049 | 25
2022-03-29 05:00 | 4.9293 | 25 | 2022-03-29 05:00 | 2.9839 | 25
2022-03-29 06:00 | 12.0351 | 25 | 2022-03-29 06:00 | 4.0959 | 25
2022-03-29 07:00 | 12.0351 | 25 | 2022-03-29 07:00 | 4.0959 | 25
2022-03-29 08:00 | 12.0351 | 27 | 2022-03-29 08:00 | 4.0959 | 27
2022-03-29 09:00 | 12.0351 | 29 | 2022-03-29 09:00 | 4.0959 | 29
2022-03-29 10:00 | 12.0351 | 31 | 2022-03-29 10:00 | 4.0959 | 31
2022-03-29 11:00 | 12.0351 | 34 | 2022-03-29 11:00 | 4.0959 | 34
2022-03-29 12:00 | 12.0351 | 36 | 2022-03-29 12:00 | 4.0959 | 36
2022-03-29 13:00 | 12.0351 | 36 | 2022-03-29 13:00 | 4.0959 | 36
2022-03-29 14:00 | 12.0351 | 37 | 2022-03-29 14:00 | 4.0959 | 37
2022-03-29 15:00 | 12.0351 | 35 | 2022-03-29 15:00 | 4.0959 | 35
2022-03-29 16:00 | 12.0351 | 37 | 2022-03-29 16:00 | 4.0959 | 37
2022-03-29 17:00 | 12.0351 | 38 | 2022-03-29 17:00 | 4.0959 | 38
2022-03-29 18:00 | 9.7974 | 38 | 2022-03-29 18:00 | 4.0959 | 38
2022-03-29 19:00 | 4.8145 | 36 | 2022-03-29 19:00 | 2.8904 | 36
2022-03-29 20:00 | 4.7948 | 35 | 2022-03-29 20:00 | 2.8761 | 35
2022-03-29 21:00 | 4.8301 | 34 | 2022-03-29 21:00 | 2.9022 | 34
2022-03-29 22:00 | 4.8516 | 34 | 2022-03-29 22:00 | 2.9188 | 34
2022-03-29 23:00 | 4.8584 | 34 | 2022-03-29 23:00 | 2.9242 | 34
2022-03-30 | 4.8701 | 32 | 2022-03-30 | 2.9336 | 32
2022-03-30 01:00 | 4.9254 | 32 | 2022-03-30 01:00 | 2.9804 | 32
2022-03-30 02:00 | 4.9437 | 31 | 2022-03-30 02:00 | 2.9969 | 31
2022-03-30 03:00 | 4.9351 | 30 | 2022-03-30 03:00 | 2.9891 | 30
2022-03-30 04:00 | 4.9457 | 29 | 2022-03-30 04:00 | 2.9987 | 29
2022-03-30 05:00 | 4.9244 | 28 | 2022-03-30 05:00 | 2.9796 | 28
2022-03-30 06:00 | 12.0351 | 29 | 2022-03-30 06:00 | 4.0959 | 29
2022-03-30 07:00 | 12.0351 | 29 | 2022-03-30 07:00 | 4.0959 | 29
2022-03-30 08:00 | 12.0351 | 32 | 2022-03-30 08:00 | 4.0959 | 32
2022-03-30 09:00 | 12.0351 | 35 | 2022-03-30 09:00 | 4.0959 | 35
2022-03-30 10:00 | 12.0351 | 37 | 2022-03-30 10:00 | 4.0959 | 37
2022-03-30 11:00 | 12.0351 | 39 | 2022-03-30 11:00 | 4.0959 | 39
2022-03-30 12:00 | 12.0351 | 40 | 2022-03-30 12:00 | 4.0959 | 40
2022-03-30 13:00 | 12.0351 | 40 | 2022-03-30 13:00 | 4.0959 | 40
2022-03-30 14:00 | 12.0351 | 42 | 2022-03-30 14:00 | 4.0959 | 42
2022-03-30 15:00 | 12.0351 | 41 | 2022-03-30 15:00 | 4.0959 | 41
2022-03-30 16:00 | 12.0351 | 42 | 2022-03-30 16:00 | 4.0959 | 42
2022-03-30 17:00 | 12.0351 | 41 | 2022-03-30 17:00 | 4.0959 | 41
2022-03-30 18:00 | 12.0351 | 41 | 2022-03-30 18:00 | 4.0959 | 41
2022-03-30 19:00 | 12.0351 | 40 | 2022-03-30 19:00 | 4.0959 | 40
2022-03-30 20:00 | 8.5305 | 41 | 2022-03-30 20:00 | 4.0959 | 41
2022-03-30 21:00 | 4.3605 | 41 | 2022-03-30 21:00 | 2.6526 | 41
2022-03-30 22:00 | 4.7899 | 42 | 2022-03-30 22:00 | 2.8726 | 42
2022-03-30 23:00 | 4.8017 | 42 | 2022-03-30 23:00 | 2.881 | 42
2022-03-31 | 4.8652 | 43 | 2022-03-31 | 2.9296 | 43
2022-03-31 01:00 | 4.8759 | 44 | 2022-03-31 01:00 | 2.9383 | 44
2022-03-31 02:00 | 4.8682 | 45 | 2022-03-31 02:00 | 2.932 | 45
2022-03-31 03:00 | 4.8944 | 46 | 2022-03-31 03:00 | 2.9536 | 46
2022-03-31 04:00 | 4.9264 | 46 | 2022-03-31 04:00 | 2.9813 | 46
2022-03-31 05:00 | 4.9206 | 47 | 2022-03-31 05:00 | 2.9762 | 47
2022-03-31 06:00 | 12.0351 | 47 | 2022-03-31 06:00 | 4.0959 | 47
2022-03-31 07:00 | 12.0351 | 47 | 2022-03-31 07:00 | 4.0959 | 47
2022-03-31 08:00 | 12.0351 | 48 | 2022-03-31 08:00 | 4.0959 | 48
2022-03-31 09:00 | 12.0351 | 52 | 2022-03-31 09:00 | 4.0959 | 52
2022-03-31 10:00 | 12.0351 | 56 | 2022-03-31 10:00 | 4.0959 | 56
2022-03-31 11:00 | 12.0351 | 54 | 2022-03-31 11:00 | 4.0959 | 54
2022-03-31 12:00 | 12.0351 | 55 | 2022-03-31 12:00 | 4.0959 | 55
2022-03-31 13:00 | 12.0351 | 54 | 2022-03-31 13:00 | 4.0959 | 54
2022-03-31 14:00 | 12.0351 | 55 | 2022-03-31 14:00 | 4.0959 | 55
2022-03-31 15:00 | 12.0351 | 54 | 2022-03-31 15:00 | 4.0959 | 54
2022-03-31 16:00 | 12.0351 | 54 | 2022-03-31 16:00 | 4.0959 | 54
2022-03-31 17:00 | 8.6689 | 53 | 2022-03-31 17:00 | 4.0959 | 53
2022-03-31 18:00 | 4.6662 | 53 | 2022-03-31 18:00 | 2.7928 | 53
2022-03-31 19:00 | 4.698 | 52 | 2022-03-31 19:00 | 2.8118 | 52
2022-03-31 20:00 | 4.6722 | 53 | 2022-03-31 20:00 | 2.7963 | 53
2022-03-31 21:00 | 4.6842 | 54 | 2022-03-31 21:00 | 2.8034 | 54
2022-03-31 22:00 | 4.6891 | 56 | 2022-03-31 22:00 | 2.8064 | 56
2022-03-31 23:00 | 4.7919 | 55 | 2022-03-31 23:00 | 2.874 | 55
2022-04-01 | 4.8203 | 54 | 2022-04-01 | 2.8948 | 54
2022-04-01 01:00 | 4.8711 | 52 | 2022-04-01 01:00 | 2.9344 | 52
2022-04-01 02:00 | 4.835 | 51 | 2022-04-01 02:00 | 2.9059 | 51
2022-04-01 03:00 | 4.837 | 49 | 2022-04-01 03:00 | 2.9074 | 49
2022-04-01 04:00 | 4.8604 | 56 | 2022-04-01 04:00 | 2.9257 | 56
2022-04-01 05:00 | 4.8818 | 59 | 2022-04-01 05:00 | 2.9431 | 59
2022-04-01 06:00 | 4.9303 | 57 | 2022-04-01 06:00 | 2.9848 | 57
2022-04-01 07:00 | 4.8555 | 54 | 2022-04-01 07:00 | 2.9219 | 54
2022-04-01 08:00 | 4.8154 | 53 | 2022-04-01 08:00 | 2.8911 | 53
2022-04-01 09:00 | 4.8174 | 52 | 2022-04-01 09:00 | 2.8926 | 52
2022-04-01 10:00 | 4.7357 | 53 | 2022-04-01 10:00 | 2.8356 | 53
2022-04-01 11:00 | 4.6692 | 54 | 2022-04-01 11:00 | 2.7945 | 54
2022-04-01 12:00 | 4.6662 | 56 | 2022-04-01 12:00 | 2.7928 | 56
2022-04-01 13:00 | 4.7258 | 56 | 2022-04-01 13:00 | 2.8292 | 56
2022-04-01 14:00 | 4.7238 | 56 | 2022-04-01 14:00 | 2.828 | 56
2022-04-01 15:00 | 4.6553 | 55 | 2022-04-01 15:00 | 2.7864 | 55
2022-04-01 16:00 | 4.6831 | 54 | 2022-04-01 16:00 | 2.8028 | 54
2022-04-01 17:00 | 4.7623 | 51 | 2022-04-01 17:00 | 2.8534 | 51
2022-04-01 18:00 | 3.925 | 50 | 2022-04-01 18:00 | 2.5429 | 50
2022-04-01 19:00 | 0.8851 | 48 | 2022-04-01 19:00 | 0.81227 | 48
2022-04-01 20:00 | 0.89983 | 46 | 2022-04-01 20:00 | 0.82753 | 46
2022-04-01 21:00 | 0.8988 | 46 | 2022-04-01 21:00 | 0.82646 | 46
2022-04-01 22:00 | 0.86635 | 45 | 2022-04-01 22:00 | 0.79299 | 45
2022-04-01 23:00 | 0.87127 | 45 | 2022-04-01 23:00 | 0.79804 | 45
2022-04-02 | 0.88903 | 44 | 2022-04-02 | 0.81634 | 44
2022-04-02 01:00 | 0.88903 | 43 | 2022-04-02 01:00 | 0.81634 | 43
2022-04-02 02:00 | 0.88999 | 43 | 2022-04-02 02:00 | 0.81733 | 43
2022-04-02 03:00 | 0.89784 | 42 | 2022-04-02 03:00 | 0.82546 | 42
2022-04-02 04:00 | 0.91053 | 41 | 2022-04-02 04:00 | 0.83867 | 41
2022-04-02 05:00 | 0.90861 | 40 | 2022-04-02 05:00 | 0.83667 | 40
2022-04-02 06:00 | 0.89096 | 40 | 2022-04-02 06:00 | 0.81833 | 40
2022-04-02 07:00 | 0.92223 | 39 | 2022-04-02 07:00 | 0.8509 | 39
2022-04-02 08:00 | 0.90175 | 39 | 2022-04-02 08:00 | 0.82953 | 39
2022-04-02 09:00 | 0.89983 | 42 | 2022-04-02 09:00 | 0.82753 | 42
2022-04-02 10:00 | 0.90175 | 42 | 2022-04-02 10:00 | 0.82953 | 42
2022-04-02 11:00 | 0.90663 | 44 | 2022-04-02 11:00 | 0.8346 | 44
2022-04-02 12:00 | 0.90957 | 46 | 2022-04-02 12:00 | 0.83767 | 46
2022-04-02 13:00 | 0.91053 | 48 | 2022-04-02 13:00 | 0.83867 | 48
2022-04-02 14:00 | 0.90175 | 50 | 2022-04-02 14:00 | 0.82953 | 50
2022-04-02 15:00 | 0.8988 | 51 | 2022-04-02 15:00 | 0.82646 | 51
2022-04-02 16:00 | 0.89983 | 52 | 2022-04-02 16:00 | 0.82753 | 52
2022-04-02 17:00 | 0.89784 | 51 | 2022-04-02 17:00 | 0.82546 | 51
2022-04-02 18:00 | 0.89983 | 51 | 2022-04-02 18:00 | 0.82753 | 51
2022-04-02 19:00 | 0.888 | 45 | 2022-04-02 19:00 | 0.81527 | 45
2022-04-02 20:00 | 0.87819 | 43 | 2022-04-02 20:00 | 0.80515 | 43
2022-04-02 21:00 | 0.8703 | 43 | 2022-04-02 21:00 | 0.79704 | 43
2022-04-02 22:00 | 0.89295 | 42 | 2022-04-02 22:00 | 0.8204 | 42
2022-04-02 23:00 | 0.88013 | 43 | 2022-04-02 23:00 | 0.80715 | 43
2022-04-03 | 0.888 | 43 | 2022-04-03 | 0.81527 | 43
2022-04-03 01:00 | 0.87722 | 43 | 2022-04-03 01:00 | 0.80416 | 43
2022-04-03 02:00 | 0.87916 | 41 | 2022-04-03 02:00 | 0.80615 | 41
2022-04-03 03:00 | 0.88903 | 39 | 2022-04-03 03:00 | 0.81634 | 39
2022-04-03 04:00 | 0.88606 | 41 | 2022-04-03 04:00 | 0.81327 | 41
2022-04-03 05:00 | 0.8851 | 41 | 2022-04-03 05:00 | 0.81227 | 41
2022-04-03 06:00 | 0.89392 | 41 | 2022-04-03 06:00 | 0.8214 | 41
2022-04-03 07:00 | 0.89392 | 40 | 2022-04-03 07:00 | 0.8214 | 40
2022-04-03 08:00 | 0.90175 | 43 | 2022-04-03 08:00 | 0.82953 | 43
2022-04-03 09:00 | 0.87819 | 45 | 2022-04-03 09:00 | 0.80515 | 45
2022-04-03 10:00 | 0.87619 | 45 | 2022-04-03 10:00 | 0.80309 | 45
2022-04-03 11:00 | 0.85941 | 46 | 2022-04-03 11:00 | 0.78589 | 46
2022-04-03 12:00 | 0.86434 | 44 | 2022-04-03 12:00 | 0.79093 | 44
2022-04-03 13:00 | 0.88213 | 44 | 2022-04-03 13:00 | 0.80921 | 44
2022-04-03 14:00 | 0.88903 | 44 | 2022-04-03 14:00 | 0.81634 | 44
2022-04-03 15:00 | 0.90079 | 45 | 2022-04-03 15:00 | 0.82853 | 45
2022-04-03 16:00 | 0.89192 | 45 | 2022-04-03 16:00 | 0.81933 | 45
2022-04-03 17:00 | 0.8851 | 46 | 2022-04-03 17:00 | 0.81227 | 46
2022-04-03 18:00 | 0.90175 | 45 | 2022-04-03 18:00 | 0.82953 | 45
2022-04-03 19:00 | 0.90861 | 45 | 2022-04-03 19:00 | 0.83667 | 45
2022-04-03 20:00 | 0.90175 | 46 | 2022-04-03 20:00 | 0.82953 | 46
2022-04-03 21:00 | 0.91348 | 45 | 2022-04-03 21:00 | 0.84175 | 45
2022-04-03 22:00 | 0.89488 | 44 | 2022-04-03 22:00 | 0.8224 | 44
2022-04-03 23:00 | 0.87619 | 42 | 2022-04-03 23:00 | 0.80309 | 42
2022-04-04 | 0.89585 | 41 | 2022-04-04 | 0.8234 | 41
2022-04-04 01:00 | 0.88013 | 40 | 2022-04-04 01:00 | 0.80715 | 40
2022-04-04 02:00 | 0.90374 | 40 | 2022-04-04 02:00 | 0.8316 | 40
2022-04-04 03:00 | 0.89192 | 40 | 2022-04-04 03:00 | 0.81933 | 40
2022-04-04 04:00 | 0.89983 | 40 | 2022-04-04 04:00 | 0.82753 | 40
2022-04-04 05:00 | 0.91444 | 40 | 2022-04-04 05:00 | 0.84275 | 40
2022-04-04 06:00 | 12.0351 | 39 | 2022-04-04 06:00 | 4.0959 | 39
2022-04-04 07:00 | 12.0351 | 40 | 2022-04-04 07:00 | 4.0959 | 40
2022-04-04 08:00 | 12.0351 | 43 | 2022-04-04 08:00 | 4.0959 | 43
2022-04-04 09:00 | 12.0351 | 45 | 2022-04-04 09:00 | 4.0959 | 45
2022-04-04 10:00 | 12.0351 | 47 | 2022-04-04 10:00 | 4.0959 | 47
2022-04-04 11:00 | 12.0351 | 50 | 2022-04-04 11:00 | 4.0959 | 50
2022-04-04 12:00 | 12.0351 | 51 | 2022-04-04 12:00 | 4.0959 | 51
2022-04-04 13:00 | 12.0351 | 52 | 2022-04-04 13:00 | 4.0959 | 52
2022-04-04 14:00 | 12.0351 | 53 | 2022-04-04 14:00 | 4.0959 | 53
2022-04-04 15:00 | 12.0351 | 54 | 2022-04-04 15:00 | 4.0959 | 54
2022-04-04 16:00 | 12.0351 | 54 | 2022-04-04 16:00 | 4.0959 | 54
2022-04-04 17:00 | 0.8831 | 53 | 2022-04-04 17:00 | 0.81021 | 53
2022-04-04 18:00 | 0.8851 | 52 | 2022-04-04 18:00 | 0.81227 | 52
2022-04-04 19:00 | 0.86927 | 51 | 2022-04-04 19:00 | 0.79598 | 51
2022-04-04 20:00 | 0.88013 | 51 | 2022-04-04 20:00 | 0.80715 | 51
2022-04-04 21:00 | 0.88999 | 50 | 2022-04-04 21:00 | 0.81733 | 50
2022-04-04 22:00 | 0.89392 | 50 | 2022-04-04 22:00 | 0.8214 | 50
2022-04-04 23:00 | 0.87328 | 48 | 2022-04-04 23:00 | 0.8001 | 48
2022-04-05 | 0.8831 | 46 | 2022-04-05 | 0.81021 | 46
2022-04-05 01:00 | 0.87819 | 46 | 2022-04-05 01:00 | 0.80515 | 46
2022-04-05 02:00 | 0.88606 | 43 | 2022-04-05 02:00 | 0.81327 | 43
2022-04-05 03:00 | 0.91936 | 39 | 2022-04-05 03:00 | 0.84789 | 39
2022-04-05 04:00 | 0.91156 | 41 | 2022-04-05 04:00 | 0.83974 | 41
2022-04-05 05:00 | 0.92714 | 40 | 2022-04-05 05:00 | 0.85605 | 40
2022-04-05 06:00 | 12.0351 | 43 | 2022-04-05 06:00 | 4.0959 | 43
2022-04-05 07:00 | 12.0351 | 42 | 2022-04-05 07:00 | 4.0959 | 42
2022-04-05 08:00 | 12.0351 | 45 | 2022-04-05 08:00 | 4.0959 | 45
2022-04-05 09:00 | 12.0351 | 46 | 2022-04-05 09:00 | 4.0959 | 46
2022-04-05 10:00 | 12.0351 | 50 | 2022-04-05 10:00 | 4.0959 | 50
2022-04-05 11:00 | 12.0351 | 51 | 2022-04-05 11:00 | 4.0959 | 51
2022-04-05 12:00 | 12.0351 | 52 | 2022-04-05 12:00 | 4.0959 | 52
2022-04-05 13:00 | 12.0351 | 52 | 2022-04-05 13:00 | 4.0959 | 52
2022-04-05 14:00 | 12.0351 | 51 | 2022-04-05 14:00 | 4.0959 | 51
2022-04-05 15:00 | 12.0351 | 51 | 2022-04-05 15:00 | 4.0959 | 51
2022-04-05 16:00 | 12.0351 | 51 | 2022-04-05 16:00 | 4.0959 | 51
2022-04-05 17:00 | 0.89392 | 50 | 2022-04-05 17:00 | 0.8214 | 50
2022-04-05 18:00 | 0.9047 | 48 | 2022-04-05 18:00 | 0.8326 | 48
2022-04-05 19:00 | 0.91053 | 47 | 2022-04-05 19:00 | 0.83867 | 47
2022-04-05 20:00 | 0.90567 | 47 | 2022-04-05 20:00 | 0.8336 | 47
2022-04-05 21:00 | 0.90765 | 47 | 2022-04-05 21:00 | 0.83567 | 47
2022-04-05 22:00 | 0.91156 | 47 | 2022-04-05 22:00 | 0.83974 | 47
2022-04-05 23:00 | 0.90861 | 47 | 2022-04-05 23:00 | 0.83667 | 47
2022-04-06 | 0.91348 | 47 | 2022-04-06 | 0.84175 | 47
2022-04-06 01:00 | 0.92516 | 47 | 2022-04-06 01:00 | 0.85398 | 47
2022-04-06 02:00 | 0.9242 | 47 | 2022-04-06 02:00 | 0.85297 | 47
2022-04-06 03:00 | 0.92127 | 47 | 2022-04-06 03:00 | 0.8499 | 47
2022-04-06 04:00 | 0.95621 | 47 | 2022-04-06 04:00 | 0.88674 | 47
2022-04-06 05:00 | 0.94265 | 48 | 2022-04-06 05:00 | 0.87239 | 48
2022-04-06 06:00 | 12.0351 | 49 | 2022-04-06 06:00 | 4.0959 | 49
2022-04-06 07:00 | 12.0351 | 50 | 2022-04-06 07:00 | 4.0959 | 50
2022-04-06 08:00 | 12.0351 | 48 | 2022-04-06 08:00 | 4.0959 | 48
2022-04-06 09:00 | 12.0351 | 48 | 2022-04-06 09:00 | 4.0959 | 48
2022-04-06 10:00 | 8.9556 | 47 | 2022-04-06 10:00 | 4.0959 | 47
2022-04-06 11:00 | 12.0351 | 49 | 2022-04-06 11:00 | 4.0959 | 49
2022-04-06 12:00 | 12.0351 | 50 | 2022-04-06 12:00 | 4.0959 | 50
2022-04-06 13:00 | 12.0351 | 52 | 2022-04-06 13:00 | 4.0959 | 52
2022-04-06 14:00 | 12.0351 | 51 | 2022-04-06 14:00 | 4.0959 | 51
2022-04-06 15:00 | 12.0351 | 51 | 2022-04-06 15:00 | 4.0959 | 51
2022-04-06 16:00 | 12.0351 | 53 | 2022-04-06 16:00 | 4.0959 | 53
2022-04-06 17:00 | 4.8565 | 53 | 2022-04-06 17:00 | 2.9226 | 53
2022-04-06 18:00 | 4.8359 | 52 | 2022-04-06 18:00 | 2.9066 | 52
2022-04-06 19:00 | 4.8798 | 51 | 2022-04-06 19:00 | 2.9415 | 51
2022-04-06 20:00 | 4.8516 | 51 | 2022-04-06 20:00 | 2.9188 | 51
2022-04-06 21:00 | 4.8203 | 50 | 2022-04-06 21:00 | 2.8948 | 50
2022-04-06 22:00 | 4.8604 | 50 | 2022-04-06 22:00 | 2.9257 | 50
2022-04-06 23:00 | 4.8623 | 50 | 2022-04-06 23:00 | 2.9273 | 50
2022-04-07 | 4.8759 | 49 | 2022-04-07 | 2.9383 | 49
2022-04-07 01:00 | 4.9544 | 49 | 2022-04-07 01:00 | 3.0067 | 49
2022-04-07 02:00 | 4.9341 | 48 | 2022-04-07 02:00 | 2.9882 | 48
2022-04-07 03:00 | 4.9264 | 47 | 2022-04-07 03:00 | 2.9813 | 47
2022-04-07 04:00 | 4.9428 | 47 | 2022-04-07 04:00 | 2.9961 | 47
2022-04-07 05:00 | 4.9736 | 47 | 2022-04-07 05:00 | 3.0248 | 47
2022-04-07 06:00 | 9.8675 | 46 | 2022-04-07 06:00 | 4.0959 | 46
2022-04-07 07:00 | 12.0351 | 45 | 2022-04-07 07:00 | 4.0959 | 45
2022-04-07 08:00 | 12.0351 | 46 | 2022-04-07 08:00 | 4.0959 | 46
2022-04-07 09:00 | 12.0351 | 46 | 2022-04-07 09:00 | 4.0959 | 46
2022-04-07 10:00 | 12.0351 | 46 | 2022-04-07 10:00 | 4.0959 | 46
2022-04-07 11:00 | 7.3804 | 46 | 2022-04-07 11:00 | 4.0959 | 46
2022-04-07 12:00 | 12.0351 | 47 | 2022-04-07 12:00 | 4.0959 | 47
2022-04-07 13:00 | 2.1307 | 48 | 2022-04-07 13:00 | 2.0525 | 48
2022-04-07 14:00 | 2.1467 | 48 | 2022-04-07 14:00 | 2.0632 | 48
2022-04-07 15:00 | 9.1665 | 48 | 2022-04-07 15:00 | 4.0959 | 48
2022-04-07 16:00 | 11.8351 | 49 | 2022-04-07 16:00 | 4.0959 | 49
2022-04-07 17:00 | 5.2705 | 48 | 2022-04-07 17:00 | 3.3899 | 48
2022-04-07 18:00 | 4.7535 | 49 | 2022-04-07 18:00 | 2.8474 | 49
2022-04-07 19:00 | 4.8085 | 49 | 2022-04-07 19:00 | 2.8861 | 49
2022-04-07 20:00 | 4.8066 | 49 | 2022-04-07 20:00 | 2.8846 | 49
2022-04-07 21:00 | 4.7909 | 49 | 2022-04-07 21:00 | 2.8733 | 49
2022-04-07 22:00 | 4.8331 | 51 | 2022-04-07 22:00 | 2.9044 | 51
2022-04-07 23:00 | 4.7811 | 51 | 2022-04-07 23:00 | 2.8663 | 51
2022-04-08 | 4.8623 | 51 | 2022-04-08 | 2.9273 | 51
2022-04-08 01:00 | 4.7238 | 51 | 2022-04-08 01:00 | 2.828 | 51
2022-04-08 02:00 | 4.7958 | 50 | 2022-04-08 02:00 | 2.8768 | 50
2022-04-08 03:00 | 4.8046 | 48 | 2022-04-08 03:00 | 2.8832 | 48
2022-04-08 04:00 | 4.8418 | 50 | 2022-04-08 04:00 | 2.9112 | 50
2022-04-08 05:00 | 4.8594 | 50 | 2022-04-08 05:00 | 2.925 | 50
2022-04-08 06:00 | 7.898 | 50 | 2022-04-08 06:00 | 4.0959 | 50
2022-04-08 07:00 | 12.0351 | 50 | 2022-04-08 07:00 | 4.0959 | 50
2022-04-08 08:00 | 12.0351 | 50 | 2022-04-08 08:00 | 4.0959 | 50
2022-04-08 09:00 | 12.0351 | 52 | 2022-04-08 09:00 | 4.0959 | 52
2022-04-08 10:00 | 12.0351 | 54 | 2022-04-08 10:00 | 4.0959 | 54
2022-04-08 11:00 | 12.0351 | 57 | 2022-04-08 11:00 | 4.0959 | 57
2022-04-08 12:00 | 12.0351 | 59 | 2022-04-08 12:00 | 4.0959 | 59
2022-04-08 13:00 | 12.0351 | 59 | 2022-04-08 13:00 | 4.0959 | 59
2022-04-08 14:00 | 12.0351 | 61 | 2022-04-08 14:00 | 4.0959 | 61
2022-04-08 15:00 | 12.0351 | 61 | 2022-04-08 15:00 | 4.0959 | 61
2022-04-08 16:00 | 12.0351 | 63 | 2022-04-08 16:00 | 4.0959 | 63
2022-04-08 17:00 | 9.4172 | 58 | 2022-04-08 17:00 | 4.0959 | 58
2022-04-08 18:00 | 4.7899 | 55 | 2022-04-08 18:00 | 2.8726 | 55
2022-04-08 19:00 | 4.785 | 53 | 2022-04-08 19:00 | 2.8691 | 53
2022-04-08 20:00 | 4.7702 | 49 | 2022-04-08 20:00 | 2.8588 | 49
2022-04-08 21:00 | 4.7958 | 48 | 2022-04-08 21:00 | 2.8768 | 48
2022-04-08 22:00 | 4.7623 | 50 | 2022-04-08 22:00 | 2.8534 | 50
2022-04-08 23:00 | 4.787 | 49 | 2022-04-08 23:00 | 2.8705 | 49
2022-04-09 | 4.787 | 49 | 2022-04-09 | 2.8705 | 49
2022-04-09 01:00 | 4.8262 | 49 | 2022-04-09 01:00 | 2.8992 | 49
2022-04-09 02:00 | 4.8672 | 50 | 2022-04-09 02:00 | 2.9312 | 50
2022-04-09 03:00 | 4.9003 | 48 | 2022-04-09 03:00 | 2.9586 | 48
2022-04-09 04:00 | 4.8992 | 50 | 2022-04-09 04:00 | 2.9577 | 50
2022-04-09 05:00 | 4.8935 | 50 | 2022-04-09 05:00 | 2.9528 | 50
2022-04-09 06:00 | 4.908 | 50 | 2022-04-09 06:00 | 2.9652 | 50
2022-04-09 07:00 | 4.8896 | 48 | 2022-04-09 07:00 | 2.9496 | 48
2022-04-09 08:00 | 4.8281 | 49 | 2022-04-09 08:00 | 2.9007 | 49
2022-04-09 09:00 | 4.7997 | 50 | 2022-04-09 09:00 | 2.8796 | 50
2022-04-09 10:00 | 4.7811 | 49 | 2022-04-09 10:00 | 2.8663 | 49
2022-04-09 11:00 | 4.785 | 51 | 2022-04-09 11:00 | 2.8691 | 51
2022-04-09 12:00 | 4.7742 | 54 | 2022-04-09 12:00 | 2.8615 | 54
2022-04-09 13:00 | 4.7988 | 55 | 2022-04-09 13:00 | 2.8789 | 55
2022-04-09 14:00 | 4.7889 | 53 | 2022-04-09 14:00 | 2.8719 | 53
2022-04-09 15:00 | 4.782 | 54 | 2022-04-09 15:00 | 2.867 | 54
2022-04-09 16:00 | 4.7623 | 56 | 2022-04-09 16:00 | 2.8534 | 56
2022-04-09 17:00 | 4.7218 | 55 | 2022-04-09 17:00 | 2.8267 | 55
2022-04-09 18:00 | 4.7258 | 55 | 2022-04-09 18:00 | 2.8292 | 55
2022-04-09 19:00 | 4.7297 | 53 | 2022-04-09 19:00 | 2.8317 | 53
2022-04-09 20:00 | 4.7238 | 52 | 2022-04-09 20:00 | 2.828 | 52
2022-04-09 21:00 | 4.6871 | 51 | 2022-04-09 21:00 | 2.8051 | 51
2022-04-09 22:00 | 4.6861 | 48 | 2022-04-09 22:00 | 2.8046 | 48
2022-04-09 23:00 | 4.7633 | 49 | 2022-04-09 23:00 | 2.854 | 49
2022-04-10 | 4.8954 | 49 | 2022-04-10 | 2.9545 | 49
2022-04-10 01:00 | 4.8896 | 49 | 2022-04-10 01:00 | 2.9496 | 49
2022-04-10 02:00 | 4.8818 | 49 | 2022-04-10 02:00 | 2.9431 | 49
2022-04-10 03:00 | 4.8905 | 48 | 2022-04-10 03:00 | 2.9504 | 48
2022-04-10 04:00 | 4.8857 | 47 | 2022-04-10 04:00 | 2.9463 | 47
2022-04-10 05:00 | 4.9022 | 46 | 2022-04-10 05:00 | 2.9602 | 46
2022-04-10 06:00 | 4.9099 | 45 | 2022-04-10 06:00 | 2.9669 | 45
2022-04-10 07:00 | 4.9611 | 45 | 2022-04-10 07:00 | 3.013 | 45
2022-04-10 08:00 | 4.964 | 44 | 2022-04-10 08:00 | 3.0157 | 44
2022-04-10 09:00 | 4.9457 | 46 | 2022-04-10 09:00 | 2.9987 | 46
2022-04-10 10:00 | 4.906 | 48 | 2022-04-10 10:00 | 2.9635 | 48
2022-04-10 11:00 | 4.8389 | 49 | 2022-04-10 11:00 | 2.9089 | 49
2022-04-10 12:00 | 4.7919 | 48 | 2022-04-10 12:00 | 2.874 | 48
2022-04-10 13:00 | 4.7889 | 48 | 2022-04-10 13:00 | 2.8719 | 48
2022-04-10 14:00 | 4.782 | 51 | 2022-04-10 14:00 | 2.867 | 51
2022-04-10 15:00 | 4.7693 | 49 | 2022-04-10 15:00 | 2.8581 | 49
2022-04-10 16:00 | 4.7771 | 50 | 2022-04-10 16:00 | 2.8636 | 50
2022-04-10 17:00 | 4.782 | 52 | 2022-04-10 17:00 | 2.867 | 52
2022-04-10 18:00 | 4.7938 | 49 | 2022-04-10 18:00 | 2.8754 | 49
2022-04-10 19:00 | 4.8232 | 47 | 2022-04-10 19:00 | 2.897 | 47
2022-04-10 20:00 | 4.8115 | 47 | 2022-04-10 20:00 | 2.8882 | 47
2022-04-10 21:00 | 4.7928 | 46 | 2022-04-10 21:00 | 2.8747 | 46
2022-04-10 22:00 | 4.8398 | 46 | 2022-04-10 22:00 | 2.9096 | 46
2022-04-10 23:00 | 4.835 | 45 | 2022-04-10 23:00 | 2.9059 | 45
2022-04-11 | 4.8652 | 44 | 2022-04-11 | 2.9296 | 44
2022-04-11 01:00 | 4.8847 | 43 | 2022-04-11 01:00 | 2.9455 | 43
2022-04-11 02:00 | 4.8992 | 42 | 2022-04-11 02:00 | 2.9577 | 42
2022-04-11 03:00 | 4.9206 | 42 | 2022-04-11 03:00 | 2.9762 | 42
2022-04-11 04:00 | 4.9679 | 41.7 | 2022-04-11 04:00 | 3.0193 | 41.7
2022-04-11 05:00 | 4.9707 | 41 | 2022-04-11 05:00 | 3.022 | 41
2022-04-11 06:00 | 9.7511 | 40 | 2022-04-11 06:00 | 4.0959 | 40
2022-04-11 07:00 | 12.0351 | 41 | 2022-04-11 07:00 | 4.0959 | 41
2022-04-11 08:00 | 12.0351 | 44 | 2022-04-11 08:00 | 4.0959 | 44
2022-04-11 09:00 | 12.0351 | 46 | 2022-04-11 09:00 | 4.0959 | 46
2022-04-11 10:00 | 12.0351 | 48 | 2022-04-11 10:00 | 4.0959 | 48
2022-04-11 11:00 | 12.0351 | 50 | 2022-04-11 11:00 | 4.0959 | 50
2022-04-11 12:00 | 12.0351 | 51 | 2022-04-11 12:00 | 4.0959 | 51
2022-04-11 13:00 | 12.0351 | 52 | 2022-04-11 13:00 | 4.0959 | 52
2022-04-11 14:00 | 12.0351 | 54 | 2022-04-11 14:00 | 4.0959 | 54
2022-04-11 15:00 | 12.0351 | 53 | 2022-04-11 15:00 | 4.0959 | 53
2022-04-11 16:00 | 12.0351 | 53 | 2022-04-11 16:00 | 4.0959 | 53
2022-04-11 17:00 | 8.4223 | 49 | 2022-04-11 17:00 | 4.0959 | 49
2022-04-11 18:00 | 4.6053 | 49 | 2022-04-11 18:00 | 2.759 | 49
2022-04-11 19:00 | 4.908 | 48 | 2022-04-11 19:00 | 2.9652 | 48
2022-04-11 20:00 | 4.9254 | 47 | 2022-04-11 20:00 | 2.9804 | 47
2022-04-11 21:00 | 4.9408 | 48 | 2022-04-11 21:00 | 2.9943 | 48
2022-04-11 22:00 | 4.9109 | 48 | 2022-04-11 22:00 | 2.9677 | 48
2022-04-11 23:00 | 4.9003 | 50 | 2022-04-11 23:00 | 2.9586 | 50
2022-04-12 | 4.9051 | 48 | 2022-04-12 | 2.9627 | 48
2022-04-12 01:00 | 4.8613 | 48 | 2022-04-12 01:00 | 2.9265 | 48
2022-04-12 02:00 | 4.8594 | 48 | 2022-04-12 02:00 | 2.925 | 48
2022-04-12 03:00 | 4.8818 | 48 | 2022-04-12 03:00 | 2.9431 | 48
2022-04-12 04:00 | 4.874 | 48 | 2022-04-12 04:00 | 2.9367 | 48
2022-04-12 05:00 | 4.9293 | 47 | 2022-04-12 05:00 | 2.9839 | 47
2022-04-12 06:00 | 4.9322 | 48 | 2022-04-12 06:00 | 2.9865 | 48
2022-04-12 07:00 | 4.6473 | 48 | 2022-04-12 07:00 | 2.7819 | 48
2022-04-12 08:00 | 4.6543 | 49 | 2022-04-12 08:00 | 2.7859 | 49
2022-04-12 09:00 | 4.6453 | 52 | 2022-04-12 09:00 | 2.7808 | 52
2022-04-12 10:00 | 4.6224 | 52 | 2022-04-12 10:00 | 2.7681 | 52
2022-04-12 11:00 | 4.6093 | 52 | 2022-04-12 11:00 | 2.7611 | 52
2022-04-12 12:00 | 4.6093 | 59 | 2022-04-12 12:00 | 2.7611 | 59
2022-04-12 13:00 | 4.5692 | 63 | 2022-04-12 13:00 | 2.7405 | 63
2022-04-12 14:00 | 4.5783 | 66 | 2022-04-12 14:00 | 2.745 | 66
2022-04-12 15:00 | 4.5732 | 68 | 2022-04-12 15:00 | 2.7425 | 68
2022-04-12 16:00 | 4.5783 | 70 | 2022-04-12 16:00 | 2.745 | 70
2022-04-12 17:00 | 4.6523 | 66 | 2022-04-12 17:00 | 2.7847 | 66
2022-04-12 18:00 | 4.5813 | 68 | 2022-04-12 18:00 | 2.7465 | 68
2022-04-12 19:00 | 4.8448 | 61 | 2022-04-12 19:00 | 2.9134 | 61
2022-04-12 20:00 | 4.873 | 55 | 2022-04-12 20:00 | 2.9359 | 55
2022-04-12 21:00 | 4.8301 | 54 | 2022-04-12 21:00 | 2.9022 | 54
2022-04-12 22:00 | 4.874 | 54 | 2022-04-12 22:00 | 2.9367 | 54
2022-04-12 23:00 | 4.8232 | 51 | 2022-04-12 23:00 | 2.897 | 51
2022-04-13 | 4.8643 | 51 | 2022-04-13 | 2.9288 | 51
2022-04-13 01:00 | 4.908 | 49 | 2022-04-13 01:00 | 2.9652 | 49
2022-04-13 02:00 | 4.8905 | 48 | 2022-04-13 02:00 | 2.9504 | 48
2022-04-13 03:00 | 4.937 | 47 | 2022-04-13 03:00 | 2.9908 | 47
2022-04-13 04:00 | 4.8983 | 48 | 2022-04-13 04:00 | 2.9569 | 48
2022-04-13 05:00 | 4.9128 | 48 | 2022-04-13 05:00 | 2.9694 | 48
2022-04-13 06:00 | 4.9351 | 50 | 2022-04-13 06:00 | 2.9891 | 50
2022-04-13 07:00 | 4.702 | 51 | 2022-04-13 07:00 | 2.8142 | 51
2022-04-13 08:00 | 4.6543 | 53 | 2022-04-13 08:00 | 2.7859 | 53
2022-04-13 09:00 | 4.6293 | 60 | 2022-04-13 09:00 | 2.7719 | 60
2022-04-13 10:00 | 4.5601 | 60 | 2022-04-13 10:00 | 2.736 | 60
2022-04-13 11:00 | 4.5149 | 62 | 2022-04-13 11:00 | 2.7146 | 62
2022-04-13 12:00 | 4.5088 | 63 | 2022-04-13 12:00 | 2.7119 | 63
2022-04-13 13:00 | 4.4663 | 64 | 2022-04-13 13:00 | 2.6934 | 64
2022-04-13 14:00 | 4.5088 | 59 | 2022-04-13 14:00 | 2.7119 | 59
2022-04-13 15:00 | 4.5098 | 59 | 2022-04-13 15:00 | 2.7123 | 59
2022-04-13 16:00 | 3.2035 | 59 | 2022-04-13 16:00 | 2.4421 | 59
2022-04-13 17:00 | 0.86434 | 59 | 2022-04-13 17:00 | 0.79093 | 59
2022-04-13 18:00 | 0.82855 | 58 | 2022-04-13 18:00 | 0.75456 | 58
2022-04-13 19:00 | 0.80545 | 58 | 2022-04-13 19:00 | 0.73139 | 58
2022-04-13 20:00 | 0.79837 | 57 | 2022-04-13 20:00 | 0.72434 | 57
2022-04-13 21:00 | 0.80849 | 57 | 2022-04-13 21:00 | 0.73442 | 57
2022-04-13 22:00 | 0.81046 | 56 | 2022-04-13 22:00 | 0.7364 | 56
2022-04-13 23:00 | 0.80043 | 56 | 2022-04-13 23:00 | 0.72638 | 56
2022-04-14 | 0.80142 | 57 | 2022-04-14 | 0.72737 | 57
2022-04-14 01:00 | 0.80644 | 55 | 2022-04-14 01:00 | 0.73238 | 55
2022-04-14 02:00 | 0.8185 | 54 | 2022-04-14 02:00 | 0.74445 | 54
2022-04-14 03:00 | 0.82356 | 53 | 2022-04-14 03:00 | 0.74954 | 53
2022-04-14 04:00 | 0.82756 | 53 | 2022-04-14 04:00 | 0.75357 | 53
2022-04-14 05:00 | 0.8385 | 53 | 2022-04-14 05:00 | 0.76462 | 53
2022-04-14 06:00 | 0.84548 | 54 | 2022-04-14 06:00 | 0.7717 | 54
2022-04-14 07:00 | 0.83254 | 54 | 2022-04-14 07:00 | 0.75859 | 54
2022-04-14 08:00 | 0.83451 | 58 | 2022-04-14 08:00 | 0.76058 | 58
2022-04-14 09:00 | 0.83451 | 62 | 2022-04-14 09:00 | 0.76058 | 62
2022-04-14 10:00 | 0.82855 | 62 | 2022-04-14 10:00 | 0.75456 | 62
2022-04-14 11:00 | 0.83451 | 65 | 2022-04-14 11:00 | 0.76058 | 65
2022-04-14 12:00 | 0.83451 | 67 | 2022-04-14 12:00 | 0.76058 | 67
2022-04-14 13:00 | 0.8185 | 67 | 2022-04-14 13:00 | 0.74445 | 67
2022-04-14 14:00 | 0.8385 | 67 | 2022-04-14 14:00 | 0.76462 | 67
2022-04-14 15:00 | 0.84052 | 68 | 2022-04-14 15:00 | 0.76667 | 68
2022-04-14 16:00 | 0.84052 | 66 | 2022-04-14 16:00 | 0.76667 | 66
2022-04-14 17:00 | 0.85245 | 66 | 2022-04-14 17:00 | 0.77879 | 66
2022-04-14 18:00 | 1.3322 | 62 | 2022-04-14 18:00 | 1.3029 | 62
2022-04-14 19:00 | 1.3267 | 68 | 2022-04-14 19:00 | 1.2968 | 68
2022-04-14 20:00 | 1.333 | 63 | 2022-04-14 20:00 | 1.3039 | 63
2022-04-14 21:00 | 1.3195 | 62 | 2022-04-14 21:00 | 1.2887 | 62
2022-04-14 22:00 | 1.3003 | 63 | 2022-04-14 22:00 | 1.2672 | 63
2022-04-14 23:00 | 1.3121 | 62 | 2022-04-14 23:00 | 1.2804 | 62
2022-04-15 | 1.3076 | 61 | 2022-04-15 | 1.2753 | 61
2022-04-15 01:00 | 1.3322 | 60 | 2022-04-15 01:00 | 1.3029 | 60
2022-04-15 02:00 | 1.3195 | 57 | 2022-04-15 02:00 | 1.2887 | 57
2022-04-15 03:00 | 1.324 | 54 | 2022-04-15 03:00 | 1.2937 | 54
2022-04-15 04:00 | 1.3304 | 54 | 2022-04-15 04:00 | 1.3009 | 54
2022-04-15 05:00 | 1.3485 | 53 | 2022-04-15 05:00 | 1.3212 | 53
2022-04-15 06:00 | 1.3449 | 49 | 2022-04-15 06:00 | 1.3171 | 49
2022-04-15 07:00 | 1.3285 | 47 | 2022-04-15 07:00 | 1.2988 | 47
2022-04-15 08:00 | 1.3322 | 55 | 2022-04-15 08:00 | 1.3029 | 55
2022-04-15 09:00 | 1.3394 | 58 | 2022-04-15 09:00 | 1.311 | 58
2022-04-15 10:00 | 1.3131 | 62 | 2022-04-15 10:00 | 1.2815 | 62
2022-04-15 11:00 | 1.2821 | 63 | 2022-04-15 11:00 | 1.2467 | 63
2022-04-15 12:00 | 1.2803 | 65 | 2022-04-15 12:00 | 1.2446 | 65
2022-04-15 13:00 | 1.2584 | 64 | 2022-04-15 13:00 | 1.22 | 64
2022-04-15 14:00 | 1.2593 | 66 | 2022-04-15 14:00 | 1.221 | 66
2022-04-15 15:00 | 1.2547 | 64 | 2022-04-15 15:00 | 1.2159 | 64
2022-04-15 16:00 | 1.2703 | 61 | 2022-04-15 16:00 | 1.2334 | 61
2022-04-15 17:00 | 1.2812 | 59 | 2022-04-15 17:00 | 1.2457 | 59
2022-04-15 18:00 | 1.2547 | 58 | 2022-04-15 18:00 | 1.2159 | 58
2022-04-15 19:00 | 1.2529 | 55 | 2022-04-15 19:00 | 1.2138 | 55
2022-04-15 20:00 | 1.2547 | 53 | 2022-04-15 20:00 | 1.2159 | 53
2022-04-15 21:00 | 1.2602 | 54 | 2022-04-15 21:00 | 1.2221 | 54
2022-04-15 22:00 | 1.2519 | 54 | 2022-04-15 22:00 | 1.2128 | 54
2022-04-15 23:00 | 1.2648 | 52 | 2022-04-15 23:00 | 1.2272 | 52
2022-04-16 | 1.304 | 51 | 2022-04-16 | 1.2713 | 51
2022-04-16 01:00 | 1.3121 | 50 | 2022-04-16 01:00 | 1.2804 | 50
2022-04-16 02:00 | 1.3131 | 51 | 2022-04-16 02:00 | 1.2815 | 51
2022-04-16 03:00 | 1.3167 | 50 | 2022-04-16 03:00 | 1.2856 | 50
2022-04-16 04:00 | 1.3058 | 50 | 2022-04-16 04:00 | 1.2733 | 50
2022-04-16 05:00 | 1.304 | 50 | 2022-04-16 05:00 | 1.2713 | 50
2022-04-16 06:00 | 1.2867 | 51 | 2022-04-16 06:00 | 1.2518 | 51
2022-04-16 07:00 | 1.3276 | 51 | 2022-04-16 07:00 | 1.2978 | 51
2022-04-16 08:00 | 1.3012 | 53 | 2022-04-16 08:00 | 1.2682 | 53
2022-04-16 09:00 | 1.2976 | 55 | 2022-04-16 09:00 | 1.2641 | 55
2022-04-16 10:00 | 1.2885 | 57 | 2022-04-16 10:00 | 1.2539 | 57
2022-04-16 11:00 | 1.3003 | 56 | 2022-04-16 11:00 | 1.2672 | 56
2022-04-16 12:00 | 1.2885 | 57 | 2022-04-16 12:00 | 1.2539 | 57
2022-04-16 13:00 | 1.2684 | 61 | 2022-04-16 13:00 | 1.2313 | 61
2022-04-16 14:00 | 1.2766 | 59 | 2022-04-16 14:00 | 1.2405 | 59
2022-04-16 15:00 | 1.2785 | 59 | 2022-04-16 15:00 | 1.2426 | 59
2022-04-16 16:00 | 1.2547 | 57 | 2022-04-16 16:00 | 1.2159 | 57
2022-04-16 17:00 | 1.2958 | 57 | 2022-04-16 17:00 | 1.2621 | 57
2022-04-16 18:00 | 1.2967 | 55 | 2022-04-16 18:00 | 1.2631 | 55
2022-04-16 19:00 | 1.2994 | 54 | 2022-04-16 19:00 | 1.2662 | 54
2022-04-16 20:00 | 1.2703 | 56 | 2022-04-16 20:00 | 1.2334 | 56
2022-04-16 21:00 | 1.2939 | 53 | 2022-04-16 21:00 | 1.26 | 53
2022-04-16 22:00 | 1.2939 | 50 | 2022-04-16 22:00 | 1.26 | 50
2022-04-16 23:00 | 1.314 | 46 | 2022-04-16 23:00 | 1.2825 | 46
2022-04-17 | 1.3022 | 45 | 2022-04-17 | 1.2692 | 45
2022-04-17 01:00 | 1.3012 | 45 | 2022-04-17 01:00 | 1.2682 | 45
2022-04-17 02:00 | 1.2976 | 45 | 2022-04-17 02:00 | 1.2641 | 45
2022-04-17 03:00 | 1.3067 | 45 | 2022-04-17 03:00 | 1.2743 | 45
2022-04-17 04:00 | 1.3185 | 45 | 2022-04-17 04:00 | 1.2876 | 45
2022-04-17 05:00 | 1.3222 | 44 | 2022-04-17 05:00 | 1.2917 | 44
2022-04-17 06:00 | 1.3485 | 43 | 2022-04-17 06:00 | 1.3212 | 43
2022-04-17 07:00 | 1.3503 | 43 | 2022-04-17 07:00 | 1.3232 | 43
2022-04-17 08:00 | 1.3521 | 44 | 2022-04-17 08:00 | 1.3252 | 44
2022-04-17 09:00 | 1.3558 | 46 | 2022-04-17 09:00 | 1.3293 | 46
2022-04-17 10:00 | 1.3413 | 47 | 2022-04-17 10:00 | 1.3131 | 47
2022-04-17 11:00 | 1.3394 | 48 | 2022-04-17 11:00 | 1.311 | 48
2022-04-17 12:00 | 1.3621 | 49 | 2022-04-17 12:00 | 1.3364 | 49
2022-04-17 13:00 | 1.3222 | 49 | 2022-04-17 13:00 | 1.2917 | 49
2022-04-17 14:00 | 1.3204 | 51 | 2022-04-17 14:00 | 1.2897 | 51
2022-04-17 15:00 | 1.3349 | 48 | 2022-04-17 15:00 | 1.3059 | 48
2022-04-17 16:00 | 1.3067 | 49 | 2022-04-17 16:00 | 1.2743 | 49
2022-04-17 17:00 | 1.3385 | 49 | 2022-04-17 17:00 | 1.31 | 49
2022-04-17 18:00 | 1.3185 | 48 | 2022-04-17 18:00 | 1.2876 | 48
2022-04-17 19:00 | 1.3249 | 48 | 2022-04-17 19:00 | 1.2947 | 48
2022-04-17 20:00 | 1.3285 | 46 | 2022-04-17 20:00 | 1.2988 | 46
2022-04-17 21:00 | 1.3349 | 45 | 2022-04-17 21:00 | 1.3059 | 45
2022-04-17 22:00 | 1.3195 | 45 | 2022-04-17 22:00 | 1.2887 | 45
2022-04-17 23:00 | 1.3121 | 43 | 2022-04-17 23:00 | 1.2804 | 43
2022-04-18 | 1.3349 | 41 | 2022-04-18 | 1.3059 | 41
2022-04-18 01:00 | 1.2967 | 40 | 2022-04-18 01:00 | 1.2631 | 40
2022-04-18 02:00 | 1.3085 | 41 | 2022-04-18 02:00 | 1.2763 | 41
2022-04-18 03:00 | 1.2976 | 39 | 2022-04-18 03:00 | 1.2641 | 39
2022-04-18 04:00 | 1.3085 | 38 | 2022-04-18 04:00 | 1.2763 | 38
2022-04-18 05:00 | 1.3149 | 38 | 2022-04-18 05:00 | 1.2835 | 38
2022-04-18 06:00 | 7.3086 | 38 | 2022-04-18 06:00 | 4.0959 | 38
2022-04-18 07:00 | 9.2086 | 40 | 2022-04-18 07:00 | 4.0959 | 40
2022-04-18 08:00 | 9.1712 | 44 | 2022-04-18 08:00 | 4.0959 | 44
2022-04-18 09:00 | 9.0564 | 47 | 2022-04-18 09:00 | 4.0959 | 47
2022-04-18 10:00 | 8.9711 | 50 | 2022-04-18 10:00 | 4.0959 | 50
2022-04-18 11:00 | 8.9237 | 50 | 2022-04-18 11:00 | 4.0959 | 50
2022-04-18 12:00 | 8.8919 | 50 | 2022-04-18 12:00 | 4.0959 | 50
2022-04-18 13:00 | 8.8533 | 50 | 2022-04-18 13:00 | 4.0959 | 50
2022-04-18 14:00 | 8.8932 | 48 | 2022-04-18 14:00 | 4.0959 | 48
2022-04-18 15:00 | 8.929 | 48 | 2022-04-18 15:00 | 4.0959 | 48
2022-04-18 16:00 | 8.9303 | 47 | 2022-04-18 16:00 | 4.0959 | 47
2022-04-18 17:00 | 6.1446 | 47 | 2022-04-18 17:00 | 4.0959 | 47
2022-04-18 18:00 | 3.4573 | 46 | 2022-04-18 18:00 | 2.4771 | 46
2022-04-18 19:00 | 3.4614 | 46 | 2022-04-18 19:00 | 2.4776 | 46
2022-04-18 20:00 | 3.4687 | 46 | 2022-04-18 20:00 | 2.4786 | 46
2022-04-18 21:00 | 3.4937 | 46 | 2022-04-18 21:00 | 2.4817 | 46
2022-04-18 22:00 | 3.4759 | 44 | 2022-04-18 22:00 | 2.4795 | 44
2022-04-18 23:00 | 3.4915 | 42 | 2022-04-18 23:00 | 2.4815 | 42
2022-04-19 | 3.4843 | 44 | 2022-04-19 | 2.4806 | 44
2022-04-19 01:00 | 3.5291 | 45 | 2022-04-19 01:00 | 2.4862 | 45
2022-04-19 02:00 | 3.5228 | 46 | 2022-04-19 02:00 | 2.4854 | 46
2022-04-19 03:00 | 3.4687 | 48 | 2022-04-19 03:00 | 2.4786 | 48
2022-04-19 04:00 | 3.4999 | 49 | 2022-04-19 04:00 | 2.4825 | 49
2022-04-19 05:00 | 3.5113 | 47 | 2022-04-19 05:00 | 2.484 | 47
2022-04-19 06:00 | 8.0566 | 44 | 2022-04-19 06:00 | 4.0959 | 44
2022-04-19 07:00 | 12.0351 | 41 | 2022-04-19 07:00 | 4.0959 | 41
2022-04-19 08:00 | 12.0351 | 43 | 2022-04-19 08:00 | 4.0959 | 43
2022-04-19 09:00 | 12.0351 | 43 | 2022-04-19 09:00 | 4.0959 | 43
2022-04-19 10:00 | 12.0351 | 45 | 2022-04-19 10:00 | 4.0959 | 45
2022-04-19 11:00 | 12.0351 | 45 | 2022-04-19 11:00 | 4.0959 | 45
2022-04-19 12:00 | 12.0351 | 46 | 2022-04-19 12:00 | 4.0959 | 46
2022-04-19 13:00 | 12.0351 | 48 | 2022-04-19 13:00 | 4.0959 | 48
2022-04-19 14:00 | 12.0351 | 49 | 2022-04-19 14:00 | 4.0959 | 49
2022-04-19 15:00 | 12.0351 | 50 | 2022-04-19 15:00 | 4.0959 | 50
2022-04-19 16:00 | 12.0351 | 50 | 2022-04-19 16:00 | 4.0959 | 50
2022-04-19 17:00 | 12.0351 | 51 | 2022-04-19 17:00 | 4.0959 | 51
2022-04-19 18:00 | 12.0351 | 50 | 2022-04-19 18:00 | 4.0959 | 50
2022-04-19 19:00 | 4.936 | 48 | 2022-04-19 19:00 | 2.9899 | 48
2022-04-19 20:00 | 4.9177 | 44 | 2022-04-19 20:00 | 2.9736 | 44
2022-04-19 21:00 | 4.9099 | 45 | 2022-04-19 21:00 | 2.9669 | 45
2022-04-19 22:00 | 4.8905 | 45 | 2022-04-19 22:00 | 2.9504 | 45
2022-04-19 23:00 | 4.9496 | 44 | 2022-04-19 23:00 | 3.0022 | 44
2022-04-20 | 4.9928 | 44 | 2022-04-20 | 3.0435 | 44
2022-04-20 01:00 | 5.0158 | 43 | 2022-04-20 01:00 | 3.0666 | 43
2022-04-20 02:00 | 5.151 | 43 | 2022-04-20 02:00 | 3.2215 | 43
2022-04-20 03:00 | 5.135 | 42 | 2022-04-20 03:00 | 3.2014 | 42
2022-04-20 04:00 | 5.1771 | 42 | 2022-04-20 04:00 | 3.2556 | 42
2022-04-20 05:00 | 5.1743 | 42 | 2022-04-20 05:00 | 3.2518 | 42
2022-04-20 06:00 | 12.0351 | 41 | 2022-04-20 06:00 | 4.0959 | 41
2022-04-20 07:00 | 12.0351 | 43 | 2022-04-20 07:00 | 4.0959 | 43
2022-04-20 08:00 | 12.0351 | 45 | 2022-04-20 08:00 | 4.0959 | 45
2022-04-20 09:00 | 12.0351 | 48 | 2022-04-20 09:00 | 4.0959 | 48
2022-04-20 10:00 | 12.0351 | 50 | 2022-04-20 10:00 | 4.0959 | 50
2022-04-20 11:00 | 12.0351 | 51 | 2022-04-20 11:00 | 4.0959 | 51
2022-04-20 12:00 | 12.0351 | 54 | 2022-04-20 12:00 | 4.0959 | 54
2022-04-20 13:00 | 12.0351 | 55 | 2022-04-20 13:00 | 4.0959 | 55
2022-04-20 14:00 | 12.0351 | 56 | 2022-04-20 14:00 | 4.0959 | 56
2022-04-20 15:00 | 12.0351 | 57 | 2022-04-20 15:00 | 4.0959 | 57
2022-04-20 16:00 | 12.0351 | 59 | 2022-04-20 16:00 | 4.0959 | 59
2022-04-20 17:00 | 12.0351 | 58 | 2022-04-20 17:00 | 4.0959 | 58
2022-04-20 18:00 | 11.9457 | 51 | 2022-04-20 18:00 | 4.0959 | 51
2022-04-20 19:00 | 4.9186 | 49 | 2022-04-20 19:00 | 2.9744 | 49
2022-04-20 20:00 | 4.9215 | 48 | 2022-04-20 20:00 | 2.977 | 48
2022-04-20 21:00 | 4.938 | 47 | 2022-04-20 21:00 | 2.9917 | 47
2022-04-20 22:00 | 4.9196 | 47 | 2022-04-20 22:00 | 2.9753 | 47
2022-04-20 23:00 | 4.9688 | 46 | 2022-04-20 23:00 | 3.0202 | 46
2022-04-21 | 4.987 | 43 | 2022-04-21 | 3.0378 | 43
2022-04-21 01:00 | 5.0965 | 42 | 2022-04-21 01:00 | 3.1549 | 42
2022-04-21 02:00 | 5.1219 | 41 | 2022-04-21 02:00 | 3.1853 | 41
2022-04-21 03:00 | 5.1219 | 40 | 2022-04-21 03:00 | 3.1853 | 40
2022-04-21 04:00 | 5.1715 | 40 | 2022-04-21 04:00 | 3.2481 | 40
2022-04-21 05:00 | 5.1837 | 41 | 2022-04-21 05:00 | 3.2643 | 41
2022-04-21 06:00 | 7.8452 | 43 | 2022-04-21 06:00 | 4.0959 | 43
2022-04-21 07:00 | 12.0351 | 45 | 2022-04-21 07:00 | 4.0959 | 45
2022-04-21 08:00 | 12.0351 | 48 | 2022-04-21 08:00 | 4.0959 | 48
2022-04-21 09:00 | 12.0351 | 51 | 2022-04-21 09:00 | 4.0959 | 51
2022-04-21 10:00 | 12.0351 | 52 | 2022-04-21 10:00 | 4.0959 | 52
2022-04-21 11:00 | 12.0351 | 53 | 2022-04-21 11:00 | 4.0959 | 53
2022-04-21 12:00 | 12.0351 | 55 | 2022-04-21 12:00 | 4.0959 | 55
2022-04-21 13:00 | 12.0351 | 54 | 2022-04-21 13:00 | 4.0959 | 54
2022-04-21 14:00 | 12.0351 | 55 | 2022-04-21 14:00 | 4.0959 | 55
2022-04-21 15:00 | 12.0351 | 53 | 2022-04-21 15:00 | 4.0959 | 53
2022-04-21 16:00 | 12.0351 | 51 | 2022-04-21 16:00 | 4.0959 | 51
2022-04-21 17:00 | 12.0351 | 51 | 2022-04-21 17:00 | 4.0959 | 51
2022-04-21 18:00 | 12.0351 | 50 | 2022-04-21 18:00 | 4.0959 | 50
2022-04-21 19:00 | 4.9419 | 50 | 2022-04-21 19:00 | 2.9952 | 50
2022-04-21 20:00 | 4.9225 | 51 | 2022-04-21 20:00 | 2.9779 | 51
2022-04-21 21:00 | 4.9457 | 51 | 2022-04-21 21:00 | 2.9987 | 51
2022-04-21 22:00 | 4.8954 | 51 | 2022-04-21 22:00 | 2.9545 | 51
2022-04-21 23:00 | 4.8643 | 51 | 2022-04-21 23:00 | 2.9288 | 51
2022-04-22 | 4.8467 | 48 | 2022-04-22 | 2.9149 | 48
2022-04-22 01:00 | 4.8808 | 47 | 2022-04-22 01:00 | 2.9423 | 47
2022-04-22 02:00 | 4.9158 | 46 | 2022-04-22 02:00 | 2.9719 | 46
2022-04-22 03:00 | 4.9399 | 47 | 2022-04-22 03:00 | 2.9934 | 47
2022-04-22 04:00 | 4.9736 | 46 | 2022-04-22 04:00 | 3.0248 | 46
2022-04-22 05:00 | 5.0291 | 46 | 2022-04-22 05:00 | 3.0804 | 46
2022-04-22 06:00 | 12.0351 | 48 | 2022-04-22 06:00 | 4.0959 | 48
2022-04-22 07:00 | 12.0351 | 51 | 2022-04-22 07:00 | 4.0959 | 51
2022-04-22 08:00 | 12.0351 | 57 | 2022-04-22 08:00 | 4.0959 | 57
2022-04-22 09:00 | 12.0351 | 61 | 2022-04-22 09:00 | 4.0959 | 61
2022-04-22 10:00 | 12.0351 | 63 | 2022-04-22 10:00 | 4.0959 | 63
2022-04-22 11:00 | 12.0351 | 65 | 2022-04-22 11:00 | 4.0959 | 65
2022-04-22 12:00 | 12.0351 | 66 | 2022-04-22 12:00 | 4.0959 | 66
2022-04-22 13:00 | 12.0351 | 68 | 2022-04-22 13:00 | 4.0959 | 68
2022-04-22 14:00 | 12.0351 | 69 | 2022-04-22 14:00 | 4.0959 | 69
2022-04-22 15:00 | 12.0351 | 69 | 2022-04-22 15:00 | 4.0959 | 69
2022-04-22 16:00 | 12.0351 | 69 | 2022-04-22 16:00 | 4.0959 | 69
2022-04-22 17:00 | 12.0351 | 69 | 2022-04-22 17:00 | 4.0959 | 69
2022-04-22 18:00 | 8.1323 | 68 | 2022-04-22 18:00 | 4.0959 | 68
2022-04-22 19:00 | 4.8983 | 66 | 2022-04-22 19:00 | 2.9569 | 66
2022-04-22 20:00 | 4.8604 | 63 | 2022-04-22 20:00 | 2.9257 | 63
2022-04-22 21:00 | 4.907 | 62 | 2022-04-22 21:00 | 2.9644 | 62
2022-04-22 22:00 | 4.9351 | 61 | 2022-04-22 22:00 | 2.9891 | 61
2022-04-22 23:00 | 4.9235 | 58 | 2022-04-22 23:00 | 2.9787 | 58
2022-04-23 | 4.9322 | 55 | 2022-04-23 | 2.9865 | 55
2022-04-23 01:00 | 5.0548 | 52 | 2022-04-23 01:00 | 3.1079 | 52
2022-04-23 02:00 | 5.0339 | 52 | 2022-04-23 02:00 | 3.0855 | 52
2022-04-23 03:00 | 5.0415 | 50 | 2022-04-23 03:00 | 3.0935 | 50
2022-04-23 04:00 | 5.0462 | 50 | 2022-04-23 04:00 | 3.0986 | 50
2022-04-23 05:00 | 5.087 | 50 | 2022-04-23 05:00 | 3.144 | 50
2022-04-23 06:00 | 5.0861 | 50 | 2022-04-23 06:00 | 3.1429 | 50
2022-04-23 07:00 | 5.0965 | 51 | 2022-04-23 07:00 | 3.1549 | 51
2022-04-23 08:00 | 5.0614 | 51 | 2022-04-23 08:00 | 3.1152 | 51
2022-04-23 09:00 | 5.0377 | 53 | 2022-04-23 09:00 | 3.0895 | 53
2022-04-23 10:00 | 5.012 | 57 | 2022-04-23 10:00 | 3.0627 | 57
2022-04-23 11:00 | 5.0081 | 59 | 2022-04-23 11:00 | 3.0588 | 59
2022-04-23 12:00 | 5.0091 | 58 | 2022-04-23 12:00 | 3.0598 | 58
2022-04-23 13:00 | 4.9563 | 59 | 2022-04-23 13:00 | 3.0085 | 59
2022-04-23 14:00 | 4.9765 | 58 | 2022-04-23 14:00 | 3.0276 | 58
2022-04-23 15:00 | 4.9823 | 57 | 2022-04-23 15:00 | 3.0332 | 57
2022-04-23 16:00 | 4.9679 | 57 | 2022-04-23 16:00 | 3.0193 | 57
2022-04-23 17:00 | 4.9592 | 56 | 2022-04-23 17:00 | 3.0112 | 56
2022-04-23 18:00 | 4.9823 | 54 | 2022-04-23 18:00 | 3.0332 | 54
2022-04-23 19:00 | 4.9602 | 52 | 2022-04-23 19:00 | 3.0121 | 52
2022-04-23 20:00 | 4.9688 | 52 | 2022-04-23 20:00 | 3.0202 | 52
2022-04-23 21:00 | 5.0091 | 52 | 2022-04-23 21:00 | 3.0598 | 52
2022-04-23 22:00 | 5.0004 | 52 | 2022-04-23 22:00 | 3.0511 | 52
2022-04-23 23:00 | 5.0004 | 52 | 2022-04-23 23:00 | 3.0511 | 52
2022-04-24 | 5.0091 | 52 | 2022-04-24 | 3.0598 | 52
2022-04-24 01:00 | 5.0158 | 51 | 2022-04-24 01:00 | 3.0666 | 51
2022-04-24 02:00 | 5.0033 | 51 | 2022-04-24 02:00 | 3.054 | 51
2022-04-24 03:00 | 5.0196 | 50 | 2022-04-24 03:00 | 3.0705 | 50
2022-04-24 04:00 | 5.0253 | 50 | 2022-04-24 04:00 | 3.0764 | 50
2022-04-24 05:00 | 5.0167 | 50 | 2022-04-24 05:00 | 3.0676 | 50
2022-04-24 06:00 | 5.0253 | 48 | 2022-04-24 06:00 | 3.0764 | 48
2022-04-24 07:00 | 5.0301 | 50 | 2022-04-24 07:00 | 3.0814 | 50
2022-04-24 08:00 | 5.0415 | 55 | 2022-04-24 08:00 | 3.0935 | 55
2022-04-24 09:00 | 5.0405 | 59 | 2022-04-24 09:00 | 3.0925 | 59
2022-04-24 10:00 | 5.0329 | 56 | 2022-04-24 10:00 | 3.0844 | 56
2022-04-24 11:00 | 5.0148 | 56 | 2022-04-24 11:00 | 3.0656 | 56
2022-04-24 12:00 | 4.9437 | 56 | 2022-04-24 12:00 | 2.9969 | 56
2022-04-24 13:00 | 4.9956 | 53 | 2022-04-24 13:00 | 3.0463 | 53
2022-04-24 14:00 | 4.9679 | 54 | 2022-04-24 14:00 | 3.0193 | 54
2022-04-24 15:00 | 4.9389 | 54 | 2022-04-24 15:00 | 2.9926 | 54
2022-04-24 16:00 | 4.9525 | 53 | 2022-04-24 16:00 | 3.0049 | 53
2022-04-24 17:00 | 4.9928 | 52 | 2022-04-24 17:00 | 3.0435 | 52
2022-04-24 18:00 | 5.0014 | 50 | 2022-04-24 18:00 | 3.0521 | 50
2022-04-24 19:00 | 5.0033 | 49 | 2022-04-24 19:00 | 3.054 | 49
2022-04-24 20:00 | 4.9889 | 47 | 2022-04-24 20:00 | 3.0397 | 47
2022-04-24 21:00 | 4.9457 | 46 | 2022-04-24 21:00 | 2.9987 | 46
2022-04-24 22:00 | 4.9745 | 46 | 2022-04-24 22:00 | 3.0257 | 46
2022-04-24 23:00 | 4.9563 | 46 | 2022-04-24 23:00 | 3.0085 | 46
2022-04-25 | 4.9899 | 45 | 2022-04-25 | 3.0407 | 45
2022-04-25 01:00 | 5.0415 | 45 | 2022-04-25 01:00 | 3.0935 | 45
2022-04-25 02:00 | 5.0681 | 45 | 2022-04-25 02:00 | 3.1225 | 45
2022-04-25 03:00 | 5.0974 | 45 | 2022-04-25 03:00 | 3.156 | 45
2022-04-25 04:00 | 5.0993 | 46 | 2022-04-25 04:00 | 3.1582 | 46
2022-04-25 05:00 | 5.1144 | 45 | 2022-04-25 05:00 | 3.1762 | 45
2022-04-25 06:00 | 12.0351 | 44 | 2022-04-25 06:00 | 4.0959 | 44
2022-04-25 07:00 | 12.0351 | 46 | 2022-04-25 07:00 | 4.0959 | 46
2022-04-25 08:00 | 12.0351 | 49 | 2022-04-25 08:00 | 4.0959 | 49
2022-04-25 09:00 | 12.0351 | 52 | 2022-04-25 09:00 | 4.0959 | 52
2022-04-25 10:00 | 12.0351 | 54 | 2022-04-25 10:00 | 4.0959 | 54
2022-04-25 11:00 | 12.0351 | 55 | 2022-04-25 11:00 | 4.0959 | 55
2022-04-25 12:00 | 12.0351 | 54 | 2022-04-25 12:00 | 4.0959 | 54
2022-04-25 13:00 | 12.0351 | 54 | 2022-04-25 13:00 | 4.0959 | 54
2022-04-25 14:00 | 12.0351 | 54 | 2022-04-25 14:00 | 4.0959 | 54
2022-04-25 15:00 | 12.0351 | 54 | 2022-04-25 15:00 | 4.0959 | 54
2022-04-25 16:00 | 12.0351 | 53 | 2022-04-25 16:00 | 4.0959 | 53
2022-04-25 17:00 | 12.0351 | 54 | 2022-04-25 17:00 | 4.0959 | 54
2022-04-25 18:00 | 4.7683 | 53 | 2022-04-25 18:00 | 2.8575 | 53
2022-04-25 19:00 | 4.9399 | 51 | 2022-04-25 19:00 | 2.9934 | 51
2022-04-25 20:00 | 4.9186 | 51 | 2022-04-25 20:00 | 2.9744 | 51
2022-04-25 21:00 | 4.9138 | 50 | 2022-04-25 21:00 | 2.9702 | 50
2022-04-25 22:00 | 4.9861 | 51 | 2022-04-25 22:00 | 3.0369 | 51
2022-04-25 23:00 | 4.9602 | 50 | 2022-04-25 23:00 | 3.0121 | 50
2022-04-26 | 4.9515 | 51 | 2022-04-26 | 3.004 | 51
2022-04-26 01:00 | 5.0272 | 51 | 2022-04-26 01:00 | 3.0784 | 51
2022-04-26 02:00 | 5.0205 | 51 | 2022-04-26 02:00 | 3.0715 | 51
2022-04-26 03:00 | 5.0205 | 51 | 2022-04-26 03:00 | 3.0715 | 51
2022-04-26 04:00 | 5.0538 | 51 | 2022-04-26 04:00 | 3.1068 | 51
2022-04-26 05:00 | 5.0785 | 52 | 2022-04-26 05:00 | 3.1343 | 52
2022-04-26 06:00 | 5.0396 | 52 | 2022-04-26 06:00 | 3.0915 | 52
2022-04-26 07:00 | 4.8379 | 51 | 2022-04-26 07:00 | 2.9081 | 51
2022-04-26 08:00 | 4.7683 | 52 | 2022-04-26 08:00 | 2.8575 | 52
2022-04-26 09:00 | 4.7762 | 53 | 2022-04-26 09:00 | 2.8629 | 53
2022-04-26 10:00 | 4.7693 | 54 | 2022-04-26 10:00 | 2.8581 | 54
2022-04-26 11:00 | 4.7327 | 56 | 2022-04-26 11:00 | 2.8337 | 56
2022-04-26 12:00 | 4.704 | 58 | 2022-04-26 12:00 | 2.8155 | 58
2022-04-26 13:00 | 4.6602 | 59 | 2022-04-26 13:00 | 2.7893 | 59
2022-04-26 14:00 | 4.6792 | 59 | 2022-04-26 14:00 | 2.8004 | 59
2022-04-26 15:00 | 4.6593 | 58 | 2022-04-26 15:00 | 2.7887 | 58
2022-04-26 16:00 | 4.8905 | 57 | 2022-04-26 16:00 | 2.9504 | 57
2022-04-26 17:00 | 4.964 | 57 | 2022-04-26 17:00 | 3.0157 | 57
2022-04-26 18:00 | 2.9721 | 58 | 2022-04-26 18:00 | 2.4004 | 58
2022-04-26 19:00 | 0.91738 | 56 | 2022-04-26 19:00 | 0.84582 | 56
2022-04-26 20:00 | 0.93878 | 55 | 2022-04-26 20:00 | 0.8683 | 55
2022-04-26 21:00 | 0.92127 | 56 | 2022-04-26 21:00 | 0.8499 | 56
2022-04-26 22:00 | 0.92714 | 56 | 2022-04-26 22:00 | 0.85605 | 56
2022-04-26 23:00 | 0.90861 | 55 | 2022-04-26 23:00 | 0.83667 | 55
2022-04-27 | 0.91833 | 54 | 2022-04-27 | 0.84682 | 54
2022-04-27 01:00 | 0.92905 | 54 | 2022-04-27 01:00 | 0.85806 | 54
2022-04-27 02:00 | 0.9436 | 57 | 2022-04-27 02:00 | 0.87339 | 57
2022-04-27 03:00 | 0.95425 | 52 | 2022-04-27 03:00 | 0.88466 | 52
2022-04-27 04:00 | 0.94652 | 50 | 2022-04-27 04:00 | 0.87648 | 50
2022-04-27 05:00 | 0.96196 | 49 | 2022-04-27 05:00 | 0.89285 | 49
2022-04-27 06:00 | 0.95716 | 49 | 2022-04-27 06:00 | 0.88775 | 49
2022-04-27 07:00 | 0.93783 | 49 | 2022-04-27 07:00 | 0.8673 | 49
2022-04-27 08:00 | 0.93681 | 50 | 2022-04-27 08:00 | 0.86623 | 50
2022-04-27 09:00 | 0.8988 | 52 | 2022-04-27 09:00 | 0.82646 | 52
2022-04-27 10:00 | 0.89585 | 54 | 2022-04-27 10:00 | 0.8234 | 54
2022-04-27 11:00 | 0.90861 | 55 | 2022-04-27 11:00 | 0.83667 | 55
2022-04-27 12:00 | 0.89585 | 54 | 2022-04-27 12:00 | 0.8234 | 54
2022-04-27 13:00 | 0.88999 | 55 | 2022-04-27 13:00 | 0.81733 | 55
2022-04-27 14:00 | 0.89585 | 54 | 2022-04-27 14:00 | 0.8234 | 54
2022-04-27 15:00 | 0.88116 | 56 | 2022-04-27 15:00 | 0.80821 | 56
2022-04-27 16:00 | 0.89983 | 56 | 2022-04-27 16:00 | 0.82753 | 56
2022-04-27 17:00 | 0.91833 | 54 | 2022-04-27 17:00 | 0.84682 | 54
2022-04-27 18:00 | 0.91348 | 52 | 2022-04-27 18:00 | 0.84175 | 52
2022-04-27 19:00 | 2.4501 | 50 | 2022-04-27 19:00 | 2.2325 | 50
2022-04-27 20:00 | 2.8677 | 48 | 2022-04-27 20:00 | 2.3764 | 48
2022-04-27 21:00 | 2.8123 | 46 | 2022-04-27 21:00 | 2.362 | 46
2022-04-27 22:00 | 2.8304 | 44 | 2022-04-27 22:00 | 2.3669 | 44
2022-04-27 23:00 | 2.8636 | 43 | 2022-04-27 23:00 | 2.3754 | 43
2022-04-28 | 2.8606 | 42 | 2022-04-28 | 2.3746 | 42
2022-04-28 01:00 | 2.9081 | 41 | 2022-04-28 01:00 | 2.3861 | 41
2022-04-28 02:00 | 2.896 | 41 | 2022-04-28 02:00 | 2.3833 | 41
2022-04-28 03:00 | 2.9528 | 41 | 2022-04-28 03:00 | 2.3962 | 41
2022-04-28 04:00 | 2.9609 | 41 | 2022-04-28 04:00 | 2.398 | 41
2022-04-28 05:00 | 3.0046 | 41 | 2022-04-28 05:00 | 2.4071 | 41
2022-04-28 06:00 | 12.0351 | 40 | 2022-04-28 06:00 | 4.0959 | 40
2022-04-28 07:00 | 12.0351 | 41 | 2022-04-28 07:00 | 4.0959 | 41
2022-04-28 08:00 | 12.0351 | 43 | 2022-04-28 08:00 | 4.0959 | 43
2022-04-28 09:00 | 12.0351 | 44 | 2022-04-28 09:00 | 4.0959 | 44
2022-04-28 10:00 | 12.0351 | 47 | 2022-04-28 10:00 | 4.0959 | 47
2022-04-28 11:00 | 12.0351 | 50 | 2022-04-28 11:00 | 4.0959 | 50
2022-04-28 12:00 | 12.0351 | 52 | 2022-04-28 12:00 | 4.0959 | 52
2022-04-28 13:00 | 12.0351 | 54 | 2022-04-28 13:00 | 4.0959 | 54
2022-04-28 14:00 | 12.0351 | 57 | 2022-04-28 14:00 | 4.0959 | 57
2022-04-28 15:00 | 12.0351 | 57 | 2022-04-28 15:00 | 4.0959 | 57
2022-04-28 16:00 | 12.0351 | 57 | 2022-04-28 16:00 | 4.0959 | 57
2022-04-28 17:00 | 12.0351 | 57 | 2022-04-28 17:00 | 4.0959 | 57
2022-04-28 18:00 | 12.0351 | 56 | 2022-04-28 18:00 | 4.0959 | 56
2022-04-28 19:00 | 7.6958 | 54 | 2022-04-28 19:00 | 4.0959 | 54
2022-04-28 20:00 | 4.8973 | 52 | 2022-04-28 20:00 | 2.9561 | 52
2022-04-28 21:00 | 4.9051 | 50 | 2022-04-28 21:00 | 2.9627 | 50
2022-04-28 22:00 | 4.8779 | 48 | 2022-04-28 22:00 | 2.9399 | 48
2022-04-28 23:00 | 4.9051 | 47 | 2022-04-28 23:00 | 2.9627 | 47
2022-04-29 | 4.937 | 46 | 2022-04-29 | 2.9908 | 46
2022-04-29 01:00 | 4.963 | 45 | 2022-04-29 01:00 | 3.0148 | 45
2022-04-29 02:00 | 4.964 | 44 | 2022-04-29 02:00 | 3.0157 | 44
2022-04-29 03:00 | 4.9918 | 44 | 2022-04-29 03:00 | 3.0425 | 44
2022-04-29 04:00 | 5.01 | 43 | 2022-04-29 04:00 | 3.0607 | 43
2022-04-29 05:00 | 5.0586 | 42 | 2022-04-29 05:00 | 3.112 | 42
2022-04-29 06:00 | 12.0351 | 42 | 2022-04-29 06:00 | 4.0959 | 42
2022-04-29 07:00 | 12.0351 | 43 | 2022-04-29 07:00 | 4.0959 | 43
2022-04-29 08:00 | 12.0351 | 45 | 2022-04-29 08:00 | 4.0959 | 45
2022-04-29 09:00 | 12.0351 | 47 | 2022-04-29 09:00 | 4.0959 | 47
2022-04-29 10:00 | 12.0351 | 50 | 2022-04-29 10:00 | 4.0959 | 50
2022-04-29 11:00 | 12.0351 | 52 | 2022-04-29 11:00 | 4.0959 | 52
2022-04-29 12:00 | 12.0351 | 56 | 2022-04-29 12:00 | 4.0959 | 56
2022-04-29 13:00 | 12.0351 | 59 | 2022-04-29 13:00 | 4.0959 | 59
2022-04-29 14:00 | 12.0351 | 60 | 2022-04-29 14:00 | 4.0959 | 60
2022-04-29 15:00 | 12.0351 | 62 | 2022-04-29 15:00 | 4.0959 | 62
2022-04-29 16:00 | 12.0351 | 63 | 2022-04-29 16:00 | 4.0959 | 63
2022-04-29 17:00 | 9.8718 | 63 | 2022-04-29 17:00 | 4.0959 | 63
2022-04-29 18:00 | 4.6114 | 62 | 2022-04-29 18:00 | 2.7622 | 62
2022-04-29 19:00 | 4.8954 | 60 | 2022-04-29 19:00 | 2.9545 | 60
2022-04-29 20:00 | 4.8759 | 58 | 2022-04-29 20:00 | 2.9383 | 58
2022-04-29 21:00 | 4.9186 | 56 | 2022-04-29 21:00 | 2.9744 | 56
2022-04-29 22:00 | 4.9031 | 55 | 2022-04-29 22:00 | 2.961 | 55
2022-04-29 23:00 | 4.938 | 53 | 2022-04-29 23:00 | 2.9917 | 53
2022-04-30 | 4.9726 | 51 | 2022-04-30 | 3.0239 | 51
2022-04-30 01:00 | 5.0291 | 50 | 2022-04-30 01:00 | 3.0804 | 50
2022-04-30 02:00 | 5.0301 | 49 | 2022-04-30 02:00 | 3.0814 | 49
2022-04-30 03:00 | 5.0443 | 47 | 2022-04-30 03:00 | 3.0965 | 47
2022-04-30 04:00 | 5.0215 | 46 | 2022-04-30 04:00 | 3.0725 | 46
2022-04-30 05:00 | 5.0415 | 45 | 2022-04-30 05:00 | 3.0935 | 45
2022-04-30 06:00 | 5.0766 | 44 | 2022-04-30 06:00 | 3.1321 | 44
2022-04-30 07:00 | 5.0662 | 46 | 2022-04-30 07:00 | 3.1204 | 46
2022-04-30 08:00 | 5.0176 | 50 | 2022-04-30 08:00 | 3.0685 | 50
2022-04-30 09:00 | 5.032 | 53 | 2022-04-30 09:00 | 3.0834 | 53
2022-04-30 10:00 | 5.0043 | 55 | 2022-04-30 10:00 | 3.055 | 55
2022-04-30 11:00 | 4.9408 | 58 | 2022-04-30 11:00 | 2.9943 | 58
2022-04-30 12:00 | 4.9486 | 60 | 2022-04-30 12:00 | 3.0014 | 60
2022-04-30 13:00 | 4.9283 | 62 | 2022-04-30 13:00 | 2.983 | 62
2022-04-30 14:00 | 4.9389 | 61 | 2022-04-30 14:00 | 2.9926 | 61
2022-04-30 15:00 | 4.9351 | 64 | 2022-04-30 15:00 | 2.9891 | 64
2022-04-30 16:00 | 4.9496 | 66 | 2022-04-30 16:00 | 3.0022 | 66
2022-04-30 17:00 | 4.9341 | 59 | 2022-04-30 17:00 | 2.9882 | 59
2022-04-30 18:00 | 4.8924 | 55 | 2022-04-30 18:00 | 2.952 | 55
2022-04-30 19:00 | 4.965 | 53 | 2022-04-30 19:00 | 3.0166 | 53
2022-04-30 20:00 | 4.9668 | 51 | 2022-04-30 20:00 | 3.0184 | 51
2022-04-30 21:00 | 4.9947 | 51 | 2022-04-30 21:00 | 3.0454 | 51
2022-04-30 22:00 | 4.9813 | 50 | 2022-04-30 22:00 | 3.0322 | 50
2022-04-30 23:00 | 5.0071 | 47 | 2022-04-30 23:00 | 3.0578 | 47
2022-05-01 | 5.0186 | 46 | 2022-05-01 | 3.0695 | 46
2022-05-01 01:00 | 5.0358 | 45 | 2022-05-01 01:00 | 3.0874 | 45
2022-05-01 02:00 | 5.0158 | 46 | 2022-05-01 02:00 | 3.0666 | 46
2022-05-01 03:00 | 5.0138 | 44 | 2022-05-01 03:00 | 3.0646 | 44
2022-05-01 04:00 | 5.0955 | 47 | 2022-05-01 04:00 | 3.1538 | 47
2022-05-01 05:00 | 5.087 | 45 | 2022-05-01 05:00 | 3.144 | 45
2022-05-01 06:00 | 5.0794 | 42 | 2022-05-01 06:00 | 3.1353 | 42
2022-05-01 07:00 | 5.0946 | 45 | 2022-05-01 07:00 | 3.1527 | 45
2022-05-01 08:00 | 4.9351 | 51 | 2022-05-01 08:00 | 2.9891 | 51
2022-05-01 09:00 | 4.9293 | 57 | 2022-05-01 09:00 | 2.9839 | 57
2022-05-01 10:00 | 4.9341 | 61 | 2022-05-01 10:00 | 2.9882 | 61
2022-05-01 11:00 | 4.9419 | 60 | 2022-05-01 11:00 | 2.9952 | 60
2022-05-01 12:00 | 4.964 | 59 | 2022-05-01 12:00 | 3.0157 | 59
2022-05-01 13:00 | 4.9196 | 61 | 2022-05-01 13:00 | 2.9753 | 61
2022-05-01 14:00 | 4.9022 | 62 | 2022-05-01 14:00 | 2.9602 | 62
2022-05-01 15:00 | 4.9109 | 62 | 2022-05-01 15:00 | 2.9677 | 62
2022-05-01 16:00 | 4.9177 | 60 | 2022-05-01 16:00 | 2.9736 | 60
2022-05-01 17:00 | 4.9206 | 58 | 2022-05-01 17:00 | 2.9762 | 58
2022-05-01 18:00 | 4.9235 | 57 | 2022-05-01 18:00 | 2.9787 | 57
2022-05-01 19:00 | 4.9177 | 55 | 2022-05-01 19:00 | 2.9736 | 55
2022-05-01 20:00 | 4.9534 | 55 | 2022-05-01 20:00 | 3.0058 | 55
2022-05-01 21:00 | 4.9525 | 54 | 2022-05-01 21:00 | 3.0049 | 54
2022-05-01 22:00 | 4.9774 | 54 | 2022-05-01 22:00 | 3.0285 | 54
2022-05-01 23:00 | 4.9457 | 53 | 2022-05-01 23:00 | 2.9987 | 53
2022-05-02 | 5.0329 | 52 | 2022-05-02 | 3.0844 | 52
2022-05-02 01:00 | 5.0282 | 53 | 2022-05-02 01:00 | 3.0794 | 53
2022-05-02 02:00 | 5.0148 | 53 | 2022-05-02 02:00 | 3.0656 | 53
2022-05-02 03:00 | 5.0205 | 53 | 2022-05-02 03:00 | 3.0715 | 53
2022-05-02 04:00 | 4.9976 | 54 | 2022-05-02 04:00 | 3.0482 | 54
2022-05-02 05:00 | 5.0234 | 52 | 2022-05-02 05:00 | 3.0745 | 52
2022-05-02 06:00 | 5.0955 | 52 | 2022-05-02 06:00 | 3.1538 | 52
2022-05-02 07:00 | 4.8242 | 52 | 2022-05-02 07:00 | 2.8977 | 52
2022-05-02 08:00 | 4.8223 | 55 | 2022-05-02 08:00 | 2.8963 | 55
2022-05-02 09:00 | 4.7614 | 54 | 2022-05-02 09:00 | 2.8527 | 54
2022-05-02 10:00 | 4.7297 | 54 | 2022-05-02 10:00 | 2.8317 | 54
2022-05-02 11:00 | 4.7169 | 55 | 2022-05-02 11:00 | 2.8235 | 55
2022-05-02 12:00 | 4.7574 | 54 | 2022-05-02 12:00 | 2.8501 | 54
2022-05-02 13:00 | 4.9592 | 53 | 2022-05-02 13:00 | 3.0112 | 53
2022-05-02 14:00 | 4.9553 | 54 | 2022-05-02 14:00 | 3.0076 | 54
2022-05-02 15:00 | 4.9437 | 55 | 2022-05-02 15:00 | 2.9969 | 55
2022-05-02 16:00 | 4.9389 | 55 | 2022-05-02 16:00 | 2.9926 | 55
2022-05-02 17:00 | 5.0004 | 55 | 2022-05-02 17:00 | 3.0511 | 55
2022-05-02 18:00 | 5.0109 | 54 | 2022-05-02 18:00 | 3.0617 | 54
2022-05-02 19:00 | 5.0176 | 52 | 2022-05-02 19:00 | 3.0685 | 52
2022-05-02 20:00 | 5.0472 | 52 | 2022-05-02 20:00 | 3.0996 | 52
2022-05-02 21:00 | 5.0443 | 52 | 2022-05-02 21:00 | 3.0965 | 52
2022-05-02 22:00 | 5.0215 | 51 | 2022-05-02 22:00 | 3.0725 | 51
2022-05-02 23:00 | 4.9947 | 51 | 2022-05-02 23:00 | 3.0454 | 51
2022-05-03 | 5.0415 | 50 | 2022-05-03 | 3.0935 | 50
2022-05-03 01:00 | 5.0908 | 52 | 2022-05-03 01:00 | 3.1483 | 52
2022-05-03 02:00 | 5.0681 | 51 | 2022-05-03 02:00 | 3.1225 | 51
2022-05-03 03:00 | 5.0983 | 51 | 2022-05-03 03:00 | 3.1571 | 51
2022-05-03 04:00 | 5.1219 | 52 | 2022-05-03 04:00 | 3.1853 | 52
2022-05-03 05:00 | 5.1049 | 51 | 2022-05-03 05:00 | 3.1649 | 51
2022-05-03 06:00 | 5.1191 | 50 | 2022-05-03 06:00 | 3.1818 | 50
2022-05-03 07:00 | 4.8944 | 52 | 2022-05-03 07:00 | 2.9536 | 52
2022-05-03 08:00 | 4.8301 | 54 | 2022-05-03 08:00 | 2.9022 | 54
2022-05-03 09:00 | 4.7702 | 55 | 2022-05-03 09:00 | 2.8588 | 55
2022-05-03 10:00 | 4.7387 | 57 | 2022-05-03 10:00 | 2.8376 | 57
2022-05-03 11:00 | 4.7426 | 59 | 2022-05-03 11:00 | 2.8402 | 59
2022-05-03 12:00 | 4.7446 | 60 | 2022-05-03 12:00 | 2.8414 | 60
2022-05-03 13:00 | 4.6961 | 61 | 2022-05-03 13:00 | 2.8106 | 61
2022-05-03 14:00 | 4.7258 | 61 | 2022-05-03 14:00 | 2.8292 | 61
2022-05-03 15:00 | 4.6931 | 59 | 2022-05-03 15:00 | 2.8088 | 59
2022-05-03 16:00 | 4.6871 | 57 | 2022-05-03 16:00 | 2.8051 | 57
2022-05-03 17:00 | 4.7771 | 56 | 2022-05-03 17:00 | 2.8636 | 56
2022-05-03 18:00 | 4.7456 | 54 | 2022-05-03 18:00 | 2.8421 | 54
2022-05-03 19:00 | 5.0358 | 53 | 2022-05-03 19:00 | 3.0874 | 53
2022-05-03 20:00 | 5.0071 | 51 | 2022-05-03 20:00 | 3.0578 | 51
2022-05-03 21:00 | 4.963 | 51 | 2022-05-03 21:00 | 3.0148 | 51
2022-05-03 22:00 | 4.9312 | 51 | 2022-05-03 22:00 | 2.9856 | 51
2022-05-03 23:00 | 4.9563 | 50 | 2022-05-03 23:00 | 3.0085 | 50
2022-05-04 | 5.0301 | 49 | 2022-05-04 | 3.0814 | 49
2022-05-04 01:00 | 5.0234 | 49 | 2022-05-04 01:00 | 3.0745 | 49
2022-05-04 02:00 | 5.0672 | 49 | 2022-05-04 02:00 | 3.1215 | 49
2022-05-04 03:00 | 5.0785 | 49 | 2022-05-04 03:00 | 3.1343 | 49
2022-05-04 04:00 | 5.1238 | 49 | 2022-05-04 04:00 | 3.1875 | 49
2022-05-04 05:00 | 5.1125 | 49 | 2022-05-04 05:00 | 3.1739 | 49
2022-05-04 06:00 | 5.1304 | 50 | 2022-05-04 06:00 | 3.1956 | 50
2022-05-04 07:00 | 4.8808 | 50 | 2022-05-04 07:00 | 2.9423 | 50
2022-05-04 08:00 | 4.8448 | 51 | 2022-05-04 08:00 | 2.9134 | 51
2022-05-04 09:00 | 4.7545 | 52 | 2022-05-04 09:00 | 2.8481 | 52
2022-05-04 10:00 | 4.7278 | 52 | 2022-05-04 10:00 | 2.8305 | 52
2022-05-04 11:00 | 4.7574 | 53 | 2022-05-04 11:00 | 2.8501 | 53
2022-05-04 12:00 | 4.7416 | 54 | 2022-05-04 12:00 | 2.8395 | 54
2022-05-04 13:00 | 4.7633 | 58 | 2022-05-04 13:00 | 2.854 | 58
2022-05-04 14:00 | 4.7396 | 59 | 2022-05-04 14:00 | 2.8382 | 59
2022-05-04 15:00 | 4.7189 | 61 | 2022-05-04 15:00 | 2.8248 | 61
2022-05-04 16:00 | 4.7327 | 59 | 2022-05-04 16:00 | 2.8337 | 59
2022-05-04 17:00 | 4.7584 | 63 | 2022-05-04 17:00 | 2.8507 | 63
2022-05-04 18:00 | 4.7268 | 63 | 2022-05-04 18:00 | 2.8299 | 63
2022-05-04 19:00 | 4.9573 | 65 | 2022-05-04 19:00 | 3.0094 | 65
2022-05-04 20:00 | 4.9573 | 57 | 2022-05-04 20:00 | 3.0094 | 57
2022-05-04 21:00 | 4.9668 | 55 | 2022-05-04 21:00 | 3.0184 | 55
2022-05-04 22:00 | 4.9457 | 56 | 2022-05-04 22:00 | 2.9987 | 56
2022-05-04 23:00 | 4.9803 | 55 | 2022-05-04 23:00 | 3.0313 | 55
2022-05-05 | 5.0158 | 60 | 2022-05-05 | 3.0666 | 60
2022-05-05 01:00 | 4.9592 | 60 | 2022-05-05 01:00 | 3.0112 | 60
2022-05-05 02:00 | 5.0024 | 59 | 2022-05-05 02:00 | 3.053 | 59
2022-05-05 03:00 | 4.987 | 59 | 2022-05-05 03:00 | 3.0378 | 59
2022-05-05 04:00 | 4.9899 | 58 | 2022-05-05 04:00 | 3.0407 | 58
2022-05-05 05:00 | 5.0205 | 58 | 2022-05-05 05:00 | 3.0715 | 58
2022-05-05 06:00 | 5.0491 | 56 | 2022-05-05 06:00 | 3.1017 | 56
2022-05-05 07:00 | 5.0453 | 57 | 2022-05-05 07:00 | 3.0976 | 57
2022-05-05 08:00 | 5.0196 | 59 | 2022-05-05 08:00 | 3.0705 | 59
2022-05-05 09:00 | 4.9486 | 62 | 2022-05-05 09:00 | 3.0014 | 62
2022-05-05 10:00 | 4.8759 | 64 | 2022-05-05 10:00 | 2.9383 | 64
2022-05-05 11:00 | 4.8672 | 65 | 2022-05-05 11:00 | 2.9312 | 65
2022-05-05 12:00 | 4.8759 | 67 | 2022-05-05 12:00 | 2.9383 | 67
2022-05-05 13:00 | 4.8506 | 68 | 2022-05-05 13:00 | 2.918 | 68
2022-05-05 14:00 | 4.8565 | 65 | 2022-05-05 14:00 | 2.9226 | 65
2022-05-05 15:00 | 4.8526 | 65 | 2022-05-05 15:00 | 2.9196 | 65
2022-05-05 16:00 | 4.8184 | 66 | 2022-05-05 16:00 | 2.8933 | 66
2022-05-05 17:00 | 4.8701 | 63 | 2022-05-05 17:00 | 2.9336 | 63
2022-05-05 18:00 | 4.8389 | 61 | 2022-05-05 18:00 | 2.9089 | 61
2022-05-05 19:00 | 4.9158 | 59 | 2022-05-05 19:00 | 2.9719 | 59
2022-05-05 20:00 | 4.8896 | 57 | 2022-05-05 20:00 | 2.9496 | 57
2022-05-05 21:00 | 4.936 | 56 | 2022-05-05 21:00 | 2.9899 | 56
2022-05-05 22:00 | 4.9717 | 55 | 2022-05-05 22:00 | 3.023 | 55
2022-05-05 23:00 | 4.907 | 54 | 2022-05-05 23:00 | 2.9644 | 54
2022-05-06 | 4.8924 | 54 | 2022-05-06 | 2.952 | 54
2022-05-06 01:00 | 4.9486 | 54 | 2022-05-06 01:00 | 3.0014 | 54
2022-05-06 02:00 | 4.9167 | 55 | 2022-05-06 02:00 | 2.9728 | 55
2022-05-06 03:00 | 4.9621 | 55 | 2022-05-06 03:00 | 3.0139 | 55
2022-05-06 04:00 | 4.9947 | 55 | 2022-05-06 04:00 | 3.0454 | 55
2022-05-06 05:00 | 4.9803 | 56 | 2022-05-06 05:00 | 3.0313 | 56
2022-05-06 06:00 | 5.0062 | 56 | 2022-05-06 06:00 | 3.0569 | 56
2022-05-06 07:00 | 4.988 | 54 | 2022-05-06 07:00 | 3.0388 | 54
2022-05-06 08:00 | 4.9553 | 55 | 2022-05-06 08:00 | 3.0076 | 55
2022-05-06 09:00 | 4.9813 | 56 | 2022-05-06 09:00 | 3.0322 | 56
2022-05-06 10:00 | 4.9437 | 58 | 2022-05-06 10:00 | 2.9969 | 58
2022-05-06 11:00 | 4.9109 | 56 | 2022-05-06 11:00 | 2.9677 | 56
2022-05-06 12:00 | 4.8992 | 56 | 2022-05-06 12:00 | 2.9577 | 56
2022-05-06 13:00 | 4.9496 | 56 | 2022-05-06 13:00 | 3.0022 | 56
2022-05-06 14:00 | 4.9515 | 56 | 2022-05-06 14:00 | 3.004 | 56
2022-05-06 15:00 | 4.8992 | 55 | 2022-05-06 15:00 | 2.9577 | 55
2022-05-06 16:00 | 4.9408 | 53 | 2022-05-06 16:00 | 2.9943 | 53
2022-05-06 17:00 | 4.9679 | 52 | 2022-05-06 17:00 | 3.0193 | 52
2022-05-06 18:00 | 4.9437 | 51 | 2022-05-06 18:00 | 2.9969 | 51
2022-05-06 19:00 | 4.9215 | 50 | 2022-05-06 19:00 | 2.977 | 50
2022-05-06 20:00 | 4.9147 | 49 | 2022-05-06 20:00 | 2.9711 | 49
2022-05-06 21:00 | 4.9774 | 49 | 2022-05-06 21:00 | 3.0285 | 49
2022-05-06 22:00 | 4.9428 | 49 | 2022-05-06 22:00 | 2.9961 | 49
2022-05-06 23:00 | 4.9167 | 49 | 2022-05-06 23:00 | 2.9728 | 49
2022-05-07 | 4.9928 | 49 | 2022-05-07 | 3.0435 | 49
2022-05-07 01:00 | 5.0109 | 49 | 2022-05-07 01:00 | 3.0617 | 49
2022-05-07 02:00 | 5.0291 | 50 | 2022-05-07 02:00 | 3.0804 | 50
2022-05-07 03:00 | 5.0196 | 50 | 2022-05-07 03:00 | 3.0705 | 50
2022-05-07 04:00 | 5.0071 | 50 | 2022-05-07 04:00 | 3.0578 | 50
2022-05-07 05:00 | 5.012 | 51 | 2022-05-07 05:00 | 3.0627 | 51
2022-05-07 06:00 | 5.012 | 50 | 2022-05-07 06:00 | 3.0627 | 50
2022-05-07 07:00 | 5.05 | 50 | 2022-05-07 07:00 | 3.1027 | 50
2022-05-07 08:00 | 5.0766 | 50 | 2022-05-07 08:00 | 3.1321 | 50
2022-05-07 09:00 | 5.0681 | 50 | 2022-05-07 09:00 | 3.1225 | 50
2022-05-07 10:00 | 4.9938 | 50 | 2022-05-07 10:00 | 3.0444 | 50
2022-05-07 11:00 | 5.0091 | 50 | 2022-05-07 11:00 | 3.0598 | 50
2022-05-07 12:00 | 5.0091 | 49 | 2022-05-07 12:00 | 3.0598 | 49
2022-05-07 13:00 | 5.0282 | 48 | 2022-05-07 13:00 | 3.0794 | 48
2022-05-07 14:00 | 5.0109 | 47 | 2022-05-07 14:00 | 3.0617 | 47
2022-05-07 15:00 | 4.9794 | 47 | 2022-05-07 15:00 | 3.0304 | 47
2022-05-07 16:00 | 4.9918 | 45 | 2022-05-07 16:00 | 3.0425 | 45
2022-05-07 17:00 | 5.0062 | 46 | 2022-05-07 17:00 | 3.0569 | 46
2022-05-07 18:00 | 4.9985 | 46 | 2022-05-07 18:00 | 3.0492 | 46
2022-05-07 19:00 | 4.9889 | 46 | 2022-05-07 19:00 | 3.0397 | 46
2022-05-07 20:00 | 5.0033 | 47 | 2022-05-07 20:00 | 3.054 | 47
2022-05-07 21:00 | 5.0062 | 47 | 2022-05-07 21:00 | 3.0569 | 47
2022-05-07 22:00 | 5.0129 | 47 | 2022-05-07 22:00 | 3.0637 | 47
2022-05-07 23:00 | 5.0081 | 46 | 2022-05-07 23:00 | 3.0588 | 46
2022-05-08 | 5.0291 | 45 | 2022-05-08 | 3.0804 | 45
2022-05-08 01:00 | 5.0993 | 44 | 2022-05-08 01:00 | 3.1582 | 44
2022-05-08 02:00 | 5.0728 | 45 | 2022-05-08 02:00 | 3.1278 | 45
2022-05-08 03:00 | 4.963 | 46 | 2022-05-08 03:00 | 3.0148 | 46
2022-05-08 04:00 | 5.0624 | 47 | 2022-05-08 04:00 | 3.1162 | 47
2022-05-08 05:00 | 5.0879 | 47 | 2022-05-08 05:00 | 3.145 | 47
2022-05-08 06:00 | 5.1106 | 47 | 2022-05-08 06:00 | 3.1717 | 47
2022-05-08 07:00 | 5.1322 | 47 | 2022-05-08 07:00 | 3.1979 | 47
2022-05-08 08:00 | 5.1388 | 48 | 2022-05-08 08:00 | 3.2061 | 48
2022-05-08 09:00 | 5.1388 | 49 | 2022-05-08 09:00 | 3.2061 | 49
2022-05-08 10:00 | 5.0386 | 51 | 2022-05-08 10:00 | 3.0905 | 51
2022-05-08 11:00 | 4.9679 | 51 | 2022-05-08 11:00 | 3.0193 | 51
2022-05-08 12:00 | 4.9726 | 53 | 2022-05-08 12:00 | 3.0239 | 53
2022-05-08 13:00 | 4.9611 | 54 | 2022-05-08 13:00 | 3.013 | 54
2022-05-08 14:00 | 4.9419 | 57 | 2022-05-08 14:00 | 2.9952 | 57
2022-05-08 15:00 | 4.9611 | 58 | 2022-05-08 15:00 | 3.013 | 58
2022-05-08 16:00 | 4.9486 | 58 | 2022-05-08 16:00 | 3.0014 | 58
2022-05-08 17:00 | 4.9457 | 57 | 2022-05-08 17:00 | 2.9987 | 57
2022-05-08 18:00 | 4.9553 | 57 | 2022-05-08 18:00 | 3.0076 | 57
2022-05-08 19:00 | 5.0024 | 55 | 2022-05-08 19:00 | 3.053 | 55
2022-05-08 20:00 | 5.0129 | 55 | 2022-05-08 20:00 | 3.0637 | 55
2022-05-08 21:00 | 4.9755 | 53 | 2022-05-08 21:00 | 3.0267 | 53
2022-05-08 22:00 | 4.9736 | 52 | 2022-05-08 22:00 | 3.0248 | 52
2022-05-08 23:00 | 5.0167 | 51 | 2022-05-08 23:00 | 3.0676 | 51
2022-05-09 | 5.0386 | 51 | 2022-05-09 | 3.0905 | 51
2022-05-09 01:00 | 4.9899 | 49 | 2022-05-09 01:00 | 3.0407 | 49
2022-05-09 02:00 | 4.9774 | 48 | 2022-05-09 02:00 | 3.0285 | 48
2022-05-09 03:00 | 5.1144 | 46 | 2022-05-09 03:00 | 3.1762 | 46
2022-05-09 04:00 | 5.0842 | 46 | 2022-05-09 04:00 | 3.1407 | 46
2022-05-09 05:00 | 5.1453 | 45 | 2022-05-09 05:00 | 3.2143 | 45
2022-05-09 06:00 | 5.1603 | 45 | 2022-05-09 06:00 | 3.2335 | 45
2022-05-09 07:00 | 8.0279 | 47 | 2022-05-09 07:00 | 4.0959 | 47
2022-05-09 08:00 | 12.0351 | 50 | 2022-05-09 08:00 | 4.0959 | 50
2022-05-09 09:00 | 12.0351 | 53 | 2022-05-09 09:00 | 4.0959 | 53
2022-05-09 10:00 | 12.0351 | 56 | 2022-05-09 10:00 | 4.0959 | 56
2022-05-09 11:00 | 12.0351 | 59 | 2022-05-09 11:00 | 4.0959 | 59
2022-05-09 12:00 | 12.0351 | 62 | 2022-05-09 12:00 | 4.0959 | 62
2022-05-09 13:00 | 12.0351 | 64 | 2022-05-09 13:00 | 4.0959 | 64
2022-05-09 14:00 | 12.0351 | 66 | 2022-05-09 14:00 | 4.0959 | 66
2022-05-09 15:00 | 12.0351 | 68 | 2022-05-09 15:00 | 4.0959 | 68
2022-05-09 16:00 | 12.0351 | 69 | 2022-05-09 16:00 | 4.0959 | 69
2022-05-09 17:00 | 12.0351 | 70 | 2022-05-09 17:00 | 4.0959 | 70
2022-05-09 18:00 | 7.1334 | 68 | 2022-05-09 18:00 | 4.0959 | 68
2022-05-09 19:00 | 4.964 | 65 | 2022-05-09 19:00 | 3.0157 | 65
2022-05-09 20:00 | 4.9976 | 62 | 2022-05-09 20:00 | 3.0482 | 62
2022-05-09 21:00 | 5.0109 | 60 | 2022-05-09 21:00 | 3.0617 | 60
2022-05-09 22:00 | 4.9697 | 59 | 2022-05-09 22:00 | 3.0211 | 59
2022-05-09 23:00 | 5.0262 | 55 | 2022-05-09 23:00 | 3.0774 | 55
2022-05-10 | 5.0205 | 54 | 2022-05-10 | 3.0715 | 54
2022-05-10 01:00 | 5.0453 | 53 | 2022-05-10 01:00 | 3.0976 | 53
2022-05-10 02:00 | 5.0519 | 52 | 2022-05-10 02:00 | 3.1047 | 52
2022-05-10 03:00 | 5.0681 | 51 | 2022-05-10 03:00 | 3.1225 | 51
2022-05-10 04:00 | 5.0643 | 51 | 2022-05-10 04:00 | 3.1183 | 51
2022-05-10 05:00 | 5.0917 | 51 | 2022-05-10 05:00 | 3.1494 | 51
2022-05-10 06:00 | 5.1219 | 51 | 2022-05-10 06:00 | 3.1853 | 51
2022-05-10 07:00 | 4.8944 | 52 | 2022-05-10 07:00 | 2.9536 | 52
2022-05-10 08:00 | 4.8983 | 55 | 2022-05-10 08:00 | 2.9569 | 55
2022-05-10 09:00 | 4.7889 | 58 | 2022-05-10 09:00 | 2.8719 | 58
2022-05-10 10:00 | 4.7238 | 61 | 2022-05-10 10:00 | 2.828 | 61
2022-05-10 11:00 | 4.6921 | 64 | 2022-05-10 11:00 | 2.8082 | 64
2022-05-10 12:00 | 4.6782 | 66 | 2022-05-10 12:00 | 2.7998 | 66
2022-05-10 13:00 | 4.6742 | 69 | 2022-05-10 13:00 | 2.7974 | 69
2022-05-10 14:00 | 4.6861 | 71 | 2022-05-10 14:00 | 2.8046 | 71
2022-05-10 15:00 | 4.6752 | 73 | 2022-05-10 15:00 | 2.798 | 73
2022-05-10 16:00 | 4.695 | 71 | 2022-05-10 16:00 | 2.81 | 71
2022-05-10 17:00 | 4.695 | 64 | 2022-05-10 17:00 | 2.81 | 64
2022-05-10 18:00 | 4.695 | 66 | 2022-05-10 18:00 | 2.81 | 66
2022-05-10 19:00 | 5.0519 | 67 | 2022-05-10 19:00 | 3.1047 | 67
2022-05-10 20:00 | 5.0329 | 64 | 2022-05-10 20:00 | 3.0844 | 64
2022-05-10 21:00 | 5.0176 | 63 | 2022-05-10 21:00 | 3.0685 | 63
2022-05-10 22:00 | 5.0558 | 60 | 2022-05-10 22:00 | 3.1089 | 60
2022-05-10 23:00 | 5.0348 | 58 | 2022-05-10 23:00 | 3.0864 | 58
2022-05-11 | 5.1284 | 57 | 2022-05-11 | 3.1932 | 57
2022-05-11 01:00 | 5.1228 | 55 | 2022-05-11 01:00 | 3.1864 | 55
2022-05-11 02:00 | 5.1144 | 54 | 2022-05-11 02:00 | 3.1762 | 54
2022-05-11 03:00 | 5.0917 | 54 | 2022-05-11 03:00 | 3.1494 | 54
2022-05-11 04:00 | 5.1547 | 53 | 2022-05-11 04:00 | 3.2263 | 53
2022-05-11 05:00 | 5.1622 | 53 | 2022-05-11 05:00 | 3.2359 | 53
2022-05-11 06:00 | 5.1948 | 54 | 2022-05-11 06:00 | 3.2794 | 54
2022-05-11 07:00 | 4.834 | 55 | 2022-05-11 07:00 | 2.9051 | 55
2022-05-11 08:00 | 4.8223 | 57 | 2022-05-11 08:00 | 2.8963 | 57
2022-05-11 09:00 | 4.7889 | 58 | 2022-05-11 09:00 | 2.8719 | 58
2022-05-11 10:00 | 4.7406 | 61 | 2022-05-11 10:00 | 2.8388 | 61
2022-05-11 11:00 | 4.7525 | 65 | 2022-05-11 11:00 | 2.8467 | 65
2022-05-11 12:00 | 4.7347 | 68 | 2022-05-11 12:00 | 2.835 | 68
2022-05-11 13:00 | 4.7771 | 68 | 2022-05-11 13:00 | 2.8636 | 68
2022-05-11 14:00 | 4.7485 | 71 | 2022-05-11 14:00 | 2.8441 | 71
2022-05-11 15:00 | 4.7426 | 72 | 2022-05-11 15:00 | 2.8402 | 72
2022-05-11 16:00 | 4.7367 | 68 | 2022-05-11 16:00 | 2.8363 | 68
2022-05-11 17:00 | 4.7653 | 62 | 2022-05-11 17:00 | 2.8554 | 62
2022-05-11 18:00 | 4.6871 | 62 | 2022-05-11 18:00 | 2.8051 | 62
2022-05-11 19:00 | 5.0367 | 60 | 2022-05-11 19:00 | 3.0884 | 60
2022-05-11 20:00 | 5.0224 | 57 | 2022-05-11 20:00 | 3.0734 | 57
2022-05-11 21:00 | 5.0424 | 55 | 2022-05-11 21:00 | 3.0945 | 55
2022-05-11 22:00 | 5.0757 | 55 | 2022-05-11 22:00 | 3.131 | 55
2022-05-11 23:00 | 5.104 | 56 | 2022-05-11 23:00 | 3.1638 | 56
2022-05-12 | 5.103 | 58 | 2022-05-12 | 3.1626 | 58
2022-05-12 01:00 | 5.0936 | 55 | 2022-05-12 01:00 | 3.1516 | 55
2022-05-12 02:00 | 5.0367 | 54 | 2022-05-12 02:00 | 3.0884 | 54
2022-05-12 03:00 | 5.0737 | 56 | 2022-05-12 03:00 | 3.1289 | 56
2022-05-12 04:00 | 5.1106 | 56 | 2022-05-12 04:00 | 3.1717 | 56
2022-05-12 05:00 | 5.0946 | 58 | 2022-05-12 05:00 | 3.1527 | 58
2022-05-12 06:00 | 12.19 | 61 | 2022-05-12 06:00 | 4.0959 | 61
2022-05-12 07:00 | 12.0351 | 57 | 2022-05-12 07:00 | 4.0959 | 57
2022-05-12 08:00 | 12.0351 | 57 | 2022-05-12 08:00 | 4.0959 | 57
2022-05-12 09:00 | 12.0351 | 61 | 2022-05-12 09:00 | 4.0959 | 61
2022-05-12 10:00 | 12.0351 | 64 | 2022-05-12 10:00 | 4.0959 | 64
2022-05-12 11:00 | 12.0351 | 62 | 2022-05-12 11:00 | 4.0959 | 62
2022-05-12 12:00 | 12.0351 | 66 | 2022-05-12 12:00 | 4.0959 | 66
2022-05-12 13:00 | 12.0351 | 70 | 2022-05-12 13:00 | 4.0959 | 70
2022-05-12 14:00 | 12.0351 | 69 | 2022-05-12 14:00 | 4.0959 | 69
2022-05-12 15:00 | 12.0351 | 68 | 2022-05-12 15:00 | 4.0959 | 68
2022-05-12 16:00 | 12.0351 | 68 | 2022-05-12 16:00 | 4.0959 | 68
2022-05-12 17:00 | 12.0351 | 68 | 2022-05-12 17:00 | 4.0959 | 68
2022-05-12 18:00 | 7.6049 | 65 | 2022-05-12 18:00 | 4.0959 | 65
2022-05-12 19:00 | 0.96006 | 61 | 2022-05-12 19:00 | 0.89083 | 61
2022-05-12 20:00 | 0.96776 | 60 | 2022-05-12 20:00 | 0.89903 | 60
2022-05-12 21:00 | 0.98601 | 59 | 2022-05-12 21:00 | 0.91853 | 59
2022-05-12 22:00 | 0.97444 | 60 | 2022-05-12 22:00 | 0.90615 | 60
2022-05-12 23:00 | 0.98218 | 59 | 2022-05-12 23:00 | 0.91443 | 59
2022-05-13 | 0.97734 | 56 | 2022-05-13 | 0.90925 | 56
2022-05-13 01:00 | 0.98218 | 57 | 2022-05-13 01:00 | 0.91443 | 57
2022-05-13 02:00 | 0.985 | 58 | 2022-05-13 02:00 | 0.91745 | 58
2022-05-13 03:00 | 0.9706 | 59 | 2022-05-13 03:00 | 0.90205 | 59
2022-05-13 04:00 | 0.97161 | 60 | 2022-05-13 04:00 | 0.90313 | 60
2022-05-13 05:00 | 1.0051 | 61 | 2022-05-13 05:00 | 0.93908 | 61
2022-05-13 06:00 | 0.99366 | 59 | 2022-05-13 06:00 | 0.92675 | 59
2022-05-13 07:00 | 0.96006 | 59 | 2022-05-13 07:00 | 0.89083 | 59
2022-05-13 08:00 | 0.96291 | 60 | 2022-05-13 08:00 | 0.89386 | 60
2022-05-13 09:00 | 0.94068 | 61 | 2022-05-13 09:00 | 0.87031 | 61
2022-05-13 10:00 | 0.90861 | 62 | 2022-05-13 10:00 | 0.83667 | 62
2022-05-13 11:00 | 0.92618 | 66 | 2022-05-13 11:00 | 0.85505 | 66
2022-05-13 12:00 | 0.91936 | 68 | 2022-05-13 12:00 | 0.84789 | 68
2022-05-13 13:00 | 0.91642 | 73 | 2022-05-13 13:00 | 0.84482 | 73
2022-05-13 14:00 | 0.91833 | 74 | 2022-05-13 14:00 | 0.84682 | 74
2022-05-13 15:00 | 0.90374 | 68 | 2022-05-13 15:00 | 0.8316 | 68
2022-05-13 16:00 | 0.90957 | 68 | 2022-05-13 16:00 | 0.83767 | 68
2022-05-13 17:00 | 1.0582 | 66 | 2022-05-13 17:00 | 0.99677 | 66
2022-05-13 18:00 | 1.6142 | 64 | 2022-05-13 18:00 | 1.6083 | 64
2022-05-13 19:00 | 1.6413 | 61 | 2022-05-13 19:00 | 1.6359 | 61
2022-05-13 20:00 | 1.6241 | 59 | 2022-05-13 20:00 | 1.6185 | 59
2022-05-13 21:00 | 1.635 | 58 | 2022-05-13 21:00 | 1.6295 | 58
2022-05-13 22:00 | 1.6567 | 58 | 2022-05-13 22:00 | 1.6514 | 58
2022-05-13 23:00 | 1.6549 | 58 | 2022-05-13 23:00 | 1.6496 | 58
2022-05-14 | 1.6458 | 58 | 2022-05-14 | 1.6405 | 58
2022-05-14 01:00 | 1.644 | 58 | 2022-05-14 01:00 | 1.6387 | 58
2022-05-14 02:00 | 1.6639 | 59 | 2022-05-14 02:00 | 1.6587 | 59
2022-05-14 03:00 | 1.6575 | 59 | 2022-05-14 03:00 | 1.6523 | 59
2022-05-14 04:00 | 1.6367 | 59 | 2022-05-14 04:00 | 1.6313 | 59
2022-05-14 05:00 | 1.6395 | 58 | 2022-05-14 05:00 | 1.6341 | 58
2022-05-14 06:00 | 1.6449 | 59 | 2022-05-14 06:00 | 1.6396 | 59
2022-05-14 07:00 | 1.6467 | 60 | 2022-05-14 07:00 | 1.6414 | 60
2022-05-14 08:00 | 1.6386 | 60 | 2022-05-14 08:00 | 1.6332 | 60
2022-05-14 09:00 | 1.6494 | 62 | 2022-05-14 09:00 | 1.6441 | 62
2022-05-14 10:00 | 1.6694 | 65 | 2022-05-14 10:00 | 1.6641 | 65
2022-05-14 11:00 | 1.6838 | 68 | 2022-05-14 11:00 | 1.6785 | 68
2022-05-14 12:00 | 1.6503 | 69 | 2022-05-14 12:00 | 1.645 | 69
2022-05-14 13:00 | 1.6612 | 67 | 2022-05-14 13:00 | 1.6559 | 67
2022-05-14 14:00 | 1.6539 | 68 | 2022-05-14 14:00 | 1.6487 | 68
2022-05-14 15:00 | 1.653 | 66 | 2022-05-14 15:00 | 1.6478 | 66
2022-05-14 16:00 | 1.6666 | 61 | 2022-05-14 16:00 | 1.6614 | 61
2022-05-14 17:00 | 1.6494 | 64 | 2022-05-14 17:00 | 1.6441 | 64
2022-05-14 18:00 | 1.6476 | 63 | 2022-05-14 18:00 | 1.6424 | 63
2022-05-14 19:00 | 1.6377 | 62 | 2022-05-14 19:00 | 1.6323 | 62
2022-05-14 20:00 | 1.6648 | 59 | 2022-05-14 20:00 | 1.6596 | 59
2022-05-14 21:00 | 1.6721 | 58 | 2022-05-14 21:00 | 1.6668 | 58
2022-05-14 22:00 | 1.6766 | 59 | 2022-05-14 22:00 | 1.6713 | 59
2022-05-14 23:00 | 1.6594 | 61 | 2022-05-14 23:00 | 1.6542 | 61
2022-05-15 | 1.644 | 60 | 2022-05-15 | 1.6387 | 60
2022-05-15 01:00 | 1.6205 | 58 | 2022-05-15 01:00 | 1.6148 | 58
2022-05-15 02:00 | 1.6232 | 57 | 2022-05-15 02:00 | 1.6176 | 57
2022-05-15 03:00 | 1.625 | 57 | 2022-05-15 03:00 | 1.6194 | 57
2022-05-15 04:00 | 1.6413 | 56 | 2022-05-15 04:00 | 1.6359 | 56
2022-05-15 05:00 | 1.6268 | 56 | 2022-05-15 05:00 | 1.6212 | 56
2022-05-15 06:00 | 1.6205 | 55 | 2022-05-15 06:00 | 1.6148 | 55
2022-05-15 07:00 | 1.6503 | 57 | 2022-05-15 07:00 | 1.645 | 57
2022-05-15 08:00 | 1.6449 | 58 | 2022-05-15 08:00 | 1.6396 | 58
2022-05-15 09:00 | 1.6313 | 60 | 2022-05-15 09:00 | 1.6258 | 60
2022-05-15 10:00 | 1.6386 | 61 | 2022-05-15 10:00 | 1.6332 | 61
2022-05-15 11:00 | 1.6467 | 64 | 2022-05-15 11:00 | 1.6414 | 64
2022-05-15 12:00 | 1.6575 | 70 | 2022-05-15 12:00 | 1.6523 | 70
2022-05-15 13:00 | 1.6322 | 71 | 2022-05-15 13:00 | 1.6267 | 71
2022-05-15 14:00 | 1.6575 | 70 | 2022-05-15 14:00 | 1.6523 | 70
2022-05-15 15:00 | 1.6784 | 68 | 2022-05-15 15:00 | 1.6731 | 68
2022-05-15 16:00 | 1.6721 | 68 | 2022-05-15 16:00 | 1.6668 | 68
2022-05-15 17:00 | 1.6639 | 67 | 2022-05-15 17:00 | 1.6587 | 67
2022-05-15 18:00 | 1.6657 | 65 | 2022-05-15 18:00 | 1.6605 | 65
2022-05-15 19:00 | 1.6802 | 64 | 2022-05-15 19:00 | 1.6749 | 64
2022-05-15 20:00 | 1.6404 | 62 | 2022-05-15 20:00 | 1.635 | 62
2022-05-15 21:00 | 1.6286 | 60 | 2022-05-15 21:00 | 1.6231 | 60
2022-05-15 22:00 | 1.6711 | 59 | 2022-05-15 22:00 | 1.6659 | 59
2022-05-15 23:00 | 1.6367 | 60 | 2022-05-15 23:00 | 1.6313 | 60
2022-05-16 | 1.6386 | 60 | 2022-05-16 | 1.6332 | 60
2022-05-16 01:00 | 1.6214 | 60 | 2022-05-16 01:00 | 1.6157 | 60
2022-05-16 02:00 | 1.6313 | 61 | 2022-05-16 02:00 | 1.6258 | 61
2022-05-16 03:00 | 1.6087 | 63 | 2022-05-16 03:00 | 1.6027 | 63
2022-05-16 04:00 | 1.6431 | 60 | 2022-05-16 04:00 | 1.6377 | 60
2022-05-16 05:00 | 1.6549 | 59 | 2022-05-16 05:00 | 1.6496 | 59
2022-05-16 06:00 | 4.5662 | 60 | 2022-05-16 06:00 | 2.739 | 60
2022-05-16 07:00 | 12.0351 | 63 | 2022-05-16 07:00 | 4.0959 | 63
2022-05-16 08:00 | 12.0351 | 63 | 2022-05-16 08:00 | 4.0959 | 63
2022-05-16 09:00 | 12.0351 | 61 | 2022-05-16 09:00 | 4.0959 | 61
2022-05-16 10:00 | 12.0351 | 67 | 2022-05-16 10:00 | 4.0959 | 67
2022-05-16 11:00 | 12.0351 | 66 | 2022-05-16 11:00 | 4.0959 | 66
2022-05-16 12:00 | 12.0351 | 69 | 2022-05-16 12:00 | 4.0959 | 69
2022-05-16 13:00 | 12.0351 | 68 | 2022-05-16 13:00 | 4.0959 | 68
2022-05-16 14:00 | 12.0351 | 67 | 2022-05-16 14:00 | 4.0959 | 67
2022-05-16 15:00 | 12.0351 | 64 | 2022-05-16 15:00 | 4.0959 | 64
2022-05-16 16:00 | 12.0351 | 63 | 2022-05-16 16:00 | 4.0959 | 63
2022-05-16 17:00 | 12.0351 | 64 | 2022-05-16 17:00 | 4.0959 | 64
2022-05-16 18:00 | 4.9031 | 62 | 2022-05-16 18:00 | 2.961 | 62
2022-05-16 19:00 | 4.8992 | 61 | 2022-05-16 19:00 | 2.9577 | 61
2022-05-16 20:00 | 4.9668 | 62 | 2022-05-16 20:00 | 3.0184 | 62
2022-05-16 21:00 | 4.909 | 66 | 2022-05-16 21:00 | 2.9661 | 66
2022-05-16 22:00 | 4.9457 | 64 | 2022-05-16 22:00 | 2.9987 | 64
2022-05-16 23:00 | 4.9283 | 63 | 2022-05-16 23:00 | 2.983 | 63
2022-05-17 | 4.9947 | 64 | 2022-05-17 | 3.0454 | 64
2022-05-17 01:00 | 4.8944 | 62 | 2022-05-17 01:00 | 2.9536 | 62
2022-05-17 02:00 | 4.9707 | 60 | 2022-05-17 02:00 | 3.022 | 60
2022-05-17 03:00 | 5.0224 | 60 | 2022-05-17 03:00 | 3.0734 | 60
2022-05-17 04:00 | 5.0329 | 59 | 2022-05-17 04:00 | 3.0844 | 59
2022-05-17 05:00 | 5.0158 | 58 | 2022-05-17 05:00 | 3.0666 | 58
2022-05-17 06:00 | 12.0351 | 57 | 2022-05-17 06:00 | 4.0959 | 57
2022-05-17 07:00 | 12.0351 | 60 | 2022-05-17 07:00 | 4.0959 | 60
2022-05-17 08:00 | 12.0351 | 62 | 2022-05-17 08:00 | 4.0959 | 62
2022-05-17 09:00 | 12.0351 | 63 | 2022-05-17 09:00 | 4.0959 | 63
2022-05-17 10:00 | 12.0351 | 67 | 2022-05-17 10:00 | 4.0959 | 67
2022-05-17 11:00 | 12.0351 | 69 | 2022-05-17 11:00 | 4.0959 | 69
2022-05-17 12:00 | 12.0351 | 71 | 2022-05-17 12:00 | 4.0959 | 71
2022-05-17 13:00 | 12.0351 | 77 | 2022-05-17 13:00 | 4.0959 | 77
2022-05-17 14:00 | 12.0351 | 77 | 2022-05-17 14:00 | 4.0959 | 77
2022-05-17 15:00 | 12.0351 | 78 | 2022-05-17 15:00 | 4.0959 | 78
2022-05-17 16:00 | 12.0351 | 77 | 2022-05-17 16:00 | 4.0959 | 77
2022-05-17 17:00 | 12.0351 | 76 | 2022-05-17 17:00 | 4.0959 | 76
2022-05-17 18:00 | 10.1685 | 77 | 2022-05-17 18:00 | 4.0959 | 77
2022-05-17 19:00 | 4.834 | 75 | 2022-05-17 19:00 | 2.9051 | 75
2022-05-17 20:00 | 4.8828 | 72 | 2022-05-17 20:00 | 2.9439 | 72
2022-05-17 21:00 | 4.8818 | 69 | 2022-05-17 21:00 | 2.9431 | 69
2022-05-17 22:00 | 4.8496 | 66 | 2022-05-17 22:00 | 2.9172 | 66
2022-05-17 23:00 | 4.8652 | 63 | 2022-05-17 23:00 | 2.9296 | 63
2022-05-18 | 4.937 | 62 | 2022-05-18 | 2.9908 | 62
2022-05-18 01:00 | 4.9322 | 60 | 2022-05-18 01:00 | 2.9865 | 60
2022-05-18 02:00 | 4.908 | 59 | 2022-05-18 02:00 | 2.9652 | 59
2022-05-18 03:00 | 4.9196 | 59 | 2022-05-18 03:00 | 2.9753 | 59
2022-05-18 04:00 | 4.9515 | 58 | 2022-05-18 04:00 | 3.004 | 58
2022-05-18 05:00 | 4.9408 | 57 | 2022-05-18 05:00 | 2.9943 | 57
2022-05-18 06:00 | 12.0351 | 56 | 2022-05-18 06:00 | 4.0959 | 56
2022-05-18 07:00 | 12.0351 | 57 | 2022-05-18 07:00 | 4.0959 | 57
2022-05-18 08:00 | 12.0351 | 60 | 2022-05-18 08:00 | 4.0959 | 60
2022-05-18 09:00 | 12.0351 | 63 | 2022-05-18 09:00 | 4.0959 | 63
2022-05-18 10:00 | 12.0351 | 63 | 2022-05-18 10:00 | 4.0959 | 63
2022-05-18 11:00 | 12.0351 | 65 | 2022-05-18 11:00 | 4.0959 | 65
2022-05-18 12:00 | 12.0351 | 66 | 2022-05-18 12:00 | 4.0959 | 66
2022-05-18 13:00 | 12.0351 | 68 | 2022-05-18 13:00 | 4.0959 | 68
2022-05-18 14:00 | 2.9487 | 69 | 2022-05-18 14:00 | 2.3953 | 69
2022-05-18 15:00 | 12.0351 | 68 | 2022-05-18 15:00 | 4.0959 | 68
2022-05-18 16:00 | 12.0351 | 70 | 2022-05-18 16:00 | 4.0959 | 70
2022-05-18 17:00 | 0.90079 | 66 | 2022-05-18 17:00 | 0.82853 | 66
2022-05-18 18:00 | 0.89488 | 61 | 2022-05-18 18:00 | 0.8224 | 61
2022-05-18 19:00 | 0.93395 | 61 | 2022-05-18 19:00 | 0.86321 | 61
2022-05-18 20:00 | 0.91546 | 59 | 2022-05-18 20:00 | 0.84382 | 59
2022-05-18 21:00 | 0.93198 | 58 | 2022-05-18 21:00 | 0.86114 | 58
2022-05-18 22:00 | 0.91546 | 58 | 2022-05-18 22:00 | 0.84382 | 58
2022-05-18 23:00 | 0.88703 | 58 | 2022-05-18 23:00 | 0.81427 | 58
2022-05-19 | 0.91348 | 59 | 2022-05-19 | 0.84175 | 59
2022-05-19 01:00 | 0.92223 | 58 | 2022-05-19 01:00 | 0.8509 | 58
2022-05-19 02:00 | 0.90272 | 58 | 2022-05-19 02:00 | 0.83053 | 58
2022-05-19 03:00 | 0.89585 | 57 | 2022-05-19 03:00 | 0.8234 | 57
2022-05-19 04:00 | 0.91156 | 56 | 2022-05-19 04:00 | 0.83974 | 56
2022-05-19 05:00 | 0.9349 | 54 | 2022-05-19 05:00 | 0.86422 | 54
2022-05-19 06:00 | 12.0351 | 54 | 2022-05-19 06:00 | 4.0959 | 54
2022-05-19 07:00 | 12.0351 | 54 | 2022-05-19 07:00 | 4.0959 | 54
2022-05-19 08:00 | 12.0351 | 54 | 2022-05-19 08:00 | 4.0959 | 54
2022-05-19 09:00 | 12.0351 | 54 | 2022-05-19 09:00 | 4.0959 | 54
2022-05-19 10:00 | 12.0351 | 55 | 2022-05-19 10:00 | 4.0959 | 55
2022-05-19 11:00 | 12.0351 | 55 | 2022-05-19 11:00 | 4.0959 | 55
2022-05-19 12:00 | 12.0351 | 56 | 2022-05-19 12:00 | 4.0959 | 56
2022-05-19 13:00 | 12.0351 | 56 | 2022-05-19 13:00 | 4.0959 | 56
2022-05-19 14:00 | 12.0351 | 58 | 2022-05-19 14:00 | 4.0959 | 58
2022-05-19 15:00 | 12.0351 | 59 | 2022-05-19 15:00 | 4.0959 | 59
2022-05-19 16:00 | 12.0351 | 60 | 2022-05-19 16:00 | 4.0959 | 60
2022-05-19 17:00 | 12.0351 | 61 | 2022-05-19 17:00 | 4.0959 | 61
2022-05-19 18:00 | 2.7381 | 62 | 2022-05-19 18:00 | 2.3408 | 62
2022-05-19 19:00 | 2.897 | 60 | 2022-05-19 19:00 | 2.3835 | 60
2022-05-19 20:00 | 2.8667 | 57 | 2022-05-19 20:00 | 2.3762 | 57
2022-05-19 21:00 | 2.8899 | 56 | 2022-05-19 21:00 | 2.3818 | 56
2022-05-19 22:00 | 2.8606 | 56 | 2022-05-19 22:00 | 2.3746 | 56
2022-05-19 23:00 | 2.8515 | 55 | 2022-05-19 23:00 | 2.3723 | 55
2022-05-20 | 2.8606 | 54 | 2022-05-20 | 2.3746 | 54
2022-05-20 01:00 | 2.899 | 55 | 2022-05-20 01:00 | 2.384 | 55
2022-05-20 02:00 | 2.9021 | 54 | 2022-05-20 02:00 | 2.3847 | 54
2022-05-20 03:00 | 2.9284 | 53 | 2022-05-20 03:00 | 2.3908 | 53
2022-05-20 04:00 | 2.9518 | 54 | 2022-05-20 04:00 | 2.396 | 54
2022-05-20 05:00 | 2.9365 | 54 | 2022-05-20 05:00 | 2.3926 | 54
2022-05-20 06:00 | 12.0351 | 53 | 2022-05-20 06:00 | 4.0959 | 53
2022-05-20 07:00 | 12.0351 | 56 | 2022-05-20 07:00 | 4.0959 | 56
2022-05-20 08:00 | 12.0351 | 59 | 2022-05-20 08:00 | 4.0959 | 59
2022-05-20 09:00 | 12.0351 | 61 | 2022-05-20 09:00 | 4.0959 | 61
2022-05-20 10:00 | 12.0351 | 63 | 2022-05-20 10:00 | 4.0959 | 63
2022-05-20 11:00 | 12.0351 | 67 | 2022-05-20 11:00 | 4.0959 | 67
2022-05-20 12:00 | 12.0351 | 65 | 2022-05-20 12:00 | 4.0959 | 65
2022-05-20 13:00 | 12.0351 | 59 | 2022-05-20 13:00 | 4.0959 | 59
2022-05-20 14:00 | 12.0351 | 61 | 2022-05-20 14:00 | 4.0959 | 61
2022-05-20 15:00 | 12.0351 | 66 | 2022-05-20 15:00 | 4.0959 | 66
2022-05-20 16:00 | 12.0351 | 63 | 2022-05-20 16:00 | 4.0959 | 63
2022-05-20 17:00 | 12.0351 | 63 | 2022-05-20 17:00 | 4.0959 | 63
2022-05-20 18:00 | 11.5232 | 62 | 2022-05-20 18:00 | 4.0959 | 62
2022-05-20 19:00 | 2.9233 | 63 | 2022-05-20 19:00 | 2.3896 | 63
2022-05-20 20:00 | 2.894 | 63 | 2022-05-20 20:00 | 2.3828 | 63
2022-05-20 21:00 | 2.8657 | 64 | 2022-05-20 21:00 | 2.3759 | 64
2022-05-20 22:00 | 2.8738 | 63 | 2022-05-20 22:00 | 2.3779 | 63
2022-05-20 23:00 | 2.8364 | 63 | 2022-05-20 23:00 | 2.3685 | 63
2022-05-21 | 2.8354 | 61 | 2022-05-21 | 2.3682 | 61
2022-05-21 01:00 | 2.8667 | 61 | 2022-05-21 01:00 | 2.3762 | 61
2022-05-21 02:00 | 2.8364 | 59 | 2022-05-21 02:00 | 2.3685 | 59
2022-05-21 03:00 | 2.8536 | 59 | 2022-05-21 03:00 | 2.3729 | 59
2022-05-21 04:00 | 2.8727 | 60 | 2022-05-21 04:00 | 2.3776 | 60
2022-05-21 05:00 | 2.8606 | 60 | 2022-05-21 05:00 | 2.3746 | 60
2022-05-21 06:00 | 2.8687 | 60 | 2022-05-21 06:00 | 2.3766 | 60
2022-05-21 07:00 | 2.8859 | 62 | 2022-05-21 07:00 | 2.3809 | 62
2022-05-21 08:00 | 2.9314 | 63 | 2022-05-21 08:00 | 2.3915 | 63
2022-05-21 09:00 | 2.9081 | 65 | 2022-05-21 09:00 | 2.3861 | 65
2022-05-21 10:00 | 2.893 | 72 | 2022-05-21 10:00 | 2.3826 | 72
2022-05-21 11:00 | 2.8717 | 77 | 2022-05-21 11:00 | 2.3774 | 77
2022-05-21 12:00 | 2.8879 | 82 | 2022-05-21 12:00 | 2.3813 | 82
2022-05-21 13:00 | 2.8657 | 86 | 2022-05-21 13:00 | 2.3759 | 86
2022-05-21 14:00 | 2.8798 | 77 | 2022-05-21 14:00 | 2.3794 | 77
2022-05-21 15:00 | 2.8909 | 73 | 2022-05-21 15:00 | 2.3821 | 73
2022-05-21 16:00 | 2.8838 | 74 | 2022-05-21 16:00 | 2.3804 | 74
2022-05-21 17:00 | 2.8828 | 77 | 2022-05-21 17:00 | 2.3801 | 77
2022-05-21 18:00 | 2.8767 | 77 | 2022-05-21 18:00 | 2.3786 | 77
2022-05-21 19:00 | 2.8677 | 78 | 2022-05-21 19:00 | 2.3764 | 78
2022-05-21 20:00 | 2.8677 | 76 | 2022-05-21 20:00 | 2.3764 | 76
2022-05-21 21:00 | 2.8475 | 75 | 2022-05-21 21:00 | 2.3713 | 75
2022-05-21 22:00 | 2.8506 | 71 | 2022-05-21 22:00 | 2.3721 | 71
2022-05-21 23:00 | 2.8767 | 71 | 2022-05-21 23:00 | 2.3786 | 71
2022-05-22 | 2.8586 | 74 | 2022-05-22 | 2.3741 | 74
2022-05-22 01:00 | 2.8153 | 69 | 2022-05-22 01:00 | 2.3629 | 69
2022-05-22 02:00 | 2.8243 | 69 | 2022-05-22 02:00 | 2.3653 | 69
2022-05-22 03:00 | 2.7581 | 67 | 2022-05-22 03:00 | 2.3468 | 67
2022-05-22 04:00 | 2.7802 | 65 | 2022-05-22 04:00 | 2.3532 | 65
2022-05-22 05:00 | 2.7561 | 65 | 2022-05-22 05:00 | 2.3462 | 65
2022-05-22 06:00 | 2.7751 | 66 | 2022-05-22 06:00 | 2.3517 | 66
2022-05-22 07:00 | 2.8143 | 67 | 2022-05-22 07:00 | 2.3626 | 67
2022-05-22 08:00 | 2.8173 | 69 | 2022-05-22 08:00 | 2.3634 | 69
2022-05-22 09:00 | 2.7541 | 70 | 2022-05-22 09:00 | 2.3456 | 70
2022-05-22 10:00 | 2.7711 | 78 | 2022-05-22 10:00 | 2.3506 | 78
2022-05-22 11:00 | 2.7651 | 82 | 2022-05-22 11:00 | 2.3488 | 82
2022-05-22 12:00 | 2.7922 | 80 | 2022-05-22 12:00 | 2.3565 | 80
2022-05-22 13:00 | 2.8022 | 78 | 2022-05-22 13:00 | 2.3593 | 78
2022-05-22 14:00 | 2.8113 | 82 | 2022-05-22 14:00 | 2.3618 | 82
2022-05-22 15:00 | 2.8042 | 79 | 2022-05-22 15:00 | 2.3599 | 79
2022-05-22 16:00 | 2.8163 | 76 | 2022-05-22 16:00 | 2.3631 | 76
2022-05-22 17:00 | 2.8102 | 74 | 2022-05-22 17:00 | 2.3615 | 74
2022-05-22 18:00 | 2.7751 | 73 | 2022-05-22 18:00 | 2.3517 | 73
2022-05-22 19:00 | 2.8083 | 71 | 2022-05-22 19:00 | 2.361 | 71
2022-05-22 20:00 | 2.7741 | 69 | 2022-05-22 20:00 | 2.3514 | 69
2022-05-22 21:00 | 2.7701 | 70 | 2022-05-22 21:00 | 2.3503 | 70
2022-05-22 22:00 | 2.7691 | 73 | 2022-05-22 22:00 | 2.35 | 73
2022-05-22 23:00 | 2.7731 | 77 | 2022-05-22 23:00 | 2.3512 | 77
2022-05-23 | 2.7812 | 74 | 2022-05-23 | 2.3534 | 74
2022-05-23 01:00 | 2.7511 | 73 | 2022-05-23 01:00 | 2.3447 | 73
2022-05-23 02:00 | 2.7611 | 72 | 2022-05-23 02:00 | 2.3477 | 72
2022-05-23 03:00 | 2.7791 | 69 | 2022-05-23 03:00 | 2.3529 | 69
2022-05-23 04:00 | 2.7731 | 67 | 2022-05-23 04:00 | 2.3512 | 67
2022-05-23 05:00 | 2.8083 | 65 | 2022-05-23 05:00 | 2.361 | 65
2022-05-23 06:00 | 11.5958 | 64 | 2022-05-23 06:00 | 4.0959 | 64
2022-05-23 07:00 | 12.0351 | 63 | 2022-05-23 07:00 | 4.0959 | 63
2022-05-23 08:00 | 12.0351 | 65 | 2022-05-23 08:00 | 4.0959 | 65
2022-05-23 09:00 | 12.0351 | 65 | 2022-05-23 09:00 | 4.0959 | 65
2022-05-23 10:00 | 12.0351 | 66 | 2022-05-23 10:00 | 4.0959 | 66
2022-05-23 11:00 | 12.0351 | 68 | 2022-05-23 11:00 | 4.0959 | 68
2022-05-23 12:00 | 12.0351 | 70 | 2022-05-23 12:00 | 4.0959 | 70
2022-05-23 13:00 | 12.0351 | 71 | 2022-05-23 13:00 | 4.0959 | 71
2022-05-23 14:00 | 12.0351 | 73 | 2022-05-23 14:00 | 4.0959 | 73
2022-05-23 15:00 | 12.0351 | 73 | 2022-05-23 15:00 | 4.0959 | 73
2022-05-23 16:00 | 12.0351 | 74 | 2022-05-23 16:00 | 4.0959 | 74
2022-05-23 17:00 | 12.0351 | 74 | 2022-05-23 17:00 | 4.0959 | 74
2022-05-23 18:00 | 2.7521 | 72 | 2022-05-23 18:00 | 2.345 | 72
2022-05-23 19:00 | 2.7611 | 71 | 2022-05-23 19:00 | 2.3477 | 71
2022-05-23 20:00 | 2.7531 | 70 | 2022-05-23 20:00 | 2.3453 | 70
2022-05-23 21:00 | 2.7451 | 64 | 2022-05-23 21:00 | 2.3429 | 64
2022-05-23 22:00 | 2.8284 | 63 | 2022-05-23 22:00 | 2.3663 | 63
2022-05-23 23:00 | 2.8274 | 63 | 2022-05-23 23:00 | 2.3661 | 63
2022-05-24 | 2.8314 | 61 | 2022-05-24 | 2.3671 | 61
2022-05-24 01:00 | 2.8133 | 61 | 2022-05-24 01:00 | 2.3623 | 61
2022-05-24 02:00 | 2.7992 | 61 | 2022-05-24 02:00 | 2.3585 | 61
2022-05-24 03:00 | 2.8495 | 60 | 2022-05-24 03:00 | 2.3718 | 60
2022-05-24 04:00 | 2.8596 | 59 | 2022-05-24 04:00 | 2.3744 | 59
2022-05-24 05:00 | 2.8889 | 58 | 2022-05-24 05:00 | 2.3816 | 58
2022-05-24 06:00 | 12.0351 | 59 | 2022-05-24 06:00 | 4.0959 | 59
2022-05-24 07:00 | 12.0351 | 60 | 2022-05-24 07:00 | 4.0959 | 60
2022-05-24 08:00 | 12.0351 | 60 | 2022-05-24 08:00 | 4.0959 | 60
2022-05-24 09:00 | 12.0351 | 62 | 2022-05-24 09:00 | 4.0959 | 62
2022-05-24 10:00 | 12.0351 | 63 | 2022-05-24 10:00 | 4.0959 | 63
2022-05-24 11:00 | 12.0351 | 63 | 2022-05-24 11:00 | 4.0959 | 63
2022-05-24 12:00 | 12.0351 | 62 | 2022-05-24 12:00 | 4.0959 | 62
2022-05-24 13:00 | 12.0351 | 63 | 2022-05-24 13:00 | 4.0959 | 63
2022-05-24 14:00 | 12.0351 | 65 | 2022-05-24 14:00 | 4.0959 | 65
2022-05-24 15:00 | 12.0351 | 67 | 2022-05-24 15:00 | 4.0959 | 67
2022-05-24 16:00 | 12.0351 | 65 | 2022-05-24 16:00 | 4.0959 | 65
2022-05-24 17:00 | 5.1688 | 66 | 2022-05-24 17:00 | 3.2445 | 66
2022-05-24 18:00 | 0.89687 | 62 | 2022-05-24 18:00 | 0.82446 | 62
2022-05-24 19:00 | 0.89488 | 59 | 2022-05-24 19:00 | 0.8224 | 59
2022-05-24 20:00 | 0.89983 | 58 | 2022-05-24 20:00 | 0.82753 | 58
2022-05-24 21:00 | 0.91053 | 58 | 2022-05-24 21:00 | 0.83867 | 58
2022-05-24 22:00 | 0.91642 | 57 | 2022-05-24 22:00 | 0.84482 | 57
2022-05-24 23:00 | 0.92223 | 55 | 2022-05-24 23:00 | 0.8509 | 55
2022-05-25 | 0.90374 | 54 | 2022-05-25 | 0.8316 | 54
2022-05-25 01:00 | 0.92516 | 54 | 2022-05-25 01:00 | 0.85398 | 54
2022-05-25 02:00 | 0.93395 | 54 | 2022-05-25 02:00 | 0.86321 | 54
2022-05-25 03:00 | 0.94842 | 54 | 2022-05-25 03:00 | 0.87849 | 54
2022-05-25 04:00 | 0.98023 | 52 | 2022-05-25 04:00 | 0.91234 | 52
2022-05-25 05:00 | 0.98984 | 52 | 2022-05-25 05:00 | 0.92264 | 52
2022-05-25 06:00 | 12.0351 | 52 | 2022-05-25 06:00 | 4.0959 | 52
2022-05-25 07:00 | 12.0351 | 55 | 2022-05-25 07:00 | 4.0959 | 55
2022-05-25 08:00 | 12.0351 | 58 | 2022-05-25 08:00 | 4.0959 | 58
2022-05-25 09:00 | 12.0351 | 60 | 2022-05-25 09:00 | 4.0959 | 60
2022-05-25 10:00 | 12.0351 | 62 | 2022-05-25 10:00 | 4.0959 | 62
2022-05-25 11:00 | 12.0351 | 64 | 2022-05-25 11:00 | 4.0959 | 64
2022-05-25 12:00 | 12.0351 | 65 | 2022-05-25 12:00 | 4.0959 | 65
2022-05-25 13:00 | 12.0351 | 64 | 2022-05-25 13:00 | 4.0959 | 64
2022-05-25 14:00 | 12.0351 | 64 | 2022-05-25 14:00 | 4.0959 | 64
2022-05-25 15:00 | 12.0351 | 63 | 2022-05-25 15:00 | 4.0959 | 63
2022-05-25 16:00 | 12.0351 | 63 | 2022-05-25 16:00 | 4.0959 | 63
2022-05-25 17:00 | 12.0351 | 61 | 2022-05-25 17:00 | 4.0959 | 61
2022-05-25 18:00 | 7.3269 | 59 | 2022-05-25 18:00 | 4.0959 | 59
2022-05-25 19:00 | 2.97 | 59 | 2022-05-25 19:00 | 2.3999 | 59
2022-05-25 20:00 | 2.9741 | 56 | 2022-05-25 20:00 | 2.4008 | 56
2022-05-25 21:00 | 3.0516 | 55 | 2022-05-25 21:00 | 2.4163 | 55
2022-05-25 22:00 | 3.025 | 55 | 2022-05-25 22:00 | 2.4112 | 55
2022-05-25 23:00 | 3.0169 | 54 | 2022-05-25 23:00 | 2.4095 | 54
2022-05-26 | 3.0138 | 54 | 2022-05-26 | 2.4089 | 54
2022-05-26 01:00 | 2.97 | 53 | 2022-05-26 01:00 | 2.3999 | 53
2022-05-26 02:00 | 3.0261 | 52 | 2022-05-26 02:00 | 2.4114 | 52
2022-05-26 03:00 | 3.0373 | 53 | 2022-05-26 03:00 | 2.4135 | 53
2022-05-26 04:00 | 3.0444 | 54 | 2022-05-26 04:00 | 2.4149 | 54
2022-05-26 05:00 | 3.067 | 53 | 2022-05-26 05:00 | 2.4191 | 53
2022-05-26 06:00 | 12.0351 | 53 | 2022-05-26 06:00 | 4.0959 | 53
2022-05-26 07:00 | 12.0351 | 56 | 2022-05-26 07:00 | 4.0959 | 56
2022-05-26 08:00 | 12.0351 | 59 | 2022-05-26 08:00 | 4.0959 | 59
2022-05-26 09:00 | 12.0351 | 61 | 2022-05-26 09:00 | 4.0959 | 61
2022-05-26 10:00 | 12.0351 | 63 | 2022-05-26 10:00 | 4.0959 | 63
2022-05-26 11:00 | 12.0351 | 64 | 2022-05-26 11:00 | 4.0959 | 64
2022-05-26 12:00 | 12.0351 | 65 | 2022-05-26 12:00 | 4.0959 | 65
2022-05-26 13:00 | 12.0351 | 66 | 2022-05-26 13:00 | 4.0959 | 66
2022-05-26 14:00 | 12.0351 | 66 | 2022-05-26 14:00 | 4.0959 | 66
2022-05-26 15:00 | 12.0351 | 64 | 2022-05-26 15:00 | 4.0959 | 64
2022-05-26 16:00 | 12.0351 | 66 | 2022-05-26 16:00 | 4.0959 | 66
2022-05-26 17:00 | 12.0351 | 65 | 2022-05-26 17:00 | 4.0959 | 65
2022-05-26 18:00 | 2.8717 | 64 | 2022-05-26 18:00 | 2.3774 | 64
2022-05-26 19:00 | 2.9822 | 63 | 2022-05-26 19:00 | 2.4025 | 63
2022-05-26 20:00 | 2.9975 | 63 | 2022-05-26 20:00 | 2.4056 | 63
2022-05-26 21:00 | 2.9649 | 62 | 2022-05-26 21:00 | 2.3988 | 62
2022-05-26 22:00 | 2.9731 | 62 | 2022-05-26 22:00 | 2.4006 | 62
2022-05-26 23:00 | 2.9609 | 63 | 2022-05-26 23:00 | 2.398 | 63
2022-05-27 | 2.9456 | 62 | 2022-05-27 | 2.3946 | 62
2022-05-27 01:00 | 2.9518 | 62 | 2022-05-27 01:00 | 2.396 | 62
2022-05-27 02:00 | 2.904 | 63 | 2022-05-27 02:00 | 2.3852 | 63
2022-05-27 03:00 | 2.9244 | 62 | 2022-05-27 03:00 | 2.3899 | 62
2022-05-27 04:00 | 2.9244 | 62 | 2022-05-27 04:00 | 2.3899 | 62
2022-05-27 05:00 | 2.9325 | 62 | 2022-05-27 05:00 | 2.3917 | 62
2022-05-27 06:00 | 12.0351 | 62 | 2022-05-27 06:00 | 4.0959 | 62
2022-05-27 07:00 | 12.0351 | 62 | 2022-05-27 07:00 | 4.0959 | 62
2022-05-27 08:00 | 12.0351 | 62 | 2022-05-27 08:00 | 4.0959 | 62
2022-05-27 09:00 | 12.0351 | 64 | 2022-05-27 09:00 | 4.0959 | 64
2022-05-27 10:00 | 12.0351 | 66 | 2022-05-27 10:00 | 4.0959 | 66
2022-05-27 11:00 | 12.0351 | 69 | 2022-05-27 11:00 | 4.0959 | 69
2022-05-27 12:00 | 12.0351 | 70 | 2022-05-27 12:00 | 4.0959 | 70
2022-05-27 13:00 | 12.0351 | 71 | 2022-05-27 13:00 | 4.0959 | 71
2022-05-27 14:00 | 12.0351 | 72 | 2022-05-27 14:00 | 4.0959 | 72
2022-05-27 15:00 | 12.0351 | 70 | 2022-05-27 15:00 | 4.0959 | 70
2022-05-27 16:00 | 12.0351 | 71 | 2022-05-27 16:00 | 4.0959 | 71
2022-05-27 17:00 | 3.9582 | 66 | 2022-05-27 17:00 | 2.5489 | 66
2022-05-27 18:00 | 1.3494 | 66 | 2022-05-27 18:00 | 1.3222 | 66
2022-05-27 19:00 | 1.2903 | 66 | 2022-05-27 19:00 | 1.2559 | 66
2022-05-27 20:00 | 1.2812 | 64 | 2022-05-27 20:00 | 1.2457 | 64
2022-05-27 21:00 | 1.2858 | 64 | 2022-05-27 21:00 | 1.2508 | 64
2022-05-27 22:00 | 1.2922 | 64 | 2022-05-27 22:00 | 1.258 | 64
2022-05-27 23:00 | 1.2785 | 63 | 2022-05-27 23:00 | 1.2426 | 63
2022-05-28 | 1.2849 | 63 | 2022-05-28 | 1.2498 | 63
2022-05-28 01:00 | 1.2794 | 63 | 2022-05-28 01:00 | 1.2436 | 63
2022-05-28 02:00 | 1.2529 | 64 | 2022-05-28 02:00 | 1.2138 | 64
2022-05-28 03:00 | 1.2666 | 63 | 2022-05-28 03:00 | 1.2293 | 63
2022-05-28 04:00 | 1.2538 | 63 | 2022-05-28 04:00 | 1.2149 | 63
2022-05-28 05:00 | 1.2493 | 64 | 2022-05-28 05:00 | 1.2097 | 64
2022-05-28 06:00 | 1.2812 | 66 | 2022-05-28 06:00 | 1.2457 | 66
2022-05-28 07:00 | 1.2538 | 65 | 2022-05-28 07:00 | 1.2149 | 65
2022-05-28 08:00 | 1.2803 | 65 | 2022-05-28 08:00 | 1.2446 | 65
2022-05-28 09:00 | 1.2931 | 66 | 2022-05-28 09:00 | 1.259 | 66
2022-05-28 10:00 | 1.2858 | 67 | 2022-05-28 10:00 | 1.2508 | 67
2022-05-28 11:00 | 1.2876 | 69 | 2022-05-28 11:00 | 1.2528 | 69
2022-05-28 12:00 | 1.2922 | 73 | 2022-05-28 12:00 | 1.258 | 73
2022-05-28 13:00 | 1.2684 | 70 | 2022-05-28 13:00 | 1.2313 | 70
2022-05-28 14:00 | 1.2511 | 69 | 2022-05-28 14:00 | 1.2118 | 69
2022-05-28 15:00 | 1.2812 | 72 | 2022-05-28 15:00 | 1.2457 | 72
2022-05-28 16:00 | 1.2456 | 74 | 2022-05-28 16:00 | 1.2056 | 74
2022-05-28 17:00 | 1.2675 | 72 | 2022-05-28 17:00 | 1.2303 | 72
2022-05-28 18:00 | 1.2483 | 72 | 2022-05-28 18:00 | 1.2086 | 72
2022-05-28 19:00 | 1.2757 | 74 | 2022-05-28 19:00 | 1.2395 | 74
2022-05-28 20:00 | 1.2867 | 73 | 2022-05-28 20:00 | 1.2518 | 73
2022-05-28 21:00 | 1.2812 | 72 | 2022-05-28 21:00 | 1.2457 | 72
2022-05-28 22:00 | 1.2584 | 71 | 2022-05-28 22:00 | 1.22 | 71
2022-05-28 23:00 | 1.2748 | 70 | 2022-05-28 23:00 | 1.2385 | 70
2022-05-29 | 1.263 | 67 | 2022-05-29 | 1.2252 | 67
2022-05-29 01:00 | 1.2364 | 66 | 2022-05-29 01:00 | 1.1953 | 66
2022-05-29 02:00 | 1.2493 | 64 | 2022-05-29 02:00 | 1.2097 | 64
2022-05-29 03:00 | 1.2437 | 63 | 2022-05-29 03:00 | 1.2035 | 63
2022-05-29 04:00 | 1.2437 | 62 | 2022-05-29 04:00 | 1.2035 | 62
2022-05-29 05:00 | 1.2502 | 62 | 2022-05-29 05:00 | 1.2107 | 62
2022-05-29 06:00 | 1.2547 | 61 | 2022-05-29 06:00 | 1.2159 | 61
2022-05-29 07:00 | 1.2566 | 64 | 2022-05-29 07:00 | 1.218 | 64
2022-05-29 08:00 | 1.2648 | 67 | 2022-05-29 08:00 | 1.2272 | 67
2022-05-29 09:00 | 1.2446 | 70 | 2022-05-29 09:00 | 1.2045 | 70
2022-05-29 10:00 | 1.2502 | 72 | 2022-05-29 10:00 | 1.2107 | 72
2022-05-29 11:00 | 1.2226 | 71 | 2022-05-29 11:00 | 1.1798 | 71
2022-05-29 12:00 | 1.23 | 72 | 2022-05-29 12:00 | 1.1881 | 72
2022-05-29 13:00 | 1.2309 | 73 | 2022-05-29 13:00 | 1.1891 | 73
2022-05-29 14:00 | 1.2593 | 73 | 2022-05-29 14:00 | 1.221 | 73
2022-05-29 15:00 | 1.2474 | 74 | 2022-05-29 15:00 | 1.2076 | 74
2022-05-29 16:00 | 1.2493 | 74 | 2022-05-29 16:00 | 1.2097 | 74
2022-05-29 17:00 | 1.2611 | 71 | 2022-05-29 17:00 | 1.2231 | 71
2022-05-29 18:00 | 1.2547 | 69 | 2022-05-29 18:00 | 1.2159 | 69
2022-05-29 19:00 | 1.2419 | 66 | 2022-05-29 19:00 | 1.2015 | 66
2022-05-29 20:00 | 1.2593 | 65 | 2022-05-29 20:00 | 1.221 | 65
2022-05-29 21:00 | 1.2666 | 63 | 2022-05-29 21:00 | 1.2293 | 63
2022-05-29 22:00 | 1.2291 | 63 | 2022-05-29 22:00 | 1.187 | 63
2022-05-29 23:00 | 1.2235 | 63 | 2022-05-29 23:00 | 1.1808 | 63
2022-05-30 | 1.2345 | 62 | 2022-05-30 | 1.1932 | 62
2022-05-30 01:00 | 1.207 | 63 | 2022-05-30 01:00 | 1.1623 | 63
2022-05-30 02:00 | 1.2309 | 62 | 2022-05-30 02:00 | 1.1891 | 62
2022-05-30 03:00 | 1.2153 | 62 | 2022-05-30 03:00 | 1.1716 | 62
2022-05-30 04:00 | 1.196 | 61 | 2022-05-30 04:00 | 1.1499 | 61
2022-05-30 05:00 | 1.2144 | 61 | 2022-05-30 05:00 | 1.1705 | 61
2022-05-30 06:00 | 1.2245 | 62 | 2022-05-30 06:00 | 1.1819 | 62
2022-05-30 07:00 | 12.0351 | 65 | 2022-05-30 07:00 | 4.0959 | 65
2022-05-30 08:00 | 12.0351 | 67 | 2022-05-30 08:00 | 4.0959 | 67
2022-05-30 09:00 | 12.0351 | 70 | 2022-05-30 09:00 | 4.0959 | 70
2022-05-30 10:00 | 12.0351 | 73 | 2022-05-30 10:00 | 4.0959 | 73
2022-05-30 11:00 | 12.0351 | 75 | 2022-05-30 11:00 | 4.0959 | 75
2022-05-30 12:00 | 12.0351 | 77 | 2022-05-30 12:00 | 4.0959 | 77
2022-05-30 13:00 | 12.0351 | 79 | 2022-05-30 13:00 | 4.0959 | 79
2022-05-30 14:00 | 12.0351 | 79 | 2022-05-30 14:00 | 4.0959 | 79
2022-05-30 15:00 | 2.7231 | 78 | 2022-05-30 15:00 | 2.3363 | 78
2022-05-30 16:00 | 2.7701 | 78 | 2022-05-30 16:00 | 2.3503 | 78
2022-05-30 17:00 | 2.7571 | 77 | 2022-05-30 17:00 | 2.3465 | 77
2022-05-30 18:00 | 2.8042 | 74 | 2022-05-30 18:00 | 2.3599 | 74
2022-05-30 19:00 | 2.7791 | 72 | 2022-05-30 19:00 | 2.3529 | 72
2022-05-30 20:00 | 2.7561 | 71 | 2022-05-30 20:00 | 2.3462 | 71
2022-05-30 21:00 | 2.7932 | 70 | 2022-05-30 21:00 | 2.3568 | 70
2022-05-30 22:00 | 2.7842 | 70 | 2022-05-30 22:00 | 2.3543 | 70
2022-05-30 23:00 | 2.8163 | 71 | 2022-05-30 23:00 | 2.3631 | 71
2022-05-31 | 2.8193 | 70 | 2022-05-31 | 2.3639 | 70
2022-05-31 01:00 | 2.7611 | 70 | 2022-05-31 01:00 | 2.3477 | 70
2022-05-31 02:00 | 2.7992 | 72 | 2022-05-31 02:00 | 2.3585 | 72
2022-05-31 03:00 | 2.7701 | 71 | 2022-05-31 03:00 | 2.3503 | 71
2022-05-31 04:00 | 2.7812 | 73 | 2022-05-31 04:00 | 2.3534 | 73
2022-05-31 05:00 | 2.8073 | 72 | 2022-05-31 05:00 | 2.3607 | 72
2022-05-31 06:00 | 12.0351 | 73 | 2022-05-31 06:00 | 4.0959 | 73
2022-05-31 07:00 | 12.0351 | 75 | 2022-05-31 07:00 | 4.0959 | 75
2022-05-31 08:00 | 12.0351 | 80 | 2022-05-31 08:00 | 4.0959 | 80
2022-05-31 09:00 | 12.0351 | 85 | 2022-05-31 09:00 | 4.0959 | 85
2022-05-31 10:00 | 12.0351 | 88 | 2022-05-31 10:00 | 4.0959 | 88
2022-05-31 11:00 | 12.0351 | 90 | 2022-05-31 11:00 | 4.0959 | 90
2022-05-31 12:00 | 12.0351 | 91 | 2022-05-31 12:00 | 4.0959 | 91
2022-05-31 13:00 | 12.0351 | 92 | 2022-05-31 13:00 | 4.0959 | 92
2022-05-31 14:00 | 12.0351 | 93 | 2022-05-31 14:00 | 4.0959 | 93
2022-05-31 15:00 | 12.0351 | 91 | 2022-05-31 15:00 | 4.0959 | 91
2022-05-31 16:00 | 12.0351 | 87 | 2022-05-31 16:00 | 4.0959 | 87
2022-05-31 17:00 | 12.0351 | 83 | 2022-05-31 17:00 | 4.0959 | 83
2022-05-31 18:00 | 12.0351 | 82 | 2022-05-31 18:00 | 4.0959 | 82
2022-05-31 19:00 | 12.0351 | 80 | 2022-05-31 19:00 | 4.0959 | 80
2022-05-31 20:00 | 12.0351 | 75 | 2022-05-31 20:00 | 4.0959 | 75
2022-05-31 21:00 | 2.9021 | 74 | 2022-05-31 21:00 | 2.3847 | 74
2022-05-31 22:00 | 2.9183 | 75 | 2022-05-31 22:00 | 2.3885 | 75
2022-05-31 23:00 | 2.8515 | 67 | 2022-05-31 23:00 | 2.3723 | 67
2022-06-01 | 2.8304 | 65 | 2022-06-01 | 2.3669 | 65
2022-06-01 01:00 | 2.8143 | 63 | 2022-06-01 01:00 | 2.3626 | 63
2022-06-01 02:00 | 2.8304 | 62 | 2022-06-01 02:00 | 2.3669 | 62
2022-06-01 03:00 | 2.8748 | 63 | 2022-06-01 03:00 | 2.3781 | 63
2022-06-01 04:00 | 2.8314 | 62 | 2022-06-01 04:00 | 2.3671 | 62
2022-06-01 05:00 | 2.8203 | 60 | 2022-06-01 05:00 | 2.3642 | 60
2022-06-01 06:00 | 4.5128 | 60 | 2022-06-01 06:00 | 2.7137 | 60
2022-06-01 07:00 | 12.0351 | 60 | 2022-06-01 07:00 | 4.0959 | 60
2022-06-01 08:00 | 12.0351 | 61 | 2022-06-01 08:00 | 4.0959 | 61
2022-06-01 09:00 | 12.0351 | 62 | 2022-06-01 09:00 | 4.0959 | 62
2022-06-01 10:00 | 12.0351 | 63 | 2022-06-01 10:00 | 4.0959 | 63
2022-06-01 11:00 | 12.0351 | 64 | 2022-06-01 11:00 | 4.0959 | 64
2022-06-01 12:00 | 12.0351 | 67 | 2022-06-01 12:00 | 4.0959 | 67
2022-06-01 13:00 | 12.0351 | 65 | 2022-06-01 13:00 | 4.0959 | 65
2022-06-01 14:00 | 12.0351 | 65 | 2022-06-01 14:00 | 4.0959 | 65
2022-06-01 15:00 | 12.0351 | 64 | 2022-06-01 15:00 | 4.0959 | 64
2022-06-01 16:00 | 12.0351 | 63 | 2022-06-01 16:00 | 4.0959 | 63
2022-06-01 17:00 | 12.0351 | 62 | 2022-06-01 17:00 | 4.0959 | 62
2022-06-01 18:00 | 6.9225 | 60 | 2022-06-01 18:00 | 4.0959 | 60
2022-06-01 19:00 | 2.9325 | 60 | 2022-06-01 19:00 | 2.3917 | 60
2022-06-01 20:00 | 2.8354 | 60 | 2022-06-01 20:00 | 2.3682 | 60
2022-06-01 21:00 | 2.8506 | 59 | 2022-06-01 21:00 | 2.3721 | 59
2022-06-01 22:00 | 2.8304 | 59 | 2022-06-01 22:00 | 2.3669 | 59
2022-06-01 23:00 | 2.7842 | 60 | 2022-06-01 23:00 | 2.3543 | 60
2022-06-02 | 2.8012 | 60 | 2022-06-02 | 2.359 | 60
2022-06-02 01:00 | 2.7731 | 60 | 2022-06-02 01:00 | 2.3512 | 60
2022-06-02 02:00 | 2.7892 | 61 | 2022-06-02 02:00 | 2.3557 | 61
2022-06-02 03:00 | 2.7871 | 63 | 2022-06-02 03:00 | 2.3551 | 63
2022-06-02 04:00 | 2.8042 | 63 | 2022-06-02 04:00 | 2.3599 | 63
2022-06-02 05:00 | 2.8234 | 63 | 2022-06-02 05:00 | 2.365 | 63
2022-06-02 06:00 | 8.3996 | 64 | 2022-06-02 06:00 | 4.0959 | 64
2022-06-02 07:00 | 12.0351 | 66 | 2022-06-02 07:00 | 4.0959 | 66
2022-06-02 08:00 | 12.0351 | 67 | 2022-06-02 08:00 | 4.0959 | 67
2022-06-02 09:00 | 12.0351 | 69 | 2022-06-02 09:00 | 4.0959 | 69
2022-06-02 10:00 | 12.0351 | 70 | 2022-06-02 10:00 | 4.0959 | 70
2022-06-02 11:00 | 12.0351 | 71 | 2022-06-02 11:00 | 4.0959 | 71
2022-06-02 12:00 | 12.0351 | 73 | 2022-06-02 12:00 | 4.0959 | 73
2022-06-02 13:00 | 12.0351 | 72 | 2022-06-02 13:00 | 4.0959 | 72
2022-06-02 14:00 | 12.0351 | 72 | 2022-06-02 14:00 | 4.0959 | 72
2022-06-02 15:00 | 12.0351 | 74 | 2022-06-02 15:00 | 4.0959 | 74
2022-06-02 16:00 | 12.0351 | 75 | 2022-06-02 16:00 | 4.0959 | 75
2022-06-02 17:00 | 12.0351 | 71 | 2022-06-02 17:00 | 4.0959 | 71
2022-06-02 18:00 | 12.0351 | 71 | 2022-06-02 18:00 | 4.0959 | 71
2022-06-02 19:00 | 2.8033 | 69 | 2022-06-02 19:00 | 2.3596 | 69
2022-06-02 20:00 | 2.8042 | 68 | 2022-06-02 20:00 | 2.3599 | 68
2022-06-02 21:00 | 2.7962 | 66 | 2022-06-02 21:00 | 2.3577 | 66
2022-06-02 22:00 | 2.7992 | 65 | 2022-06-02 22:00 | 2.3585 | 65
2022-06-02 23:00 | 2.8183 | 65 | 2022-06-02 23:00 | 2.3637 | 65
2022-06-03 | 2.8002 | 66 | 2022-06-03 | 2.3588 | 66
2022-06-03 01:00 | 2.7842 | 66 | 2022-06-03 01:00 | 2.3543 | 66
2022-06-03 02:00 | 2.7831 | 65 | 2022-06-03 02:00 | 2.354 | 65
2022-06-03 03:00 | 2.7531 | 66 | 2022-06-03 03:00 | 2.3453 | 66
2022-06-03 04:00 | 2.7621 | 66 | 2022-06-03 04:00 | 2.348 | 66
2022-06-03 05:00 | 2.8073 | 66 | 2022-06-03 05:00 | 2.3607 | 66
2022-06-03 06:00 | 12.0351 | 65 | 2022-06-03 06:00 | 4.0959 | 65
2022-06-03 07:00 | 12.0351 | 65 | 2022-06-03 07:00 | 4.0959 | 65
2022-06-03 08:00 | 12.0351 | 64 | 2022-06-03 08:00 | 4.0959 | 64
2022-06-03 09:00 | 12.0351 | 64 | 2022-06-03 09:00 | 4.0959 | 64
2022-06-03 10:00 | 12.0351 | 67 | 2022-06-03 10:00 | 4.0959 | 67
2022-06-03 11:00 | 12.0351 | 66 | 2022-06-03 11:00 | 4.0959 | 66
2022-06-03 12:00 | 12.0351 | 66 | 2022-06-03 12:00 | 4.0959 | 66
2022-06-03 13:00 | 12.0351 | 68 | 2022-06-03 13:00 | 4.0959 | 68
2022-06-03 14:00 | 12.0351 | 68 | 2022-06-03 14:00 | 4.0959 | 68
2022-06-03 15:00 | 12.0351 | 68 | 2022-06-03 15:00 | 4.0959 | 68
2022-06-03 16:00 | 12.0351 | 68 | 2022-06-03 16:00 | 4.0959 | 68
2022-06-03 17:00 | 12.0351 | 67 | 2022-06-03 17:00 | 4.0959 | 67
2022-06-03 18:00 | 12.0351 | 68 | 2022-06-03 18:00 | 4.0959 | 68
2022-06-03 19:00 | 12.0351 | 67 | 2022-06-03 19:00 | 4.0959 | 67
2022-06-03 20:00 | 6.8727 | 65 | 2022-06-03 20:00 | 4.0959 | 65
2022-06-03 21:00 | 2.8485 | 64 | 2022-06-03 21:00 | 2.3716 | 64
2022-06-03 22:00 | 2.8606 | 63 | 2022-06-03 22:00 | 2.3746 | 63
2022-06-03 23:00 | 2.8435 | 63 | 2022-06-03 23:00 | 2.3703 | 63
2022-06-04 | 2.8113 | 63 | 2022-06-04 | 2.3618 | 63
2022-06-04 01:00 | 2.7501 | 61 | 2022-06-04 01:00 | 2.3444 | 61
2022-06-04 02:00 | 2.7912 | 62 | 2022-06-04 02:00 | 2.3562 | 62
2022-06-04 03:00 | 2.8243 | 62 | 2022-06-04 03:00 | 2.3653 | 62
2022-06-04 04:00 | 2.8033 | 59 | 2022-06-04 04:00 | 2.3596 | 59
2022-06-04 05:00 | 2.8033 | 59 | 2022-06-04 05:00 | 2.3596 | 59
2022-06-04 06:00 | 2.7871 | 60 | 2022-06-04 06:00 | 2.3551 | 60
2022-06-04 07:00 | 2.8203 | 64 | 2022-06-04 07:00 | 2.3642 | 64
2022-06-04 08:00 | 2.7791 | 69 | 2022-06-04 08:00 | 2.3529 | 69
2022-06-04 09:00 | 2.7842 | 71 | 2022-06-04 09:00 | 2.3543 | 71
2022-06-04 10:00 | 2.8042 | 74 | 2022-06-04 10:00 | 2.3599 | 74
2022-06-04 11:00 | 2.7751 | 72 | 2022-06-04 11:00 | 2.3517 | 72
2022-06-04 12:00 | 2.7711 | 71 | 2022-06-04 12:00 | 2.3506 | 71
2022-06-04 13:00 | 2.7952 | 72 | 2022-06-04 13:00 | 2.3574 | 72
2022-06-04 14:00 | 2.7762 | 71 | 2022-06-04 14:00 | 2.352 | 71
2022-06-04 15:00 | 2.7641 | 71 | 2022-06-04 15:00 | 2.3485 | 71
2022-06-04 16:00 | 2.7722 | 72 | 2022-06-04 16:00 | 2.3509 | 72
2022-06-04 17:00 | 2.7401 | 71 | 2022-06-04 17:00 | 2.3414 | 71
2022-06-04 18:00 | 2.7351 | 69 | 2022-06-04 18:00 | 2.3399 | 69
2022-06-04 19:00 | 2.7331 | 68 | 2022-06-04 19:00 | 2.3393 | 68
2022-06-04 20:00 | 2.7561 | 66 | 2022-06-04 20:00 | 2.3462 | 66
2022-06-04 21:00 | 2.7301 | 64 | 2022-06-04 21:00 | 2.3384 | 64
2022-06-04 22:00 | 2.7311 | 64 | 2022-06-04 22:00 | 2.3387 | 64
2022-06-04 23:00 | 2.7371 | 64 | 2022-06-04 23:00 | 2.3405 | 64
2022-06-05 | 2.7831 | 63 | 2022-06-05 | 2.354 | 63
2022-06-05 01:00 | 2.7631 | 64 | 2022-06-05 01:00 | 2.3483 | 64
2022-06-05 02:00 | 2.7852 | 63 | 2022-06-05 02:00 | 2.3546 | 63
2022-06-05 03:00 | 2.7621 | 62 | 2022-06-05 03:00 | 2.348 | 62
2022-06-05 04:00 | 2.7701 | 58 | 2022-06-05 04:00 | 2.3503 | 58
2022-06-05 05:00 | 2.8002 | 56 | 2022-06-05 05:00 | 2.3588 | 56
2022-06-05 06:00 | 2.7992 | 57 | 2022-06-05 06:00 | 2.3585 | 57
2022-06-05 07:00 | 2.8133 | 61 | 2022-06-05 07:00 | 2.3623 | 61
2022-06-05 08:00 | 2.8123 | 64 | 2022-06-05 08:00 | 2.362 | 64
2022-06-05 09:00 | 2.8294 | 66 | 2022-06-05 09:00 | 2.3666 | 66
2022-06-05 10:00 | 2.8284 | 68 | 2022-06-05 10:00 | 2.3663 | 68
2022-06-05 11:00 | 2.7731 | 71 | 2022-06-05 11:00 | 2.3512 | 71
2022-06-05 12:00 | 2.8052 | 72 | 2022-06-05 12:00 | 2.3601 | 72
2022-06-05 13:00 | 2.8264 | 74 | 2022-06-05 13:00 | 2.3658 | 74
2022-06-05 14:00 | 2.8062 | 70 | 2022-06-05 14:00 | 2.3604 | 70
2022-06-05 15:00 | 2.8062 | 71 | 2022-06-05 15:00 | 2.3604 | 71
2022-06-05 16:00 | 2.7831 | 71 | 2022-06-05 16:00 | 2.354 | 71
2022-06-05 17:00 | 2.7551 | 71 | 2022-06-05 17:00 | 2.3459 | 71
2022-06-05 18:00 | 2.7601 | 70 | 2022-06-05 18:00 | 2.3474 | 70
2022-06-05 19:00 | 2.7491 | 68 | 2022-06-05 19:00 | 2.3441 | 68
2022-06-05 20:00 | 2.7661 | 66 | 2022-06-05 20:00 | 2.3491 | 66
2022-06-05 21:00 | 2.7651 | 62 | 2022-06-05 21:00 | 2.3488 | 62
2022-06-05 22:00 | 2.7571 | 61 | 2022-06-05 22:00 | 2.3465 | 61
2022-06-05 23:00 | 2.7251 | 62 | 2022-06-05 23:00 | 2.3369 | 62
2022-06-06 | 2.7922 | 62 | 2022-06-06 | 2.3565 | 62
2022-06-06 01:00 | 2.7751 | 63 | 2022-06-06 01:00 | 2.3517 | 63
2022-06-06 02:00 | 2.7902 | 63 | 2022-06-06 02:00 | 2.356 | 63
2022-06-06 03:00 | 2.7972 | 63 | 2022-06-06 03:00 | 2.3579 | 63
2022-06-06 04:00 | 2.8223 | 62 | 2022-06-06 04:00 | 2.3647 | 62
2022-06-06 05:00 | 2.8102 | 62 | 2022-06-06 05:00 | 2.3615 | 62
2022-06-06 06:00 | 9.1642 | 61 | 2022-06-06 06:00 | 4.0959 | 61
2022-06-06 07:00 | 12.0351 | 66 | 2022-06-06 07:00 | 4.0959 | 66
2022-06-06 08:00 | 12.0351 | 69 | 2022-06-06 08:00 | 4.0959 | 69
2022-06-06 09:00 | 12.0351 | 72 | 2022-06-06 09:00 | 4.0959 | 72
2022-06-06 10:00 | 12.0351 | 74 | 2022-06-06 10:00 | 4.0959 | 74
2022-06-06 11:00 | 12.0351 | 75 | 2022-06-06 11:00 | 4.0959 | 75
2022-06-06 12:00 | 12.0351 | 77 | 2022-06-06 12:00 | 4.0959 | 77
2022-06-06 13:00 | 12.0351 | 74 | 2022-06-06 13:00 | 4.0959 | 74
2022-06-06 14:00 | 12.0351 | 75 | 2022-06-06 14:00 | 4.0959 | 75
2022-06-06 15:00 | 12.0351 | 76 | 2022-06-06 15:00 | 4.0959 | 76
2022-06-06 16:00 | 12.0351 | 75 | 2022-06-06 16:00 | 4.0959 | 75
2022-06-06 17:00 | 10.3876 | 74 | 2022-06-06 17:00 | 4.0959 | 74
2022-06-06 18:00 | 2.7421 | 72 | 2022-06-06 18:00 | 2.342 | 72
2022-06-06 19:00 | 2.7741 | 70 | 2022-06-06 19:00 | 2.3514 | 70
2022-06-06 20:00 | 2.7952 | 68 | 2022-06-06 20:00 | 2.3574 | 68
2022-06-06 21:00 | 2.8012 | 67 | 2022-06-06 21:00 | 2.359 | 67
2022-06-06 22:00 | 2.8536 | 67 | 2022-06-06 22:00 | 2.3729 | 67
2022-06-06 23:00 | 2.7781 | 67 | 2022-06-06 23:00 | 2.3526 | 67
2022-06-07 | 2.8223 | 65 | 2022-06-07 | 2.3647 | 65
2022-06-07 01:00 | 2.8143 | 63 | 2022-06-07 01:00 | 2.3626 | 63
2022-06-07 02:00 | 2.8033 | 64 | 2022-06-07 02:00 | 2.3596 | 64
2022-06-07 03:00 | 2.8274 | 61 | 2022-06-07 03:00 | 2.3661 | 61
2022-06-07 04:00 | 2.8223 | 60 | 2022-06-07 04:00 | 2.3647 | 60
2022-06-07 05:00 | 2.8667 | 59 | 2022-06-07 05:00 | 2.3762 | 59
2022-06-07 06:00 | 12.0351 | 60 | 2022-06-07 06:00 | 4.0959 | 60
2022-06-07 07:00 | 12.0351 | 66 | 2022-06-07 07:00 | 4.0959 | 66
2022-06-07 08:00 | 12.0351 | 68 | 2022-06-07 08:00 | 4.0959 | 68
2022-06-07 09:00 | 12.0351 | 70 | 2022-06-07 09:00 | 4.0959 | 70
2022-06-07 10:00 | 12.0351 | 70 | 2022-06-07 10:00 | 4.0959 | 70
2022-06-07 11:00 | 12.0351 | 72 | 2022-06-07 11:00 | 4.0959 | 72
2022-06-07 12:00 | 12.0351 | 72 | 2022-06-07 12:00 | 4.0959 | 72
2022-06-07 13:00 | 12.0351 | 74 | 2022-06-07 13:00 | 4.0959 | 74
2022-06-07 14:00 | 12.0351 | 74 | 2022-06-07 14:00 | 4.0959 | 74
2022-06-07 15:00 | 12.0351 | 75 | 2022-06-07 15:00 | 4.0959 | 75
2022-06-07 16:00 | 12.0351 | 71 | 2022-06-07 16:00 | 4.0959 | 71
2022-06-07 17:00 | 12.4137 | 71 | 2022-06-07 17:00 | 4.0959 | 71
2022-06-07 18:00 | 2.8445 | 71 | 2022-06-07 18:00 | 2.3705 | 71
2022-06-07 19:00 | 2.8062 | 70 | 2022-06-07 19:00 | 2.3604 | 70
2022-06-07 20:00 | 2.7681 | 69 | 2022-06-07 20:00 | 2.3497 | 69
2022-06-07 21:00 | 2.7611 | 69 | 2022-06-07 21:00 | 2.3477 | 69
2022-06-07 22:00 | 2.8102 | 68 | 2022-06-07 22:00 | 2.3615 | 68
2022-06-07 23:00 | 2.8133 | 67 | 2022-06-07 23:00 | 2.3623 | 67
2022-06-08 | 2.7762 | 67 | 2022-06-08 | 2.352 | 67
2022-06-08 01:00 | 2.7491 | 67 | 2022-06-08 01:00 | 2.3441 | 67
2022-06-08 02:00 | 2.7391 | 67 | 2022-06-08 02:00 | 2.3411 | 67
2022-06-08 03:00 | 2.7281 | 67 | 2022-06-08 03:00 | 2.3378 | 67
2022-06-08 04:00 | 2.7671 | 67 | 2022-06-08 04:00 | 2.3494 | 67
2022-06-08 05:00 | 2.8033 | 67 | 2022-06-08 05:00 | 2.3596 | 67
2022-06-08 06:00 | 12.0351 | 67 | 2022-06-08 06:00 | 4.0959 | 67
2022-06-08 07:00 | 12.0351 | 68 | 2022-06-08 07:00 | 4.0959 | 68
2022-06-08 08:00 | 12.0351 | 71 | 2022-06-08 08:00 | 4.0959 | 71
2022-06-08 09:00 | 12.0351 | 74 | 2022-06-08 09:00 | 4.0959 | 74
2022-06-08 10:00 | 12.0351 | 78 | 2022-06-08 10:00 | 4.0959 | 78
2022-06-08 11:00 | 12.0351 | 80 | 2022-06-08 11:00 | 4.0959 | 80
2022-06-08 12:00 | 12.0351 | 82 | 2022-06-08 12:00 | 4.0959 | 82
2022-06-08 13:00 | 12.0351 | 83 | 2022-06-08 13:00 | 4.0959 | 83
2022-06-08 14:00 | 12.0351 | 83 | 2022-06-08 14:00 | 4.0959 | 83
2022-06-08 15:00 | 12.0351 | 83 | 2022-06-08 15:00 | 4.0959 | 83
2022-06-08 16:00 | 12.0351 | 83 | 2022-06-08 16:00 | 4.0959 | 83
2022-06-08 17:00 | 12.0351 | 78 | 2022-06-08 17:00 | 4.0959 | 78
2022-06-08 18:00 | 4.4683 | 78 | 2022-06-08 18:00 | 2.6942 | 78
2022-06-08 19:00 | 2.7962 | 76 | 2022-06-08 19:00 | 2.3577 | 76
2022-06-08 20:00 | 2.7791 | 73 | 2022-06-08 20:00 | 2.3529 | 73
2022-06-08 21:00 | 2.8002 | 70 | 2022-06-08 21:00 | 2.3588 | 70
2022-06-08 22:00 | 2.7601 | 70 | 2022-06-08 22:00 | 2.3474 | 70
2022-06-08 23:00 | 2.7411 | 70 | 2022-06-08 23:00 | 2.3417 | 70
2022-06-09 | 2.7842 | 69 | 2022-06-09 | 2.3543 | 69
2022-06-09 01:00 | 2.7581 | 69 | 2022-06-09 01:00 | 2.3468 | 69
2022-06-09 02:00 | 2.7301 | 69 | 2022-06-09 02:00 | 2.3384 | 69
2022-06-09 03:00 | 2.7491 | 69 | 2022-06-09 03:00 | 2.3441 | 69
2022-06-09 04:00 | 2.7391 | 69 | 2022-06-09 04:00 | 2.3411 | 69
2022-06-09 05:00 | 2.7611 | 69 | 2022-06-09 05:00 | 2.3477 | 69
2022-06-09 06:00 | 12.0351 | 69 | 2022-06-09 06:00 | 4.0959 | 69
2022-06-09 07:00 | 12.0351 | 68 | 2022-06-09 07:00 | 4.0959 | 68
2022-06-09 08:00 | 12.0351 | 69 | 2022-06-09 08:00 | 4.0959 | 69
2022-06-09 09:00 | 12.0351 | 70 | 2022-06-09 09:00 | 4.0959 | 70
2022-06-09 10:00 | 12.0351 | 75 | 2022-06-09 10:00 | 4.0959 | 75
2022-06-09 11:00 | 12.0351 | 79 | 2022-06-09 11:00 | 4.0959 | 79
2022-06-09 12:00 | 12.0351 | 81 | 2022-06-09 12:00 | 4.0959 | 81
2022-06-09 13:00 | 12.0351 | 82 | 2022-06-09 13:00 | 4.0959 | 82
2022-06-09 14:00 | 12.0351 | 83 | 2022-06-09 14:00 | 4.0959 | 83
2022-06-09 15:00 | 12.0351 | 83 | 2022-06-09 15:00 | 4.0959 | 83
2022-06-09 16:00 | 12.0351 | 82 | 2022-06-09 16:00 | 4.0959 | 82
2022-06-09 17:00 | 12.0351 | 81 | 2022-06-09 17:00 | 4.0959 | 81
2022-06-09 18:00 | 12.0351 | 80 | 2022-06-09 18:00 | 4.0959 | 80
2022-06-09 19:00 | 12.0351 | 80 | 2022-06-09 19:00 | 4.0959 | 80
2022-06-09 20:00 | 12.0351 | 76 | 2022-06-09 20:00 | 4.0959 | 76
2022-06-09 21:00 | 12.0351 | 74 | 2022-06-09 21:00 | 4.0959 | 74
2022-06-09 22:00 | 5.3226 | 72 | 2022-06-09 22:00 | 3.4743 | 72
2022-06-09 23:00 | 2.8414 | 69 | 2022-06-09 23:00 | 2.3698 | 69
2022-06-10 | 2.7762 | 69 | 2022-06-10 | 2.352 | 69
2022-06-10 01:00 | 2.7802 | 66 | 2022-06-10 01:00 | 2.3532 | 66
2022-06-10 02:00 | 2.8304 | 65 | 2022-06-10 02:00 | 2.3669 | 65
2022-06-10 03:00 | 2.7942 | 64 | 2022-06-10 03:00 | 2.3571 | 64
2022-06-10 04:00 | 2.7731 | 65 | 2022-06-10 04:00 | 2.3512 | 65
2022-06-10 05:00 | 2.8193 | 64 | 2022-06-10 05:00 | 2.3639 | 64
2022-06-10 06:00 | 12.0351 | 64 | 2022-06-10 06:00 | 4.0959 | 64
2022-06-10 07:00 | 12.0351 | 66 | 2022-06-10 07:00 | 4.0959 | 66
2022-06-10 08:00 | 12.0351 | 68 | 2022-06-10 08:00 | 4.0959 | 68
2022-06-10 09:00 | 12.0351 | 71 | 2022-06-10 09:00 | 4.0959 | 71
2022-06-10 10:00 | 12.0351 | 72 | 2022-06-10 10:00 | 4.0959 | 72
2022-06-10 11:00 | 12.0351 | 74 | 2022-06-10 11:00 | 4.0959 | 74
2022-06-10 12:00 | 12.0351 | 75 | 2022-06-10 12:00 | 4.0959 | 75
2022-06-10 13:00 | 12.0351 | 78 | 2022-06-10 13:00 | 4.0959 | 78
2022-06-10 14:00 | 12.0351 | 79 | 2022-06-10 14:00 | 4.0959 | 79
2022-06-10 15:00 | 12.0351 | 80 | 2022-06-10 15:00 | 4.0959 | 80
2022-06-10 16:00 | 12.0351 | 79 | 2022-06-10 16:00 | 4.0959 | 79
2022-06-10 17:00 | 12.0351 | 77 | 2022-06-10 17:00 | 4.0959 | 77
2022-06-10 18:00 | 2.895 | 72 | 2022-06-10 18:00 | 2.383 | 72
2022-06-10 19:00 | 2.8889 | 71 | 2022-06-10 19:00 | 2.3816 | 71
2022-06-10 20:00 | 2.8234 | 70 | 2022-06-10 20:00 | 2.365 | 70
2022-06-10 21:00 | 2.8506 | 75 | 2022-06-10 21:00 | 2.3721 | 75
2022-06-10 22:00 | 2.8183 | 73 | 2022-06-10 22:00 | 2.3637 | 73
2022-06-10 23:00 | 2.7912 | 73 | 2022-06-10 23:00 | 2.3562 | 73
2022-06-11 | 2.7802 | 72 | 2022-06-11 | 2.3532 | 72
2022-06-11 01:00 | 2.7671 | 69 | 2022-06-11 01:00 | 2.3494 | 69
2022-06-11 02:00 | 2.7711 | 67 | 2022-06-11 02:00 | 2.3506 | 67
2022-06-11 03:00 | 2.7812 | 67 | 2022-06-11 03:00 | 2.3534 | 67
2022-06-11 04:00 | 2.7571 | 68 | 2022-06-11 04:00 | 2.3465 | 68
2022-06-11 05:00 | 2.7731 | 65 | 2022-06-11 05:00 | 2.3512 | 65
2022-06-11 06:00 | 2.7411 | 66 | 2022-06-11 06:00 | 2.3417 | 66
2022-06-11 07:00 | 2.7821 | 68 | 2022-06-11 07:00 | 2.3537 | 68
2022-06-11 08:00 | 2.8284 | 69 | 2022-06-11 08:00 | 2.3663 | 69
2022-06-11 09:00 | 2.8173 | 72 | 2022-06-11 09:00 | 2.3634 | 72
2022-06-11 10:00 | 2.7972 | 76 | 2022-06-11 10:00 | 2.3579 | 76
2022-06-11 11:00 | 2.8093 | 76 | 2022-06-11 11:00 | 2.3612 | 76
2022-06-11 12:00 | 2.8133 | 79 | 2022-06-11 12:00 | 2.3623 | 79
2022-06-11 13:00 | 2.7852 | 72 | 2022-06-11 13:00 | 2.3546 | 72
2022-06-11 14:00 | 2.8374 | 72 | 2022-06-11 14:00 | 2.3687 | 72
2022-06-11 15:00 | 2.8113 | 71 | 2022-06-11 15:00 | 2.3618 | 71
2022-06-11 16:00 | 2.7942 | 71 | 2022-06-11 16:00 | 2.3571 | 71
2022-06-11 17:00 | 2.8203 | 72 | 2022-06-11 17:00 | 2.3642 | 72
2022-06-11 18:00 | 2.7821 | 70 | 2022-06-11 18:00 | 2.3537 | 70
2022-06-11 19:00 | 2.8264 | 70 | 2022-06-11 19:00 | 2.3658 | 70
2022-06-11 20:00 | 2.8404 | 70 | 2022-06-11 20:00 | 2.3695 | 70
2022-06-11 21:00 | 2.8052 | 69 | 2022-06-11 21:00 | 2.3601 | 69
2022-06-11 22:00 | 2.8253 | 68 | 2022-06-11 22:00 | 2.3655 | 68
2022-06-11 23:00 | 2.7892 | 67 | 2022-06-11 23:00 | 2.3557 | 67
2022-06-12 | 2.7651 | 66 | 2022-06-12 | 2.3488 | 66
2022-06-12 01:00 | 2.7972 | 66 | 2022-06-12 01:00 | 2.3579 | 66
2022-06-12 02:00 | 2.7972 | 65 | 2022-06-12 02:00 | 2.3579 | 65
2022-06-12 03:00 | 2.8153 | 64 | 2022-06-12 03:00 | 2.3629 | 64
2022-06-12 04:00 | 2.8475 | 64 | 2022-06-12 04:00 | 2.3713 | 64
2022-06-12 05:00 | 2.8617 | 65 | 2022-06-12 05:00 | 2.3749 | 65
2022-06-12 06:00 | 2.8475 | 65 | 2022-06-12 06:00 | 2.3713 | 65
2022-06-12 07:00 | 2.8445 | 66 | 2022-06-12 07:00 | 2.3705 | 66
2022-06-12 08:00 | 2.8646 | 66 | 2022-06-12 08:00 | 2.3756 | 66
2022-06-12 09:00 | 2.8909 | 64 | 2022-06-12 09:00 | 2.3821 | 64
2022-06-12 10:00 | 2.8778 | 64 | 2022-06-12 10:00 | 2.3789 | 64
2022-06-12 11:00 | 2.8213 | 65 | 2022-06-12 11:00 | 2.3645 | 65
2022-06-12 12:00 | 2.8586 | 65 | 2022-06-12 12:00 | 2.3741 | 65
2022-06-12 13:00 | 2.8445 | 66 | 2022-06-12 13:00 | 2.3705 | 66
2022-06-12 14:00 | 2.8455 | 67 | 2022-06-12 14:00 | 2.3708 | 67
2022-06-12 15:00 | 2.8364 | 70 | 2022-06-12 15:00 | 2.3685 | 70
2022-06-12 16:00 | 2.8586 | 69 | 2022-06-12 16:00 | 2.3741 | 69
2022-06-12 17:00 | 2.8697 | 72 | 2022-06-12 17:00 | 2.3769 | 72
2022-06-12 18:00 | 2.8173 | 71 | 2022-06-12 18:00 | 2.3634 | 71
2022-06-12 19:00 | 2.8576 | 70 | 2022-06-12 19:00 | 2.3739 | 70
2022-06-12 20:00 | 2.8073 | 69 | 2022-06-12 20:00 | 2.3607 | 69
2022-06-12 21:00 | 2.8083 | 68 | 2022-06-12 21:00 | 2.361 | 68
2022-06-12 22:00 | 2.8133 | 68 | 2022-06-12 22:00 | 2.3623 | 68
2022-06-12 23:00 | 2.7902 | 68 | 2022-06-12 23:00 | 2.356 | 68
2022-06-13 | 2.8093 | 68 | 2022-06-13 | 2.3612 | 68
2022-06-13 01:00 | 2.8133 | 68 | 2022-06-13 01:00 | 2.3623 | 68
2022-06-13 02:00 | 2.7671 | 67 | 2022-06-13 02:00 | 2.3494 | 67
2022-06-13 03:00 | 2.8042 | 68 | 2022-06-13 03:00 | 2.3599 | 68
2022-06-13 04:00 | 2.8304 | 67 | 2022-06-13 04:00 | 2.3669 | 67
2022-06-13 05:00 | 2.8596 | 66 | 2022-06-13 05:00 | 2.3744 | 66
2022-06-13 06:00 | 12.0351 | 67 | 2022-06-13 06:00 | 4.0959 | 67
2022-06-13 07:00 | 12.0351 | 68 | 2022-06-13 07:00 | 4.0959 | 68
2022-06-13 08:00 | 12.0351 | 69 | 2022-06-13 08:00 | 4.0959 | 69
2022-06-13 09:00 | 12.0351 | 72 | 2022-06-13 09:00 | 4.0959 | 72
2022-06-13 10:00 | 12.0351 | 76 | 2022-06-13 10:00 | 4.0959 | 76
2022-06-13 11:00 | 12.0351 | 77 | 2022-06-13 11:00 | 4.0959 | 77
2022-06-13 12:00 | 12.0351 | 77 | 2022-06-13 12:00 | 4.0959 | 77
2022-06-13 13:00 | 12.0351 | 79 | 2022-06-13 13:00 | 4.0959 | 79
2022-06-13 14:00 | 12.0351 | 75 | 2022-06-13 14:00 | 4.0959 | 75
2022-06-13 15:00 | 12.0351 | 77 | 2022-06-13 15:00 | 4.0959 | 77
2022-06-13 16:00 | 12.0351 | 79 | 2022-06-13 16:00 | 4.0959 | 79
2022-06-13 17:00 | 12.0351 | 79 | 2022-06-13 17:00 | 4.0959 | 79
2022-06-13 18:00 | 12.0351 | 78 | 2022-06-13 18:00 | 4.0959 | 78
2022-06-13 19:00 | 7.7841 | 76 | 2022-06-13 19:00 | 4.0959 | 76
2022-06-13 20:00 | 3.6363 | 76 | 2022-06-13 20:00 | 2.4999 | 76
2022-06-13 21:00 | 3.6113 | 74 | 2022-06-13 21:00 | 2.4967 | 74
2022-06-13 22:00 | 3.5947 | 76 | 2022-06-13 22:00 | 2.4945 | 76
2022-06-13 23:00 | 3.554 | 77 | 2022-06-13 23:00 | 2.4894 | 77
2022-06-14 | 3.5676 | 75 | 2022-06-14 | 2.4911 | 75
2022-06-14 01:00 | 3.5592 | 73 | 2022-06-14 01:00 | 2.49 | 73
2022-06-14 02:00 | 3.5467 | 73 | 2022-06-14 02:00 | 2.4884 | 73
2022-06-14 03:00 | 3.5489 | 70 | 2022-06-14 03:00 | 2.4887 | 70
2022-06-14 04:00 | 3.5394 | 69 | 2022-06-14 04:00 | 2.4875 | 69
2022-06-14 05:00 | 3.5811 | 68 | 2022-06-14 05:00 | 2.4928 | 68
2022-06-14 06:00 | 12.0351 | 68 | 2022-06-14 06:00 | 4.0959 | 68
2022-06-14 07:00 | 12.0351 | 67 | 2022-06-14 07:00 | 4.0959 | 67
2022-06-14 08:00 | 12.0351 | 68 | 2022-06-14 08:00 | 4.0959 | 68
2022-06-14 09:00 | 12.0351 | 69 | 2022-06-14 09:00 | 4.0959 | 69
2022-06-14 10:00 | 12.0351 | 70 | 2022-06-14 10:00 | 4.0959 | 70
2022-06-14 11:00 | 12.0351 | 73 | 2022-06-14 11:00 | 4.0959 | 73
2022-06-14 12:00 | 12.0351 | 77 | 2022-06-14 12:00 | 4.0959 | 77
2022-06-14 13:00 | 12.0351 | 78 | 2022-06-14 13:00 | 4.0959 | 78
2022-06-14 14:00 | 12.0351 | 76 | 2022-06-14 14:00 | 4.0959 | 76
2022-06-14 15:00 | 12.0351 | 75 | 2022-06-14 15:00 | 4.0959 | 75
2022-06-14 16:00 | 12.0351 | 76 | 2022-06-14 16:00 | 4.0959 | 76
2022-06-14 17:00 | 6.0663 | 77 | 2022-06-14 17:00 | 4.0959 | 77
2022-06-14 18:00 | 2.8838 | 77 | 2022-06-14 18:00 | 2.3804 | 77
2022-06-14 19:00 | 2.9031 | 77 | 2022-06-14 19:00 | 2.3849 | 77
2022-06-14 20:00 | 2.8566 | 79 | 2022-06-14 20:00 | 2.3736 | 79
2022-06-14 21:00 | 2.8536 | 76 | 2022-06-14 21:00 | 2.3729 | 76
2022-06-14 22:00 | 2.8264 | 68 | 2022-06-14 22:00 | 2.3658 | 68
2022-06-14 23:00 | 2.8203 | 69 | 2022-06-14 23:00 | 2.3642 | 69
2022-06-15 | 2.8556 | 67 | 2022-06-15 | 2.3734 | 67
2022-06-15 01:00 | 2.8073 | 72 | 2022-06-15 01:00 | 2.3607 | 72
2022-06-15 02:00 | 2.8213 | 70 | 2022-06-15 02:00 | 2.3645 | 70
2022-06-15 03:00 | 2.7982 | 69 | 2022-06-15 03:00 | 2.3582 | 69
2022-06-15 04:00 | 2.8243 | 68 | 2022-06-15 04:00 | 2.3653 | 68
2022-06-15 05:00 | 2.8586 | 67 | 2022-06-15 05:00 | 2.3741 | 67
2022-06-15 06:00 | 12.0351 | 67 | 2022-06-15 06:00 | 4.0959 | 67
2022-06-15 07:00 | 12.0351 | 71 | 2022-06-15 07:00 | 4.0959 | 71
2022-06-15 08:00 | 12.0351 | 75 | 2022-06-15 08:00 | 4.0959 | 75
2022-06-15 09:00 | 12.0351 | 76 | 2022-06-15 09:00 | 4.0959 | 76
2022-06-15 10:00 | 12.0351 | 79 | 2022-06-15 10:00 | 4.0959 | 79
2022-06-15 11:00 | 12.0351 | 77 | 2022-06-15 11:00 | 4.0959 | 77
2022-06-15 12:00 | 12.0351 | 76 | 2022-06-15 12:00 | 4.0959 | 76
2022-06-15 13:00 | 12.0351 | 74 | 2022-06-15 13:00 | 4.0959 | 74
2022-06-15 14:00 | 12.0351 | 74 | 2022-06-15 14:00 | 4.0959 | 74
2022-06-15 15:00 | 12.0351 | 75 | 2022-06-15 15:00 | 4.0959 | 75
2022-06-15 16:00 | 12.0351 | 73 | 2022-06-15 16:00 | 4.0959 | 73
2022-06-15 17:00 | 5.6591 | 72 | 2022-06-15 17:00 | 4.2434 | 72
2022-06-15 18:00 | 2.8566 | 71 | 2022-06-15 18:00 | 2.3736 | 71
2022-06-15 19:00 | 2.9021 | 70 | 2022-06-15 19:00 | 2.3847 | 70
2022-06-15 20:00 | 2.8506 | 68 | 2022-06-15 20:00 | 2.3721 | 68
2022-06-15 21:00 | 2.8828 | 67 | 2022-06-15 21:00 | 2.3801 | 67
2022-06-15 22:00 | 2.8767 | 67 | 2022-06-15 22:00 | 2.3786 | 67
2022-06-15 23:00 | 2.8617 | 67 | 2022-06-15 23:00 | 2.3749 | 67
2022-06-16 | 2.8717 | 67 | 2022-06-16 | 2.3774 | 67
2022-06-16 01:00 | 2.8687 | 67 | 2022-06-16 01:00 | 2.3766 | 67
2022-06-16 02:00 | 2.8234 | 67 | 2022-06-16 02:00 | 2.365 | 67
2022-06-16 03:00 | 2.8445 | 68 | 2022-06-16 03:00 | 2.3705 | 68
2022-06-16 04:00 | 2.8324 | 67 | 2022-06-16 04:00 | 2.3674 | 67
2022-06-16 05:00 | 2.8536 | 67 | 2022-06-16 05:00 | 2.3729 | 67
2022-06-16 06:00 | 12.0351 | 68 | 2022-06-16 06:00 | 4.0959 | 68
2022-06-16 07:00 | 12.0351 | 68 | 2022-06-16 07:00 | 4.0959 | 68
2022-06-16 08:00 | 12.0351 | 66 | 2022-06-16 08:00 | 4.0959 | 66
2022-06-16 09:00 | 12.0351 | 65 | 2022-06-16 09:00 | 4.0959 | 65
2022-06-16 10:00 | 12.0351 | 66 | 2022-06-16 10:00 | 4.0959 | 66
2022-06-16 11:00 | 12.0351 | 68 | 2022-06-16 11:00 | 4.0959 | 68
2022-06-16 12:00 | 12.0351 | 69 | 2022-06-16 12:00 | 4.0959 | 69
2022-06-16 13:00 | 12.0351 | 71 | 2022-06-16 13:00 | 4.0959 | 71
2022-06-16 14:00 | 12.0351 | 69 | 2022-06-16 14:00 | 4.0959 | 69
2022-06-16 15:00 | 12.0351 | 70 | 2022-06-16 15:00 | 4.0959 | 70
2022-06-16 16:00 | 12.0351 | 70 | 2022-06-16 16:00 | 4.0959 | 70
2022-06-16 17:00 | 5.0719 | 70 | 2022-06-16 17:00 | 3.1268 | 70
2022-06-16 18:00 | 2.8173 | 69 | 2022-06-16 18:00 | 2.3634 | 69
2022-06-16 19:00 | 2.8617 | 69 | 2022-06-16 19:00 | 2.3749 | 69
2022-06-16 20:00 | 2.8425 | 69 | 2022-06-16 20:00 | 2.37 | 69
2022-06-16 21:00 | 2.8123 | 69 | 2022-06-16 21:00 | 2.362 | 69
2022-06-16 22:00 | 2.8617 | 69 | 2022-06-16 22:00 | 2.3749 | 69
2022-06-16 23:00 | 2.8304 | 69 | 2022-06-16 23:00 | 2.3669 | 69
2022-06-17 | 2.8435 | 69 | 2022-06-17 | 2.3703 | 69
2022-06-17 01:00 | 2.8012 | 69 | 2022-06-17 01:00 | 2.359 | 69
2022-06-17 02:00 | 2.7882 | 69 | 2022-06-17 02:00 | 2.3554 | 69
2022-06-17 03:00 | 2.8002 | 69 | 2022-06-17 03:00 | 2.3588 | 69
2022-06-17 04:00 | 2.7992 | 68 | 2022-06-17 04:00 | 2.3585 | 68
2022-06-17 05:00 | 2.8536 | 69 | 2022-06-17 05:00 | 2.3729 | 69
2022-06-17 06:00 | 12.0351 | 69 | 2022-06-17 06:00 | 4.0959 | 69
2022-06-17 07:00 | 12.0351 | 71 | 2022-06-17 07:00 | 4.0959 | 71
2022-06-17 08:00 | 12.0351 | 71 | 2022-06-17 08:00 | 4.0959 | 71
2022-06-17 09:00 | 12.0351 | 73 | 2022-06-17 09:00 | 4.0959 | 73
2022-06-17 10:00 | 12.0351 | 76 | 2022-06-17 10:00 | 4.0959 | 76
2022-06-17 11:00 | 12.0351 | 80 | 2022-06-17 11:00 | 4.0959 | 80
2022-06-17 12:00 | 12.0351 | 80 | 2022-06-17 12:00 | 4.0959 | 80
2022-06-17 13:00 | 12.0351 | 83 | 2022-06-17 13:00 | 4.0959 | 83
2022-06-17 14:00 | 12.0351 | 91 | 2022-06-17 14:00 | 4.0959 | 91
2022-06-17 15:00 | 12.0351 | 93 | 2022-06-17 15:00 | 4.0959 | 93
2022-06-17 16:00 | 12.0351 | 92 | 2022-06-17 16:00 | 4.0959 | 92
2022-06-17 17:00 | 7.9093 | 91 | 2022-06-17 17:00 | 4.0959 | 91
2022-06-17 18:00 | 0.9533 | 90 | 2022-06-17 18:00 | 0.88365 | 90
2022-06-17 19:00 | 0.92809 | 89 | 2022-06-17 19:00 | 0.85705 | 89
2022-06-17 20:00 | 0.89392 | 86 | 2022-06-17 20:00 | 0.8214 | 86
2022-06-17 21:00 | 0.88213 | 84 | 2022-06-17 21:00 | 0.80921 | 84
2022-06-17 22:00 | 0.88903 | 82 | 2022-06-17 22:00 | 0.81634 | 82
2022-06-17 23:00 | 0.87328 | 80 | 2022-06-17 23:00 | 0.8001 | 80
2022-06-18 | 0.87127 | 80 | 2022-06-18 | 0.79804 | 80
2022-06-18 01:00 | 0.85343 | 78 | 2022-06-18 01:00 | 0.77979 | 78
2022-06-18 02:00 | 0.83254 | 77 | 2022-06-18 02:00 | 0.75859 | 77
2022-06-18 03:00 | 0.83254 | 76 | 2022-06-18 03:00 | 0.75859 | 76
2022-06-18 04:00 | 0.84352 | 74 | 2022-06-18 04:00 | 0.76971 | 74
2022-06-18 05:00 | 0.8385 | 73 | 2022-06-18 05:00 | 0.76462 | 73
2022-06-18 06:00 | 0.82356 | 70 | 2022-06-18 06:00 | 0.74954 | 70
2022-06-18 07:00 | 0.8185 | 69 | 2022-06-18 07:00 | 0.74445 | 69
2022-06-18 08:00 | 0.86337 | 70 | 2022-06-18 08:00 | 0.78994 | 70
2022-06-18 09:00 | 0.8415 | 70 | 2022-06-18 09:00 | 0.76766 | 70
2022-06-18 10:00 | 0.83752 | 70 | 2022-06-18 10:00 | 0.76362 | 70
2022-06-18 11:00 | 0.83352 | 70 | 2022-06-18 11:00 | 0.75959 | 70
2022-06-18 12:00 | 0.85447 | 69 | 2022-06-18 12:00 | 0.78085 | 69
2022-06-18 13:00 | 0.8445 | 71 | 2022-06-18 13:00 | 0.77071 | 71
2022-06-18 14:00 | 0.85447 | 71 | 2022-06-18 14:00 | 0.78085 | 71
2022-06-18 15:00 | 0.85447 | 69 | 2022-06-18 15:00 | 0.78085 | 69
2022-06-18 16:00 | 0.85447 | 70 | 2022-06-18 16:00 | 0.78085 | 70
2022-06-18 17:00 | 0.83051 | 68 | 2022-06-18 17:00 | 0.75654 | 68
2022-06-18 18:00 | 0.8445 | 64 | 2022-06-18 18:00 | 0.77071 | 64
2022-06-18 19:00 | 0.8475 | 63 | 2022-06-18 19:00 | 0.77375 | 63
2022-06-18 20:00 | 0.85245 | 63 | 2022-06-18 20:00 | 0.77879 | 63
2022-06-18 21:00 | 0.85545 | 63 | 2022-06-18 21:00 | 0.78184 | 63
2022-06-18 22:00 | 0.83352 | 62 | 2022-06-18 22:00 | 0.75959 | 62
2022-06-18 23:00 | 0.82855 | 61 | 2022-06-18 23:00 | 0.75456 | 61
2022-06-19 | 0.83156 | 60 | 2022-06-19 | 0.7576 | 60
2022-06-19 01:00 | 0.84352 | 59 | 2022-06-19 01:00 | 0.76971 | 59
2022-06-19 02:00 | 0.87225 | 58 | 2022-06-19 02:00 | 0.79904 | 58
2022-06-19 03:00 | 0.88606 | 59 | 2022-06-19 03:00 | 0.81327 | 59
2022-06-19 04:00 | 0.87722 | 58 | 2022-06-19 04:00 | 0.80416 | 58
2022-06-19 05:00 | 0.88116 | 57 | 2022-06-19 05:00 | 0.80821 | 57
2022-06-19 06:00 | 0.87819 | 55 | 2022-06-19 06:00 | 0.80515 | 55
2022-06-19 07:00 | 0.88213 | 57 | 2022-06-19 07:00 | 0.80921 | 57
2022-06-19 08:00 | 0.88606 | 59 | 2022-06-19 08:00 | 0.81327 | 59
2022-06-19 09:00 | 0.89096 | 62 | 2022-06-19 09:00 | 0.81833 | 62
2022-06-19 10:00 | 0.86337 | 64 | 2022-06-19 10:00 | 0.78994 | 64
2022-06-19 11:00 | 0.85941 | 66 | 2022-06-19 11:00 | 0.78589 | 66
2022-06-19 12:00 | 0.8683 | 68 | 2022-06-19 12:00 | 0.79498 | 68
2022-06-19 13:00 | 0.85343 | 71 | 2022-06-19 13:00 | 0.77979 | 71
2022-06-19 14:00 | 0.83555 | 73 | 2022-06-19 14:00 | 0.76164 | 73
2022-06-19 15:00 | 0.84653 | 74 | 2022-06-19 15:00 | 0.77276 | 74
2022-06-19 16:00 | 0.8624 | 75 | 2022-06-19 16:00 | 0.78894 | 75
2022-06-19 17:00 | 0.86136 | 75 | 2022-06-19 17:00 | 0.78788 | 75
2022-06-19 18:00 | 0.87522 | 74 | 2022-06-19 18:00 | 0.8021 | 74
2022-06-19 19:00 | 0.86532 | 73 | 2022-06-19 19:00 | 0.79193 | 73
2022-06-19 20:00 | 0.86434 | 71 | 2022-06-19 20:00 | 0.79093 | 71
2022-06-19 21:00 | 0.86635 | 69 | 2022-06-19 21:00 | 0.79299 | 69
2022-06-19 22:00 | 0.85148 | 68 | 2022-06-19 22:00 | 0.7778 | 68
2022-06-19 23:00 | 0.85844 | 66 | 2022-06-19 23:00 | 0.78489 | 66
2022-06-20 | 0.86635 | 64 | 2022-06-20 | 0.79299 | 64
2022-06-20 01:00 | 0.87225 | 63 | 2022-06-20 01:00 | 0.79904 | 63
2022-06-20 02:00 | 0.86038 | 62 | 2022-06-20 02:00 | 0.78688 | 62
2022-06-20 03:00 | 0.87619 | 62 | 2022-06-20 03:00 | 0.80309 | 62
2022-06-20 04:00 | 0.8851 | 61 | 2022-06-20 04:00 | 0.81227 | 61
2022-06-20 05:00 | 0.89585 | 59 | 2022-06-20 05:00 | 0.8234 | 59
2022-06-20 06:00 | 0.93102 | 60 | 2022-06-20 06:00 | 0.86013 | 60
2022-06-20 07:00 | 0.88903 | 63 | 2022-06-20 07:00 | 0.81634 | 63
2022-06-20 08:00 | 0.87819 | 66 | 2022-06-20 08:00 | 0.80515 | 66
2022-06-20 09:00 | 0.87819 | 70 | 2022-06-20 09:00 | 0.80515 | 70
2022-06-20 10:00 | 0.86136 | 72 | 2022-06-20 10:00 | 0.78788 | 72
2022-06-20 11:00 | 0.87225 | 73 | 2022-06-20 11:00 | 0.79904 | 73
2022-06-20 12:00 | 0.85148 | 75 | 2022-06-20 12:00 | 0.7778 | 75
2022-06-20 13:00 | 0.83954 | 77 | 2022-06-20 13:00 | 0.76567 | 77
2022-06-20 14:00 | 0.86434 | 79 | 2022-06-20 14:00 | 0.79093 | 79
2022-06-20 15:00 | 0.85447 | 80 | 2022-06-20 15:00 | 0.78085 | 80
2022-06-20 16:00 | 0.86532 | 81 | 2022-06-20 16:00 | 0.79193 | 81
2022-06-20 17:00 | 0.88116 | 81 | 2022-06-20 17:00 | 0.80821 | 81
2022-06-20 18:00 | 0.86532 | 79 | 2022-06-20 18:00 | 0.79193 | 79
2022-06-20 19:00 | 0.87522 | 71 | 2022-06-20 19:00 | 0.8021 | 71
2022-06-20 20:00 | 0.89192 | 69 | 2022-06-20 20:00 | 0.81933 | 69
2022-06-20 21:00 | 0.88013 | 66 | 2022-06-20 21:00 | 0.80715 | 66
2022-06-20 22:00 | 0.88213 | 65 | 2022-06-20 22:00 | 0.80921 | 65
2022-06-20 23:00 | 0.86927 | 65 | 2022-06-20 23:00 | 0.79598 | 65
2022-06-21 | 0.88013 | 64 | 2022-06-21 | 0.80715 | 64
2022-06-21 01:00 | 0.87916 | 65 | 2022-06-21 01:00 | 0.80615 | 65
2022-06-21 02:00 | 0.88213 | 65 | 2022-06-21 02:00 | 0.80921 | 65
2022-06-21 03:00 | 0.88116 | 63 | 2022-06-21 03:00 | 0.80821 | 63
2022-06-21 04:00 | 0.90175 | 63 | 2022-06-21 04:00 | 0.82953 | 63
2022-06-21 05:00 | 1.2345 | 64 | 2022-06-21 05:00 | 1.1932 | 64
2022-06-21 06:00 | 12.0351 | 65 | 2022-06-21 06:00 | 4.0959 | 65
2022-06-21 07:00 | 12.0351 | 67 | 2022-06-21 07:00 | 4.0959 | 67
2022-06-21 08:00 | 12.0351 | 70 | 2022-06-21 08:00 | 4.0959 | 70
2022-06-21 09:00 | 12.0351 | 74 | 2022-06-21 09:00 | 4.0959 | 74
2022-06-21 10:00 | 12.0351 | 76 | 2022-06-21 10:00 | 4.0959 | 76
2022-06-21 11:00 | 12.0351 | 76 | 2022-06-21 11:00 | 4.0959 | 76
2022-06-21 12:00 | 12.0351 | 74 | 2022-06-21 12:00 | 4.0959 | 74
2022-06-21 13:00 | 12.0351 | 77 | 2022-06-21 13:00 | 4.0959 | 77
2022-06-21 14:00 | 12.0351 | 76 | 2022-06-21 14:00 | 4.0959 | 76
2022-06-21 15:00 | 12.0351 | 77 | 2022-06-21 15:00 | 4.0959 | 77
2022-06-21 16:00 | 12.0351 | 75 | 2022-06-21 16:00 | 4.0959 | 75
2022-06-21 17:00 | 0.89784 | 73 | 2022-06-21 17:00 | 0.82546 | 73
2022-06-21 18:00 | 0.86434 | 72 | 2022-06-21 18:00 | 0.79093 | 72
2022-06-21 19:00 | 0.90272 | 71 | 2022-06-21 19:00 | 0.83053 | 71
2022-06-21 20:00 | 0.888 | 69 | 2022-06-21 20:00 | 0.81527 | 69
2022-06-21 21:00 | 0.92223 | 68 | 2022-06-21 21:00 | 0.8509 | 68
2022-06-21 22:00 | 0.92031 | 68 | 2022-06-21 22:00 | 0.8489 | 68
2022-06-21 23:00 | 0.92031 | 67 | 2022-06-21 23:00 | 0.8489 | 67
2022-06-22 | 0.91444 | 67 | 2022-06-22 | 0.84275 | 67
2022-06-22 01:00 | 0.89392 | 67 | 2022-06-22 01:00 | 0.8214 | 67
2022-06-22 02:00 | 0.90272 | 66 | 2022-06-22 02:00 | 0.83053 | 66
2022-06-22 03:00 | 0.8988 | 66 | 2022-06-22 03:00 | 0.82646 | 66
2022-06-22 04:00 | 0.91642 | 67 | 2022-06-22 04:00 | 0.84482 | 67
2022-06-22 05:00 | 0.92809 | 66 | 2022-06-22 05:00 | 0.85705 | 66
2022-06-22 06:00 | 12.0351 | 65 | 2022-06-22 06:00 | 4.0959 | 65
2022-06-22 07:00 | 12.0351 | 65 | 2022-06-22 07:00 | 4.0959 | 65
2022-06-22 08:00 | 12.0351 | 63 | 2022-06-22 08:00 | 4.0959 | 63
2022-06-22 09:00 | 12.0351 | 63 | 2022-06-22 09:00 | 4.0959 | 63
2022-06-22 10:00 | 12.0351 | 64 | 2022-06-22 10:00 | 4.0959 | 64
2022-06-22 11:00 | 12.0351 | 64 | 2022-06-22 11:00 | 4.0959 | 64
2022-06-22 12:00 | 12.0351 | 64 | 2022-06-22 12:00 | 4.0959 | 64
2022-06-22 13:00 | 12.0351 | 64 | 2022-06-22 13:00 | 4.0959 | 64
2022-06-22 14:00 | 12.0351 | 64 | 2022-06-22 14:00 | 4.0959 | 64
2022-06-22 15:00 | 12.0351 | 63 | 2022-06-22 15:00 | 4.0959 | 63
2022-06-22 16:00 | 12.0351 | 64 | 2022-06-22 16:00 | 4.0959 | 64
2022-06-22 17:00 | 4.7762 | 63 | 2022-06-22 17:00 | 2.8629 | 63
2022-06-22 18:00 | 2.898 | 62 | 2022-06-22 18:00 | 2.3838 | 62
2022-06-22 19:00 | 2.904 | 63 | 2022-06-22 19:00 | 2.3852 | 63
2022-06-22 20:00 | 2.898 | 63 | 2022-06-22 20:00 | 2.3838 | 63
2022-06-22 21:00 | 2.9142 | 64 | 2022-06-22 21:00 | 2.3875 | 64
2022-06-22 22:00 | 2.894 | 63 | 2022-06-22 22:00 | 2.3828 | 63
2022-06-22 23:00 | 2.8818 | 64 | 2022-06-22 23:00 | 2.3799 | 64
2022-06-23 | 2.8859 | 63 | 2022-06-23 | 2.3809 | 63
2022-06-23 01:00 | 2.9061 | 61 | 2022-06-23 01:00 | 2.3857 | 61
2022-06-23 02:00 | 2.898 | 61 | 2022-06-23 02:00 | 2.3838 | 61
2022-06-23 03:00 | 2.8707 | 60 | 2022-06-23 03:00 | 2.3772 | 60
2022-06-23 04:00 | 2.8738 | 62 | 2022-06-23 04:00 | 2.3779 | 62
2022-06-23 05:00 | 2.9142 | 62 | 2022-06-23 05:00 | 2.3875 | 62
2022-06-23 06:00 | 12.0351 | 62 | 2022-06-23 06:00 | 4.0959 | 62
2022-06-23 07:00 | 12.0351 | 65 | 2022-06-23 07:00 | 4.0959 | 65
2022-06-23 08:00 | 12.0351 | 67 | 2022-06-23 08:00 | 4.0959 | 67
2022-06-23 09:00 | 12.0351 | 68 | 2022-06-23 09:00 | 4.0959 | 68
2022-06-23 10:00 | 12.0351 | 71 | 2022-06-23 10:00 | 4.0959 | 71
2022-06-23 11:00 | 12.0351 | 72 | 2022-06-23 11:00 | 4.0959 | 72
2022-06-23 12:00 | 12.0351 | 73 | 2022-06-23 12:00 | 4.0959 | 73
2022-06-23 13:00 | 12.0351 | 73 | 2022-06-23 13:00 | 4.0959 | 73
2022-06-23 14:00 | 12.0351 | 73 | 2022-06-23 14:00 | 4.0959 | 73
2022-06-23 15:00 | 12.0351 | 72 | 2022-06-23 15:00 | 4.0959 | 72
2022-06-23 16:00 | 12.0351 | 73 | 2022-06-23 16:00 | 4.0959 | 73
2022-06-23 17:00 | 4.2602 | 72 | 2022-06-23 17:00 | 2.6201 | 72
2022-06-23 18:00 | 0.92809 | 73 | 2022-06-23 18:00 | 0.85705 | 73
2022-06-23 19:00 | 0.9706 | 70 | 2022-06-23 19:00 | 0.90205 | 70
2022-06-23 20:00 | 0.93395 | 68 | 2022-06-23 20:00 | 0.86321 | 68
2022-06-23 21:00 | 0.95621 | 68 | 2022-06-23 21:00 | 0.88674 | 68
2022-06-23 22:00 | 0.9417 | 67 | 2022-06-23 22:00 | 0.87138 | 67
2022-06-23 23:00 | 0.93102 | 67 | 2022-06-23 23:00 | 0.86013 | 67
2022-06-24 | 0.9242 | 65 | 2022-06-24 | 0.85297 | 65
2022-06-24 01:00 | 0.91738 | 64 | 2022-06-24 01:00 | 0.84582 | 64
2022-06-24 02:00 | 0.90765 | 64 | 2022-06-24 02:00 | 0.83567 | 64
2022-06-24 03:00 | 0.90957 | 63 | 2022-06-24 03:00 | 0.83767 | 63
2022-06-24 04:00 | 0.9242 | 62 | 2022-06-24 04:00 | 0.85297 | 62
2022-06-24 05:00 | 0.93681 | 61 | 2022-06-24 05:00 | 0.86623 | 61
2022-06-24 06:00 | 12.0351 | 61 | 2022-06-24 06:00 | 4.0959 | 61
2022-06-24 07:00 | 12.0351 | 65 | 2022-06-24 07:00 | 4.0959 | 65
2022-06-24 08:00 | 12.0351 | 66 | 2022-06-24 08:00 | 4.0959 | 66
2022-06-24 09:00 | 12.0351 | 69 | 2022-06-24 09:00 | 4.0959 | 69
2022-06-24 10:00 | 12.0351 | 71 | 2022-06-24 10:00 | 4.0959 | 71
2022-06-24 11:00 | 12.0351 | 72 | 2022-06-24 11:00 | 4.0959 | 72
2022-06-24 12:00 | 12.0351 | 72 | 2022-06-24 12:00 | 4.0959 | 72
2022-06-24 13:00 | 12.0351 | 74 | 2022-06-24 13:00 | 4.0959 | 74
2022-06-24 14:00 | 12.0351 | 75 | 2022-06-24 14:00 | 4.0959 | 75
2022-06-24 15:00 | 12.0351 | 75 | 2022-06-24 15:00 | 4.0959 | 75
2022-06-24 16:00 | 12.0351 | 74 | 2022-06-24 16:00 | 4.0959 | 74
2022-06-24 17:00 | 5.1911 | 73 | 2022-06-24 17:00 | 3.2744 | 73
2022-06-24 18:00 | 2.0557 | 72 | 2022-06-24 18:00 | 1.9998 | 72
2022-06-24 19:00 | 2.0417 | 70 | 2022-06-24 19:00 | 1.9895 | 70
2022-06-24 20:00 | 2.0212 | 69 | 2022-06-24 20:00 | 1.9742 | 69
2022-06-24 21:00 | 2.0287 | 69 | 2022-06-24 21:00 | 1.9798 | 69
2022-06-24 22:00 | 2.0641 | 69 | 2022-06-24 22:00 | 2.0059 | 69
2022-06-24 23:00 | 2.0306 | 69 | 2022-06-24 23:00 | 1.9812 | 69
2022-06-25 | 2.0055 | 68 | 2022-06-25 | 1.9621 | 68
2022-06-25 01:00 | 1.9656 | 68 | 2022-06-25 01:00 | 1.931 | 68
2022-06-25 02:00 | 1.9924 | 68 | 2022-06-25 02:00 | 1.9521 | 68
2022-06-25 03:00 | 1.9952 | 67 | 2022-06-25 03:00 | 1.9543 | 67
2022-06-25 04:00 | 1.985 | 67 | 2022-06-25 04:00 | 1.9463 | 67
2022-06-25 05:00 | 2.0101 | 67 | 2022-06-25 05:00 | 1.9657 | 67
2022-06-25 06:00 | 2.0055 | 68 | 2022-06-25 06:00 | 1.9621 | 68
2022-06-25 07:00 | 1.998 | 74 | 2022-06-25 07:00 | 1.9564 | 74
2022-06-25 08:00 | 2.0036 | 77 | 2022-06-25 08:00 | 1.9607 | 77
2022-06-25 09:00 | 1.9933 | 81 | 2022-06-25 09:00 | 1.9528 | 81
2022-06-25 10:00 | 2.0073 | 84 | 2022-06-25 10:00 | 1.9636 | 84
2022-06-25 11:00 | 2.0184 | 86 | 2022-06-25 11:00 | 1.972 | 86
2022-06-25 12:00 | 2.0157 | 86 | 2022-06-25 12:00 | 1.97 | 86
2022-06-25 13:00 | 2.024 | 86 | 2022-06-25 13:00 | 1.9763 | 86
2022-06-25 14:00 | 2.0184 | 86 | 2022-06-25 14:00 | 1.972 | 86
2022-06-25 15:00 | 2.0268 | 87 | 2022-06-25 15:00 | 1.9784 | 87
2022-06-25 16:00 | 2.0483 | 84 | 2022-06-25 16:00 | 1.9944 | 84
2022-06-25 17:00 | 2.0287 | 82 | 2022-06-25 17:00 | 1.9798 | 82
2022-06-25 18:00 | 2.024 | 80 | 2022-06-25 18:00 | 1.9763 | 80
2022-06-25 19:00 | 2.0138 | 79 | 2022-06-25 19:00 | 1.9685 | 79
2022-06-25 20:00 | 2.0222 | 77 | 2022-06-25 20:00 | 1.9749 | 77
2022-06-25 21:00 | 2.0427 | 75 | 2022-06-25 21:00 | 1.9902 | 75
2022-06-25 22:00 | 2.0083 | 74 | 2022-06-25 22:00 | 1.9643 | 74
2022-06-25 23:00 | 1.9915 | 72 | 2022-06-25 23:00 | 1.9514 | 72
2022-06-26 | 2.011 | 70 | 2022-06-26 | 1.9664 | 70
2022-06-26 01:00 | 2.0138 | 70 | 2022-06-26 01:00 | 1.9685 | 70
2022-06-26 02:00 | 1.9952 | 69 | 2022-06-26 02:00 | 1.9543 | 69
2022-06-26 03:00 | 1.9915 | 69 | 2022-06-26 03:00 | 1.9514 | 69
2022-06-26 04:00 | 2.0129 | 68 | 2022-06-26 04:00 | 1.9678 | 68
2022-06-26 05:00 | 2.0203 | 68 | 2022-06-26 05:00 | 1.9735 | 68
2022-06-26 06:00 | 1.9961 | 69 | 2022-06-26 06:00 | 1.955 | 69
2022-06-26 07:00 | 2.0361 | 71 | 2022-06-26 07:00 | 1.9853 | 71
2022-06-26 08:00 | 2.0027 | 74 | 2022-06-26 08:00 | 1.96 | 74
2022-06-26 09:00 | 2.0073 | 77 | 2022-06-26 09:00 | 1.9636 | 77
2022-06-26 10:00 | 1.9776 | 79 | 2022-06-26 10:00 | 1.9405 | 79
2022-06-26 11:00 | 2.0101 | 82 | 2022-06-26 11:00 | 1.9657 | 82
2022-06-26 12:00 | 1.9989 | 82 | 2022-06-26 12:00 | 1.9571 | 82
2022-06-26 13:00 | 2.0064 | 82 | 2022-06-26 13:00 | 1.9628 | 82
2022-06-26 14:00 | 2.0064 | 83 | 2022-06-26 14:00 | 1.9628 | 83
2022-06-26 15:00 | 2.0055 | 82 | 2022-06-26 15:00 | 1.9621 | 82
2022-06-26 16:00 | 2.0157 | 80 | 2022-06-26 16:00 | 1.97 | 80
2022-06-26 17:00 | 2.0352 | 80 | 2022-06-26 17:00 | 1.9847 | 80
2022-06-26 18:00 | 2.0278 | 78 | 2022-06-26 18:00 | 1.9791 | 78
2022-06-26 19:00 | 2.0398 | 75 | 2022-06-26 19:00 | 1.9881 | 75
2022-06-26 20:00 | 2.0203 | 74 | 2022-06-26 20:00 | 1.9735 | 74
2022-06-26 21:00 | 2.0259 | 73 | 2022-06-26 21:00 | 1.9777 | 73
2022-06-26 22:00 | 2.011 | 72 | 2022-06-26 22:00 | 1.9664 | 72
2022-06-26 23:00 | 1.9702 | 72 | 2022-06-26 23:00 | 1.9346 | 72
2022-06-27 | 2.0138 | 71 | 2022-06-27 | 1.9685 | 71
2022-06-27 01:00 | 2.0045 | 71 | 2022-06-27 01:00 | 1.9614 | 71
2022-06-27 02:00 | 1.9943 | 70 | 2022-06-27 02:00 | 1.9536 | 70
2022-06-27 03:00 | 1.9961 | 71 | 2022-06-27 03:00 | 1.955 | 71
2022-06-27 04:00 | 1.9906 | 70 | 2022-06-27 04:00 | 1.9507 | 70
2022-06-27 05:00 | 2.0138 | 70 | 2022-06-27 05:00 | 1.9685 | 70
2022-06-27 06:00 | 12.0351 | 70 | 2022-06-27 06:00 | 4.0959 | 70
2022-06-27 07:00 | 12.0351 | 71 | 2022-06-27 07:00 | 4.0959 | 71
2022-06-27 08:00 | 12.0351 | 72 | 2022-06-27 08:00 | 4.0959 | 72
2022-06-27 09:00 | 12.0351 | 73 | 2022-06-27 09:00 | 4.0959 | 73
2022-06-27 10:00 | 12.0351 | 75 | 2022-06-27 10:00 | 4.0959 | 75
2022-06-27 11:00 | 12.0351 | 73 | 2022-06-27 11:00 | 4.0959 | 73
2022-06-27 12:00 | 12.0351 | 71 | 2022-06-27 12:00 | 4.0959 | 71
2022-06-27 13:00 | 12.0351 | 76 | 2022-06-27 13:00 | 4.0959 | 76
2022-06-27 14:00 | 12.0351 | 75 | 2022-06-27 14:00 | 4.0959 | 75
2022-06-27 15:00 | 12.0351 | 75 | 2022-06-27 15:00 | 4.0959 | 75
2022-06-27 16:00 | 12.0351 | 73 | 2022-06-27 16:00 | 4.0959 | 73
2022-06-27 17:00 | 6.4801 | 73 | 2022-06-27 17:00 | 4.0959 | 73
2022-06-27 18:00 | 2.0324 | 72 | 2022-06-27 18:00 | 1.9826 | 72
2022-06-27 19:00 | 2.0613 | 72 | 2022-06-27 19:00 | 2.0039 | 72
2022-06-27 20:00 | 2.0595 | 72 | 2022-06-27 20:00 | 2.0025 | 72
2022-06-27 21:00 | 2.0371 | 73 | 2022-06-27 21:00 | 1.9861 | 73
2022-06-27 22:00 | 2.0408 | 72 | 2022-06-27 22:00 | 1.9888 | 72
2022-06-27 23:00 | 1.9711 | 74 | 2022-06-27 23:00 | 1.9354 | 74
2022-06-28 | 2.0352 | 71 | 2022-06-28 | 1.9847 | 71
2022-06-28 01:00 | 2.0268 | 69 | 2022-06-28 01:00 | 1.9784 | 69
2022-06-28 02:00 | 1.985 | 67 | 2022-06-28 02:00 | 1.9463 | 67
2022-06-28 03:00 | 2.011 | 66 | 2022-06-28 03:00 | 1.9664 | 66
2022-06-28 04:00 | 2.0203 | 66 | 2022-06-28 04:00 | 1.9735 | 66
2022-06-28 05:00 | 3.3306 | 65 | 2022-06-28 05:00 | 2.4605 | 65
2022-06-28 06:00 | 12.0351 | 65 | 2022-06-28 06:00 | 4.0959 | 65
2022-06-28 07:00 | 12.0351 | 66 | 2022-06-28 07:00 | 4.0959 | 66
2022-06-28 08:00 | 12.0351 | 70 | 2022-06-28 08:00 | 4.0959 | 70
2022-06-28 09:00 | 12.0351 | 70 | 2022-06-28 09:00 | 4.0959 | 70
2022-06-28 10:00 | 12.0351 | 73 | 2022-06-28 10:00 | 4.0959 | 73
2022-06-28 11:00 | 12.0351 | 75 | 2022-06-28 11:00 | 4.0959 | 75
2022-06-28 12:00 | 12.0351 | 77 | 2022-06-28 12:00 | 4.0959 | 77
2022-06-28 13:00 | 12.0351 | 76 | 2022-06-28 13:00 | 4.0959 | 76
2022-06-28 14:00 | 12.0351 | 76 | 2022-06-28 14:00 | 4.0959 | 76
2022-06-28 15:00 | 12.0351 | 76 | 2022-06-28 15:00 | 4.0959 | 76
2022-06-28 16:00 | 12.0351 | 77 | 2022-06-28 16:00 | 4.0959 | 77
2022-06-28 17:00 | 6.2393 | 79 | 2022-06-28 17:00 | 4.0959 | 79
2022-06-28 18:00 | 2.0184 | 74 | 2022-06-28 18:00 | 1.972 | 74
2022-06-28 19:00 | 2.0688 | 73 | 2022-06-28 19:00 | 2.0093 | 73
2022-06-28 20:00 | 2.0129 | 70 | 2022-06-28 20:00 | 1.9678 | 70
2022-06-28 21:00 | 2.0259 | 69 | 2022-06-28 21:00 | 1.9777 | 69
2022-06-28 22:00 | 2.0055 | 69 | 2022-06-28 22:00 | 1.9621 | 69
2022-06-28 23:00 | 2.0101 | 68 | 2022-06-28 23:00 | 1.9657 | 68
2022-06-29 | 2.0157 | 67 | 2022-06-29 | 1.97 | 67
2022-06-29 01:00 | 1.9841 | 66 | 2022-06-29 01:00 | 1.9456 | 66
2022-06-29 02:00 | 1.9758 | 65 | 2022-06-29 02:00 | 1.939 | 65
2022-06-29 03:00 | 1.9832 | 65 | 2022-06-29 03:00 | 1.9449 | 65
2022-06-29 04:00 | 1.9887 | 65 | 2022-06-29 04:00 | 1.9492 | 65
2022-06-29 05:00 | 2.0203 | 65 | 2022-06-29 05:00 | 1.9735 | 65
2022-06-29 06:00 | 12.0351 | 64 | 2022-06-29 06:00 | 4.0959 | 64
2022-06-29 07:00 | 12.0351 | 67 | 2022-06-29 07:00 | 4.0959 | 67
2022-06-29 08:00 | 12.0351 | 70 | 2022-06-29 08:00 | 4.0959 | 70
2022-06-29 09:00 | 12.0351 | 72 | 2022-06-29 09:00 | 4.0959 | 72
2022-06-29 10:00 | 12.0351 | 75 | 2022-06-29 10:00 | 4.0959 | 75
2022-06-29 11:00 | 12.0351 | 79 | 2022-06-29 11:00 | 4.0959 | 79
2022-06-29 12:00 | 12.0351 | 80 | 2022-06-29 12:00 | 4.0959 | 80
2022-06-29 13:00 | 12.0351 | 81 | 2022-06-29 13:00 | 4.0959 | 81
2022-06-29 14:00 | 12.0351 | 81 | 2022-06-29 14:00 | 4.0959 | 81
2022-06-29 15:00 | 12.0351 | 81 | 2022-06-29 15:00 | 4.0959 | 81
2022-06-29 16:00 | 12.0351 | 80 | 2022-06-29 16:00 | 4.0959 | 80
2022-06-29 17:00 | 8.9074 | 79 | 2022-06-29 17:00 | 4.0959 | 79
2022-06-29 18:00 | 1.1664 | 75 | 2022-06-29 18:00 | 1.1168 | 75
2022-06-29 19:00 | 1.1886 | 75 | 2022-06-29 19:00 | 1.1416 | 75
2022-06-29 20:00 | 1.1664 | 73 | 2022-06-29 20:00 | 1.1168 | 73
2022-06-29 21:00 | 1.1553 | 71 | 2022-06-29 21:00 | 1.1044 | 71
2022-06-29 22:00 | 1.1322 | 71 | 2022-06-29 22:00 | 1.0785 | 71
2022-06-29 23:00 | 1.1451 | 70 | 2022-06-29 23:00 | 1.093 | 70
2022-06-30 | 1.1387 | 68 | 2022-06-30 | 1.0858 | 68
2022-06-30 01:00 | 1.1312 | 70 | 2022-06-30 01:00 | 1.0774 | 70
2022-06-30 02:00 | 1.1173 | 70 | 2022-06-30 02:00 | 1.062 | 70
2022-06-30 03:00 | 1.1516 | 68 | 2022-06-30 03:00 | 1.1002 | 68
2022-06-30 04:00 | 1.1572 | 70 | 2022-06-30 04:00 | 1.1065 | 70
2022-06-30 05:00 | 1.1738 | 69 | 2022-06-30 05:00 | 1.125 | 69
2022-06-30 06:00 | 12.0351 | 70 | 2022-06-30 06:00 | 4.0959 | 70
2022-06-30 07:00 | 12.0351 | 72 | 2022-06-30 07:00 | 4.0959 | 72
2022-06-30 08:00 | 12.0351 | 75 | 2022-06-30 08:00 | 4.0959 | 75
2022-06-30 09:00 | 12.0351 | 77 | 2022-06-30 09:00 | 4.0959 | 77
2022-06-30 10:00 | 12.0351 | 80 | 2022-06-30 10:00 | 4.0959 | 80
2022-06-30 11:00 | 12.0351 | 82 | 2022-06-30 11:00 | 4.0959 | 82
2022-06-30 12:00 | 12.0351 | 79 | 2022-06-30 12:00 | 4.0959 | 79
2022-06-30 13:00 | 12.0351 | 81 | 2022-06-30 13:00 | 4.0959 | 81
2022-06-30 14:00 | 12.0351 | 82 | 2022-06-30 14:00 | 4.0959 | 82
2022-06-30 15:00 | 12.0351 | 81 | 2022-06-30 15:00 | 4.0959 | 81
2022-06-30 16:00 | 12.0351 | 82 | 2022-06-30 16:00 | 4.0959 | 82
2022-06-30 17:00 | 2.0548 | 80 | 2022-06-30 17:00 | 1.9992 | 80
2022-06-30 18:00 | 2.0464 | 79 | 2022-06-30 18:00 | 1.993 | 79
2022-06-30 19:00 | 2.0567 | 77 | 2022-06-30 19:00 | 2.0005 | 77
2022-06-30 20:00 | 2.0613 | 74 | 2022-06-30 20:00 | 2.0039 | 74
2022-06-30 21:00 | 2.0464 | 73 | 2022-06-30 21:00 | 1.993 | 73
2022-06-30 22:00 | 2.0483 | 73 | 2022-06-30 22:00 | 1.9944 | 73
2022-06-30 23:00 | 2.012 | 72 | 2022-06-30 23:00 | 1.9671 | 72
2022-07-01 | 2.0064 | 70 | 2022-07-01 | 1.9628 | 70
2022-07-01 01:00 | 2.012 | 73 | 2022-07-01 01:00 | 1.9671 | 73
2022-07-01 02:00 | 2.0147 | 73 | 2022-07-01 02:00 | 1.9692 | 73
2022-07-01 03:00 | 2.0138 | 73 | 2022-07-01 03:00 | 1.9685 | 73
2022-07-01 04:00 | 2.0212 | 73 | 2022-07-01 04:00 | 1.9742 | 73
2022-07-01 05:00 | 3.3929 | 71 | 2022-07-01 05:00 | 2.4688 | 71
2022-07-01 06:00 | 12.0351 | 71 | 2022-07-01 06:00 | 4.0959 | 71
2022-07-01 07:00 | 12.0351 | 73 | 2022-07-01 07:00 | 4.0959 | 73
2022-07-01 08:00 | 12.0351 | 74 | 2022-07-01 08:00 | 4.0959 | 74
2022-07-01 09:00 | 12.0351 | 77 | 2022-07-01 09:00 | 4.0959 | 77
2022-07-01 10:00 | 12.0351 | 78 | 2022-07-01 10:00 | 4.0959 | 78
2022-07-01 11:00 | 12.0351 | 80 | 2022-07-01 11:00 | 4.0959 | 80
2022-07-01 12:00 | 12.0351 | 81 | 2022-07-01 12:00 | 4.0959 | 81
2022-07-01 13:00 | 12.0351 | 83 | 2022-07-01 13:00 | 4.0959 | 83
2022-07-01 14:00 | 12.0351 | 84 | 2022-07-01 14:00 | 4.0959 | 84
2022-07-01 15:00 | 12.0351 | 84 | 2022-07-01 15:00 | 4.0959 | 84
2022-07-01 16:00 | 12.0351 | 83 | 2022-07-01 16:00 | 4.0959 | 83
2022-07-01 17:00 | 5.4092 | 81 | 2022-07-01 17:00 | 3.6319 | 81
2022-07-01 18:00 | 2.0576 | 79 | 2022-07-01 18:00 | 2.0012 | 79
2022-07-01 19:00 | 2.0427 | 79 | 2022-07-01 19:00 | 1.9902 | 79
2022-07-01 20:00 | 2.0203 | 77 | 2022-07-01 20:00 | 1.9735 | 77
2022-07-01 21:00 | 2.0361 | 76 | 2022-07-01 21:00 | 1.9853 | 76
2022-07-01 22:00 | 2.0259 | 75 | 2022-07-01 22:00 | 1.9777 | 75
2022-07-01 23:00 | 2.0064 | 75 | 2022-07-01 23:00 | 1.9628 | 75
2022-07-02 | 2.0092 | 77 | 2022-07-02 | 1.965 | 77
2022-07-02 01:00 | 2.0045 | 74 | 2022-07-02 01:00 | 1.9614 | 74
2022-07-02 02:00 | 1.9971 | 73 | 2022-07-02 02:00 | 1.9557 | 73
2022-07-02 03:00 | 1.9804 | 73 | 2022-07-02 03:00 | 1.9427 | 73
2022-07-02 04:00 | 2.0212 | 74 | 2022-07-02 04:00 | 1.9742 | 74
2022-07-02 05:00 | 2.0147 | 73 | 2022-07-02 05:00 | 1.9692 | 73
2022-07-02 06:00 | 1.9915 | 74 | 2022-07-02 06:00 | 1.9514 | 74
2022-07-02 07:00 | 1.985 | 76 | 2022-07-02 07:00 | 1.9463 | 76
2022-07-02 08:00 | 2.0259 | 76 | 2022-07-02 08:00 | 1.9777 | 76
2022-07-02 09:00 | 2.0389 | 79 | 2022-07-02 09:00 | 1.9874 | 79
2022-07-02 10:00 | 2.0389 | 79 | 2022-07-02 10:00 | 1.9874 | 79
2022-07-02 11:00 | 2.0222 | 83 | 2022-07-02 11:00 | 1.9749 | 83
2022-07-02 12:00 | 2.0175 | 84 | 2022-07-02 12:00 | 1.9714 | 84
2022-07-02 13:00 | 2.0343 | 82 | 2022-07-02 13:00 | 1.984 | 82
2022-07-02 14:00 | 2.0352 | 85 | 2022-07-02 14:00 | 1.9847 | 85
2022-07-02 15:00 | 2.0147 | 84 | 2022-07-02 15:00 | 1.9692 | 84
2022-07-02 16:00 | 2.0073 | 83 | 2022-07-02 16:00 | 1.9636 | 83
2022-07-02 17:00 | 1.9952 | 83 | 2022-07-02 17:00 | 1.9543 | 83
2022-07-02 18:00 | 2.0092 | 81 | 2022-07-02 18:00 | 1.965 | 81
2022-07-02 19:00 | 2.0361 | 79 | 2022-07-02 19:00 | 1.9853 | 79
2022-07-02 20:00 | 2.0464 | 79 | 2022-07-02 20:00 | 1.993 | 79
2022-07-02 21:00 | 2.0278 | 78 | 2022-07-02 21:00 | 1.9791 | 78
2022-07-02 22:00 | 2.0147 | 73 | 2022-07-02 22:00 | 1.9692 | 73
2022-07-02 23:00 | 1.9961 | 75 | 2022-07-02 23:00 | 1.955 | 75
2022-07-03 | 1.9693 | 77 | 2022-07-03 | 1.9339 | 77
2022-07-03 01:00 | 1.9674 | 79 | 2022-07-03 01:00 | 1.9324 | 79
2022-07-03 02:00 | 1.9776 | 79 | 2022-07-03 02:00 | 1.9405 | 79
2022-07-03 03:00 | 1.9841 | 79 | 2022-07-03 03:00 | 1.9456 | 79
2022-07-03 04:00 | 1.9785 | 78 | 2022-07-03 04:00 | 1.9412 | 78
2022-07-03 05:00 | 1.9767 | 77 | 2022-07-03 05:00 | 1.9398 | 77
2022-07-03 06:00 | 1.9646 | 76 | 2022-07-03 06:00 | 1.9302 | 76
2022-07-03 07:00 | 1.9943 | 76 | 2022-07-03 07:00 | 1.9536 | 76
2022-07-03 08:00 | 1.9813 | 77 | 2022-07-03 08:00 | 1.9434 | 77
2022-07-03 09:00 | 1.9887 | 77 | 2022-07-03 09:00 | 1.9492 | 77
2022-07-03 10:00 | 1.9702 | 78 | 2022-07-03 10:00 | 1.9346 | 78
2022-07-03 11:00 | 1.9813 | 79 | 2022-07-03 11:00 | 1.9434 | 79
2022-07-03 12:00 | 1.9961 | 83 | 2022-07-03 12:00 | 1.955 | 83
2022-07-03 13:00 | 1.9971 | 86 | 2022-07-03 13:00 | 1.9557 | 86
2022-07-03 14:00 | 1.9748 | 86 | 2022-07-03 14:00 | 1.9383 | 86
2022-07-03 15:00 | 1.9693 | 84 | 2022-07-03 15:00 | 1.9339 | 84
2022-07-03 16:00 | 1.9915 | 82 | 2022-07-03 16:00 | 1.9514 | 82
2022-07-03 17:00 | 1.9952 | 82 | 2022-07-03 17:00 | 1.9543 | 82
2022-07-03 18:00 | 1.9924 | 80 | 2022-07-03 18:00 | 1.9521 | 80
2022-07-03 19:00 | 2.0092 | 79 | 2022-07-03 19:00 | 1.965 | 79
2022-07-03 20:00 | 1.9859 | 75 | 2022-07-03 20:00 | 1.947 | 75
2022-07-03 21:00 | 2.0017 | 72 | 2022-07-03 21:00 | 1.9593 | 72
2022-07-03 22:00 | 1.9804 | 71 | 2022-07-03 22:00 | 1.9427 | 71
2022-07-03 23:00 | 1.9795 | 77 | 2022-07-03 23:00 | 1.942 | 77
2022-07-04 | 1.985 | 76 | 2022-07-04 | 1.9463 | 76
2022-07-04 01:00 | 1.9795 | 74 | 2022-07-04 01:00 | 1.942 | 74
2022-07-04 02:00 | 1.9609 | 71 | 2022-07-04 02:00 | 1.9272 | 71
2022-07-04 03:00 | 1.9841 | 70 | 2022-07-04 03:00 | 1.9456 | 70
2022-07-04 04:00 | 1.9943 | 68 | 2022-07-04 04:00 | 1.9536 | 68
2022-07-04 05:00 | 1.9878 | 66 | 2022-07-04 05:00 | 1.9485 | 66
2022-07-04 06:00 | 1.998 | 66 | 2022-07-04 06:00 | 1.9564 | 66
2022-07-04 07:00 | 2.0194 | 70 | 2022-07-04 07:00 | 1.9728 | 70
2022-07-04 08:00 | 1.9971 | 73 | 2022-07-04 08:00 | 1.9557 | 73
2022-07-04 09:00 | 2.0101 | 77 | 2022-07-04 09:00 | 1.9657 | 77
2022-07-04 10:00 | 1.9999 | 79 | 2022-07-04 10:00 | 1.9578 | 79
2022-07-04 11:00 | 2.0073 | 82 | 2022-07-04 11:00 | 1.9636 | 82
2022-07-04 12:00 | 2.0027 | 84 | 2022-07-04 12:00 | 1.96 | 84
2022-07-04 13:00 | 2.0101 | 82 | 2022-07-04 13:00 | 1.9657 | 82
2022-07-04 14:00 | 2.0027 | 83 | 2022-07-04 14:00 | 1.96 | 83
2022-07-04 15:00 | 1.998 | 81 | 2022-07-04 15:00 | 1.9564 | 81
2022-07-04 16:00 | 2.0147 | 81 | 2022-07-04 16:00 | 1.9692 | 81
2022-07-04 17:00 | 2.012 | 79 | 2022-07-04 17:00 | 1.9671 | 79
2022-07-04 18:00 | 2.0036 | 78 | 2022-07-04 18:00 | 1.9607 | 78
2022-07-04 19:00 | 2.0157 | 76 | 2022-07-04 19:00 | 1.97 | 76
2022-07-04 20:00 | 2.0036 | 75 | 2022-07-04 20:00 | 1.9607 | 75
2022-07-04 21:00 | 2.0027 | 73 | 2022-07-04 21:00 | 1.96 | 73
2022-07-04 22:00 | 1.9887 | 74 | 2022-07-04 22:00 | 1.9492 | 74
2022-07-04 23:00 | 2.024 | 72 | 2022-07-04 23:00 | 1.9763 | 72
2022-07-05 | 2.0315 | 72 | 2022-07-05 | 1.9819 | 72
2022-07-05 01:00 | 2.0212 | 71 | 2022-07-05 01:00 | 1.9742 | 71
2022-07-05 02:00 | 1.998 | 71 | 2022-07-05 02:00 | 1.9564 | 71
2022-07-05 03:00 | 1.9869 | 69 | 2022-07-05 03:00 | 1.9478 | 69
2022-07-05 04:00 | 1.9933 | 69 | 2022-07-05 04:00 | 1.9528 | 69
2022-07-05 05:00 | 2.0249 | 69 | 2022-07-05 05:00 | 1.977 | 69
2022-07-05 06:00 | 12.0351 | 70 | 2022-07-05 06:00 | 4.0959 | 70
2022-07-05 07:00 | 12.0351 | 72 | 2022-07-05 07:00 | 4.0959 | 72
2022-07-05 08:00 | 12.0351 | 73 | 2022-07-05 08:00 | 4.0959 | 73
2022-07-05 09:00 | 12.0351 | 76 | 2022-07-05 09:00 | 4.0959 | 76
2022-07-05 10:00 | 12.0351 | 77 | 2022-07-05 10:00 | 4.0959 | 77
2022-07-05 11:00 | 12.0351 | 81 | 2022-07-05 11:00 | 4.0959 | 81
2022-07-05 12:00 | 12.0351 | 82 | 2022-07-05 12:00 | 4.0959 | 82
2022-07-05 13:00 | 12.0351 | 81 | 2022-07-05 13:00 | 4.0959 | 81
2022-07-05 14:00 | 12.0351 | 81 | 2022-07-05 14:00 | 4.0959 | 81
2022-07-05 15:00 | 12.0351 | 77 | 2022-07-05 15:00 | 4.0959 | 77
2022-07-05 16:00 | 12.0351 | 76 | 2022-07-05 16:00 | 4.0959 | 76
2022-07-05 17:00 | 12.0351 | 75 | 2022-07-05 17:00 | 4.0959 | 75
2022-07-05 18:00 | 7.5048 | 75 | 2022-07-05 18:00 | 4.0959 | 75
2022-07-05 19:00 | 2.0595 | 74 | 2022-07-05 19:00 | 2.0025 | 74
2022-07-05 20:00 | 2.038 | 73 | 2022-07-05 20:00 | 1.9868 | 73
2022-07-05 21:00 | 2.0231 | 71 | 2022-07-05 21:00 | 1.9756 | 71
2022-07-05 22:00 | 2.024 | 72 | 2022-07-05 22:00 | 1.9763 | 72
2022-07-05 23:00 | 2.0008 | 71 | 2022-07-05 23:00 | 1.9586 | 71
2022-07-06 | 1.9896 | 72 | 2022-07-06 | 1.9499 | 72
2022-07-06 01:00 | 2.0092 | 72 | 2022-07-06 01:00 | 1.965 | 72
2022-07-06 02:00 | 2.0138 | 72 | 2022-07-06 02:00 | 1.9685 | 72
2022-07-06 03:00 | 2.0203 | 72 | 2022-07-06 03:00 | 1.9735 | 72
2022-07-06 04:00 | 2.0017 | 71 | 2022-07-06 04:00 | 1.9593 | 71
2022-07-06 05:00 | 2.0175 | 72 | 2022-07-06 05:00 | 1.9714 | 72
2022-07-06 06:00 | 12.0351 | 73 | 2022-07-06 06:00 | 4.0959 | 73
2022-07-06 07:00 | 12.0351 | 76 | 2022-07-06 07:00 | 4.0959 | 76
2022-07-06 08:00 | 12.0351 | 79 | 2022-07-06 08:00 | 4.0959 | 79
2022-07-06 09:00 | 12.0351 | 83 | 2022-07-06 09:00 | 4.0959 | 83
2022-07-06 10:00 | 12.0351 | 87 | 2022-07-06 10:00 | 4.0959 | 87
2022-07-06 11:00 | 12.0351 | 86 | 2022-07-06 11:00 | 4.0959 | 86
2022-07-06 12:00 | 12.0351 | 86 | 2022-07-06 12:00 | 4.0959 | 86
2022-07-06 13:00 | 12.0351 | 86 | 2022-07-06 13:00 | 4.0959 | 86
2022-07-06 14:00 | 12.0351 | 86 | 2022-07-06 14:00 | 4.0959 | 86
2022-07-06 15:00 | 12.0351 | 86 | 2022-07-06 15:00 | 4.0959 | 86
2022-07-06 16:00 | 12.0351 | 87 | 2022-07-06 16:00 | 4.0959 | 87
2022-07-06 17:00 | 9.4978 | 87 | 2022-07-06 17:00 | 4.0959 | 87
2022-07-06 18:00 | 1.6341 | 87 | 2022-07-06 18:00 | 1.6286 | 87
2022-07-06 19:00 | 1.6875 | 84 | 2022-07-06 19:00 | 1.6821 | 84
2022-07-06 20:00 | 1.6413 | 83 | 2022-07-06 20:00 | 1.6359 | 83
2022-07-06 21:00 | 1.6639 | 81 | 2022-07-06 21:00 | 1.6587 | 81
2022-07-06 22:00 | 1.6277 | 79 | 2022-07-06 22:00 | 1.6222 | 79
2022-07-06 23:00 | 1.6169 | 79 | 2022-07-06 23:00 | 1.6111 | 79
2022-07-07 | 1.635 | 78 | 2022-07-07 | 1.6295 | 78
2022-07-07 01:00 | 1.6413 | 77 | 2022-07-07 01:00 | 1.6359 | 77
2022-07-07 02:00 | 1.6331 | 76 | 2022-07-07 02:00 | 1.6276 | 76
2022-07-07 03:00 | 1.6277 | 75 | 2022-07-07 03:00 | 1.6222 | 75
2022-07-07 04:00 | 1.6286 | 73 | 2022-07-07 04:00 | 1.6231 | 73
2022-07-07 05:00 | 2.8073 | 73 | 2022-07-07 05:00 | 2.3607 | 73
2022-07-07 06:00 | 12.0351 | 73 | 2022-07-07 06:00 | 4.0959 | 73
2022-07-07 07:00 | 12.0351 | 74 | 2022-07-07 07:00 | 4.0959 | 74
2022-07-07 08:00 | 12.0351 | 74 | 2022-07-07 08:00 | 4.0959 | 74
2022-07-07 09:00 | 12.0351 | 76 | 2022-07-07 09:00 | 4.0959 | 76
2022-07-07 10:00 | 12.0351 | 77 | 2022-07-07 10:00 | 4.0959 | 77
2022-07-07 11:00 | 12.0351 | 78 | 2022-07-07 11:00 | 4.0959 | 78
2022-07-07 12:00 | 12.0351 | 79 | 2022-07-07 12:00 | 4.0959 | 79
2022-07-07 13:00 | 12.0351 | 81 | 2022-07-07 13:00 | 4.0959 | 81
2022-07-07 14:00 | 12.0351 | 81 | 2022-07-07 14:00 | 4.0959 | 81
2022-07-07 15:00 | 12.0351 | 79 | 2022-07-07 15:00 | 4.0959 | 79
2022-07-07 16:00 | 12.0351 | 80 | 2022-07-07 16:00 | 4.0959 | 80
2022-07-07 17:00 | 8.8652 | 78 | 2022-07-07 17:00 | 4.0959 | 78
2022-07-07 18:00 | 1.96 | 78 | 2022-07-07 18:00 | 1.9265 | 78
2022-07-07 19:00 | 2.0092 | 74 | 2022-07-07 19:00 | 1.965 | 74
2022-07-07 20:00 | 2.0045 | 73 | 2022-07-07 20:00 | 1.9614 | 73
2022-07-07 21:00 | 1.998 | 71 | 2022-07-07 21:00 | 1.9564 | 71
2022-07-07 22:00 | 2.0036 | 70 | 2022-07-07 22:00 | 1.9607 | 70
2022-07-07 23:00 | 1.998 | 70 | 2022-07-07 23:00 | 1.9564 | 70
2022-07-08 | 1.9999 | 69 | 2022-07-08 | 1.9578 | 69
2022-07-08 01:00 | 1.9915 | 69 | 2022-07-08 01:00 | 1.9514 | 69
2022-07-08 02:00 | 2.0064 | 68 | 2022-07-08 02:00 | 1.9628 | 68
2022-07-08 03:00 | 2.0203 | 67 | 2022-07-08 03:00 | 1.9735 | 67
2022-07-08 04:00 | 2.0278 | 67 | 2022-07-08 04:00 | 1.9791 | 67
2022-07-08 05:00 | 2.0222 | 66 | 2022-07-08 05:00 | 1.9749 | 66
2022-07-08 06:00 | 12.0351 | 67 | 2022-07-08 06:00 | 4.0959 | 67
2022-07-08 07:00 | 12.0351 | 70 | 2022-07-08 07:00 | 4.0959 | 70
2022-07-08 08:00 | 12.0351 | 71 | 2022-07-08 08:00 | 4.0959 | 71
2022-07-08 09:00 | 12.0351 | 74 | 2022-07-08 09:00 | 4.0959 | 74
2022-07-08 10:00 | 12.0351 | 74 | 2022-07-08 10:00 | 4.0959 | 74
2022-07-08 11:00 | 12.0351 | 77 | 2022-07-08 11:00 | 4.0959 | 77
2022-07-08 12:00 | 12.0351 | 77 | 2022-07-08 12:00 | 4.0959 | 77
2022-07-08 13:00 | 12.0351 | 78 | 2022-07-08 13:00 | 4.0959 | 78
2022-07-08 14:00 | 12.0351 | 80 | 2022-07-08 14:00 | 4.0959 | 80
2022-07-08 15:00 | 12.0351 | 79 | 2022-07-08 15:00 | 4.0959 | 79
2022-07-08 16:00 | 12.0351 | 77 | 2022-07-08 16:00 | 4.0959 | 77
2022-07-08 17:00 | 7.2317 | 75 | 2022-07-08 17:00 | 4.0959 | 75
2022-07-08 18:00 | 2.0492 | 73 | 2022-07-08 18:00 | 1.995 | 73
2022-07-08 19:00 | 2.024 | 72 | 2022-07-08 19:00 | 1.9763 | 72
2022-07-08 20:00 | 1.9656 | 70 | 2022-07-08 20:00 | 1.931 | 70
2022-07-08 21:00 | 1.9971 | 71 | 2022-07-08 21:00 | 1.9557 | 71
2022-07-08 22:00 | 1.9971 | 72 | 2022-07-08 22:00 | 1.9557 | 72
2022-07-08 23:00 | 2.0036 | 73 | 2022-07-08 23:00 | 1.9607 | 73
2022-07-09 | 1.9952 | 72 | 2022-07-09 | 1.9543 | 72
2022-07-09 01:00 | 1.9933 | 72 | 2022-07-09 01:00 | 1.9528 | 72
2022-07-09 02:00 | 2.0027 | 73 | 2022-07-09 02:00 | 1.96 | 73
2022-07-09 03:00 | 1.9739 | 73 | 2022-07-09 03:00 | 1.9376 | 73
2022-07-09 04:00 | 1.9887 | 73 | 2022-07-09 04:00 | 1.9492 | 73
2022-07-09 05:00 | 1.9841 | 72 | 2022-07-09 05:00 | 1.9456 | 72
2022-07-09 06:00 | 1.9878 | 72 | 2022-07-09 06:00 | 1.9485 | 72
2022-07-09 07:00 | 1.9915 | 72 | 2022-07-09 07:00 | 1.9514 | 72
2022-07-09 08:00 | 2.0101 | 74 | 2022-07-09 08:00 | 1.9657 | 74
2022-07-09 09:00 | 1.9869 | 78 | 2022-07-09 09:00 | 1.9478 | 78
2022-07-09 10:00 | 1.9915 | 80 | 2022-07-09 10:00 | 1.9514 | 80
2022-07-09 11:00 | 2.0027 | 82 | 2022-07-09 11:00 | 1.96 | 82
2022-07-09 12:00 | 1.998 | 84 | 2022-07-09 12:00 | 1.9564 | 84
2022-07-09 13:00 | 2.0092 | 84 | 2022-07-09 13:00 | 1.965 | 84
2022-07-09 14:00 | 2.0017 | 85 | 2022-07-09 14:00 | 1.9593 | 85
2022-07-09 15:00 | 2.0083 | 82 | 2022-07-09 15:00 | 1.9643 | 82
2022-07-09 16:00 | 1.9961 | 81 | 2022-07-09 16:00 | 1.955 | 81
2022-07-09 17:00 | 1.9952 | 80 | 2022-07-09 17:00 | 1.9543 | 80
2022-07-09 18:00 | 1.9591 | 79 | 2022-07-09 18:00 | 1.9258 | 79
2022-07-09 19:00 | 1.9434 | 77 | 2022-07-09 19:00 | 1.9131 | 77
2022-07-09 20:00 | 1.9471 | 74 | 2022-07-09 20:00 | 1.9161 | 74
2022-07-09 21:00 | 1.9259 | 72 | 2022-07-09 21:00 | 1.8987 | 72
2022-07-09 22:00 | 1.9415 | 71 | 2022-07-09 22:00 | 1.9116 | 71
2022-07-09 23:00 | 1.9535 | 71 | 2022-07-09 23:00 | 1.9213 | 71
2022-07-10 | 1.9388 | 70 | 2022-07-10 | 1.9093 | 70
2022-07-10 01:00 | 1.9452 | 70 | 2022-07-10 01:00 | 1.9146 | 70
2022-07-10 02:00 | 1.9609 | 68 | 2022-07-10 02:00 | 1.9272 | 68
2022-07-10 03:00 | 1.9822 | 66 | 2022-07-10 03:00 | 1.9441 | 66
2022-07-10 04:00 | 1.9933 | 66 | 2022-07-10 04:00 | 1.9528 | 66
2022-07-10 05:00 | 1.985 | 66 | 2022-07-10 05:00 | 1.9463 | 66
2022-07-10 06:00 | 1.9915 | 67 | 2022-07-10 06:00 | 1.9514 | 67
2022-07-10 07:00 | 1.9896 | 68 | 2022-07-10 07:00 | 1.9499 | 68
2022-07-10 08:00 | 1.9684 | 70 | 2022-07-10 08:00 | 1.9332 | 70
2022-07-10 09:00 | 1.9989 | 73 | 2022-07-10 09:00 | 1.9571 | 73
2022-07-10 10:00 | 1.9711 | 76 | 2022-07-10 10:00 | 1.9354 | 76
2022-07-10 11:00 | 1.9832 | 78 | 2022-07-10 11:00 | 1.9449 | 78
2022-07-10 12:00 | 2.0092 | 81 | 2022-07-10 12:00 | 1.965 | 81
2022-07-10 13:00 | 2.012 | 79 | 2022-07-10 13:00 | 1.9671 | 79
2022-07-10 14:00 | 1.9887 | 79 | 2022-07-10 14:00 | 1.9492 | 79
2022-07-10 15:00 | 1.9859 | 79 | 2022-07-10 15:00 | 1.947 | 79
2022-07-10 16:00 | 2.0036 | 79 | 2022-07-10 16:00 | 1.9607 | 79
2022-07-10 17:00 | 1.9999 | 78 | 2022-07-10 17:00 | 1.9578 | 78
2022-07-10 18:00 | 1.9943 | 77 | 2022-07-10 18:00 | 1.9536 | 77
2022-07-10 19:00 | 1.9674 | 75 | 2022-07-10 19:00 | 1.9324 | 75
2022-07-10 20:00 | 1.9869 | 73 | 2022-07-10 20:00 | 1.9478 | 73
2022-07-10 21:00 | 1.9952 | 71 | 2022-07-10 21:00 | 1.9543 | 71
2022-07-10 22:00 | 1.9832 | 70 | 2022-07-10 22:00 | 1.9449 | 70
2022-07-10 23:00 | 1.9804 | 69 | 2022-07-10 23:00 | 1.9427 | 69
2022-07-11 | 1.9933 | 68 | 2022-07-11 | 1.9528 | 68
2022-07-11 01:00 | 1.9804 | 68 | 2022-07-11 01:00 | 1.9427 | 68
2022-07-11 02:00 | 1.9906 | 67 | 2022-07-11 02:00 | 1.9507 | 67
2022-07-11 03:00 | 2.0175 | 67 | 2022-07-11 03:00 | 1.9714 | 67
2022-07-11 04:00 | 1.9869 | 66 | 2022-07-11 04:00 | 1.9478 | 66
2022-07-11 05:00 | 5.7635 | 66 | 2022-07-11 05:00 | 4.0959 | 66
2022-07-11 06:00 | 12.0351 | 65 | 2022-07-11 06:00 | 4.0959 | 65
2022-07-11 07:00 | 12.0351 | 69 | 2022-07-11 07:00 | 4.0959 | 69
2022-07-11 08:00 | 12.0351 | 72 | 2022-07-11 08:00 | 4.0959 | 72
2022-07-11 09:00 | 12.0351 | 75 | 2022-07-11 09:00 | 4.0959 | 75
2022-07-11 10:00 | 12.0351 | 77 | 2022-07-11 10:00 | 4.0959 | 77
2022-07-11 11:00 | 12.0351 | 79 | 2022-07-11 11:00 | 4.0959 | 79
2022-07-11 12:00 | 12.0351 | 79 | 2022-07-11 12:00 | 4.0959 | 79
2022-07-11 13:00 | 12.0351 | 80 | 2022-07-11 13:00 | 4.0959 | 80
2022-07-11 14:00 | 12.0351 | 80 | 2022-07-11 14:00 | 4.0959 | 80
2022-07-11 15:00 | 12.0351 | 81 | 2022-07-11 15:00 | 4.0959 | 81
2022-07-11 16:00 | 12.0351 | 80 | 2022-07-11 16:00 | 4.0959 | 80
2022-07-11 17:00 | 12.0351 | 78 | 2022-07-11 17:00 | 4.0959 | 78
2022-07-11 18:00 | 6.731 | 76 | 2022-07-11 18:00 | 4.0959 | 76
2022-07-11 19:00 | 4.8691 | 75 | 2022-07-11 19:00 | 2.9328 | 75
2022-07-11 20:00 | 4.7948 | 73 | 2022-07-11 20:00 | 2.8761 | 73
2022-07-11 21:00 | 4.7446 | 72 | 2022-07-11 21:00 | 2.8414 | 72
2022-07-11 22:00 | 4.7475 | 72 | 2022-07-11 22:00 | 2.8434 | 72
2022-07-11 23:00 | 4.7159 | 72 | 2022-07-11 23:00 | 2.8229 | 72
2022-07-12 | 4.7396 | 71 | 2022-07-12 | 2.8382 | 71
2022-07-12 01:00 | 4.8164 | 70 | 2022-07-12 01:00 | 2.8918 | 70
2022-07-12 02:00 | 4.7948 | 69 | 2022-07-12 02:00 | 2.8761 | 69
2022-07-12 03:00 | 4.8154 | 69 | 2022-07-12 03:00 | 2.8911 | 69
2022-07-12 04:00 | 4.8232 | 69 | 2022-07-12 04:00 | 2.897 | 69
2022-07-12 05:00 | 4.8125 | 69 | 2022-07-12 05:00 | 2.8889 | 69
2022-07-12 06:00 | 12.0351 | 70 | 2022-07-12 06:00 | 4.0959 | 70
2022-07-12 07:00 | 12.0351 | 71 | 2022-07-12 07:00 | 4.0959 | 71
2022-07-12 08:00 | 12.0351 | 73 | 2022-07-12 08:00 | 4.0959 | 73
2022-07-12 09:00 | 12.0351 | 75 | 2022-07-12 09:00 | 4.0959 | 75
2022-07-12 10:00 | 12.0351 | 77 | 2022-07-12 10:00 | 4.0959 | 77
2022-07-12 11:00 | 12.0351 | 80 | 2022-07-12 11:00 | 4.0959 | 80
2022-07-12 12:00 | 12.0351 | 82 | 2022-07-12 12:00 | 4.0959 | 82
2022-07-12 13:00 | 12.0351 | 82 | 2022-07-12 13:00 | 4.0959 | 82
2022-07-12 14:00 | 12.0351 | 83 | 2022-07-12 14:00 | 4.0959 | 83
2022-07-12 15:00 | 12.0351 | 82 | 2022-07-12 15:00 | 4.0959 | 82
2022-07-12 16:00 | 12.0351 | 82 | 2022-07-12 16:00 | 4.0959 | 82
2022-07-12 17:00 | 12.0351 | 81 | 2022-07-12 17:00 | 4.0959 | 81
2022-07-12 18:00 | 3.5499 | 79 | 2022-07-12 18:00 | 2.4888 | 79
2022-07-12 19:00 | 2.1016 | 77 | 2022-07-12 19:00 | 2.0326 | 77
2022-07-12 20:00 | 2.0885 | 77 | 2022-07-12 20:00 | 2.0233 | 77
2022-07-12 21:00 | 2.1204 | 79 | 2022-07-12 21:00 | 2.0455 | 79
2022-07-12 22:00 | 2.1109 | 78 | 2022-07-12 22:00 | 2.039 | 78
2022-07-12 23:00 | 2.0988 | 81 | 2022-07-12 23:00 | 2.0306 | 81
2022-07-13 | 2.0988 | 79 | 2022-07-13 | 2.0306 | 79
2022-07-13 01:00 | 2.0988 | 78 | 2022-07-13 01:00 | 2.0306 | 78
2022-07-13 02:00 | 2.0885 | 76 | 2022-07-13 02:00 | 2.0233 | 76
2022-07-13 03:00 | 2.0847 | 76 | 2022-07-13 03:00 | 2.0207 | 76
2022-07-13 04:00 | 2.1016 | 78 | 2022-07-13 04:00 | 2.0326 | 78
2022-07-13 05:00 | 4.7278 | 76 | 2022-07-13 05:00 | 2.8305 | 76
2022-07-13 06:00 | 12.0351 | 75 | 2022-07-13 06:00 | 4.0959 | 75
2022-07-13 07:00 | 12.0351 | 78 | 2022-07-13 07:00 | 4.0959 | 78
2022-07-13 08:00 | 12.0351 | 80 | 2022-07-13 08:00 | 4.0959 | 80
2022-07-13 09:00 | 12.0351 | 82 | 2022-07-13 09:00 | 4.0959 | 82
2022-07-13 10:00 | 12.0351 | 86 | 2022-07-13 10:00 | 4.0959 | 86
2022-07-13 11:00 | 12.0351 | 85 | 2022-07-13 11:00 | 4.0959 | 85
2022-07-13 12:00 | 12.0351 | 88 | 2022-07-13 12:00 | 4.0959 | 88
2022-07-13 13:00 | 12.0351 | 88 | 2022-07-13 13:00 | 4.0959 | 88
2022-07-13 14:00 | 12.0351 | 89 | 2022-07-13 14:00 | 4.0959 | 89
2022-07-13 15:00 | 12.0351 | 91 | 2022-07-13 15:00 | 4.0959 | 91
2022-07-13 16:00 | 12.0351 | 88 | 2022-07-13 16:00 | 4.0959 | 88
2022-07-13 17:00 | 12.0351 | 84 | 2022-07-13 17:00 | 4.0959 | 84
2022-07-13 18:00 | 7.1532 | 84 | 2022-07-13 18:00 | 4.0959 | 84
2022-07-13 19:00 | 7.1915 | 80 | 2022-07-13 19:00 | 4.0959 | 80
2022-07-13 20:00 | 7.1777 | 77 | 2022-07-13 20:00 | 4.0959 | 77
2022-07-13 21:00 | 7.1545 | 76 | 2022-07-13 21:00 | 4.0959 | 76
2022-07-13 22:00 | 7.1603 | 75 | 2022-07-13 22:00 | 4.0959 | 75
2022-07-13 23:00 | 7.1595 | 75 | 2022-07-13 23:00 | 4.0959 | 75
2022-07-14 | 7.1818 | 73 | 2022-07-14 | 4.0959 | 73
2022-07-14 01:00 | 7.1591 | 73 | 2022-07-14 01:00 | 4.0959 | 73
2022-07-14 02:00 | 7.1507 | 72 | 2022-07-14 02:00 | 4.0959 | 72
2022-07-14 03:00 | 7.169 | 72 | 2022-07-14 03:00 | 4.0959 | 72
2022-07-14 04:00 | 7.1956 | 74 | 2022-07-14 04:00 | 4.0959 | 74
2022-07-14 05:00 | 7.8506 | 73 | 2022-07-14 05:00 | 4.0959 | 73
2022-07-14 06:00 | 12.0351 | 72 | 2022-07-14 06:00 | 4.0959 | 72
2022-07-14 07:00 | 12.0351 | 73 | 2022-07-14 07:00 | 4.0959 | 73
2022-07-14 08:00 | 12.0351 | 74 | 2022-07-14 08:00 | 4.0959 | 74
Note on T2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: to eliminate data rows when the motor is turned off
Note on V2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Last row with data. The count of data points for the supply fan data. Used for the regression calculations.

## Step 3. Regression
Total Measurement Points |  |  |  | Total Measurement Points
3000 |  |  |  | 3000
Total Measurement Points > 0 |  |  |  | Total Measurement Points > 0
3000 |  |  |  | 3000
Regression Starting Point |  |  |  | Regression Starting Point
26 |  |  |  | 26
Regression Ending Point |  |  |  | Regression Ending Point
3025 |  |  |  | 3025
| OAT^2` | OAT | Constant |  | OAT^2 | OAT | Constant
Coefficient Value | 0.0024251 | -0.28065 | 13.4062 | Coefficient Value | 0.00062366 | -0.077003 | 5.0606
Standard Error | 0.00035987 | 0.0427 | 1.2359 | Standard Error | 9.2736e-05 | 0.011004 | 0.31849
r^2 and se(y) | 0.015106 | 4.1334 | #N/A | r^2 and se(y) | 0.016808 | 1.0651 | #N/A
F-stat and df | 22.9828 | 2997 | #N/A | F-stat and df | 25.6169 | 2997 | #N/A
ssreg and ssresid | 785.3164 | 51203.2758 | #N/A | ssreg and ssresid | 58.1265 | 3400.2036 | #N/A
Sorted Supply Fan RMS Power (kW) | Sorted Supply Fan OAT (F) | Sorted Supply Fan OAT^2 (F) |  | Sorted Return Fan RMS Power (kW) | Sorted Return Fan OAT (F) | Sorted Return Fan OAT^2 (F)
0.79837 | 57 | 3249 |  | 0.72434 | 57 | 3249
0.80043 | 56 | 3136 |  | 0.72638 | 56 | 3136
0.80142 | 57 | 3249 |  | 0.72737 | 57 | 3249
0.80545 | 58 | 3364 |  | 0.73139 | 58 | 3364
0.80644 | 55 | 3025 |  | 0.73238 | 55 | 3025
0.80849 | 57 | 3249 |  | 0.73442 | 57 | 3249
0.81046 | 56 | 3136 |  | 0.7364 | 56 | 3136
0.8185 | 54 | 2916 |  | 0.74445 | 54 | 2916
0.8185 | 67 | 4489 |  | 0.74445 | 67 | 4489
0.8185 | 69 | 4761 |  | 0.74445 | 69 | 4761
0.82356 | 53 | 2809 |  | 0.74954 | 53 | 2809
0.82356 | 70 | 4900 |  | 0.74954 | 70 | 4900
0.82756 | 53 | 2809 |  | 0.75357 | 53 | 2809
0.82855 | 58 | 3364 |  | 0.75456 | 58 | 3364
0.82855 | 62 | 3844 |  | 0.75456 | 62 | 3844
0.82855 | 61 | 3721 |  | 0.75456 | 61 | 3721
0.83051 | 68 | 4624 |  | 0.75654 | 68 | 4624
0.83156 | 60 | 3600 |  | 0.7576 | 60 | 3600
0.83254 | 54 | 2916 |  | 0.75859 | 54 | 2916
0.83254 | 77 | 5929 |  | 0.75859 | 77 | 5929
0.83254 | 76 | 5776 |  | 0.75859 | 76 | 5776
0.83352 | 70 | 4900 |  | 0.75959 | 70 | 4900
0.83352 | 62 | 3844 |  | 0.75959 | 62 | 3844
0.83451 | 58 | 3364 |  | 0.76058 | 58 | 3364
0.83451 | 62 | 3844 |  | 0.76058 | 62 | 3844
0.83451 | 65 | 4225 |  | 0.76058 | 65 | 4225
0.83451 | 67 | 4489 |  | 0.76058 | 67 | 4489
0.83555 | 73 | 5329 |  | 0.76164 | 73 | 5329
0.83752 | 70 | 4900 |  | 0.76362 | 70 | 4900
0.8385 | 53 | 2809 |  | 0.76462 | 53 | 2809
0.8385 | 67 | 4489 |  | 0.76462 | 67 | 4489
0.8385 | 73 | 5329 |  | 0.76462 | 73 | 5329
0.83954 | 77 | 5929 |  | 0.76567 | 77 | 5929
0.84052 | 68 | 4624 |  | 0.76667 | 68 | 4624
0.84052 | 66 | 4356 |  | 0.76667 | 66 | 4356
0.8415 | 70 | 4900 |  | 0.76766 | 70 | 4900
0.84352 | 74 | 5476 |  | 0.76971 | 74 | 5476
0.84352 | 59 | 3481 |  | 0.76971 | 59 | 3481
0.8445 | 71 | 5041 |  | 0.77071 | 71 | 5041
0.8445 | 64 | 4096 |  | 0.77071 | 64 | 4096
0.84548 | 54 | 2916 |  | 0.7717 | 54 | 2916
0.84653 | 74 | 5476 |  | 0.77276 | 74 | 5476
0.8475 | 63 | 3969 |  | 0.77375 | 63 | 3969
0.85148 | 68 | 4624 |  | 0.7778 | 68 | 4624
0.85148 | 75 | 5625 |  | 0.7778 | 75 | 5625
0.85245 | 66 | 4356 |  | 0.77879 | 66 | 4356
0.85245 | 63 | 3969 |  | 0.77879 | 63 | 3969
0.85343 | 78 | 6084 |  | 0.77979 | 78 | 6084
0.85343 | 71 | 5041 |  | 0.77979 | 71 | 5041
0.85447 | 69 | 4761 |  | 0.78085 | 69 | 4761
0.85447 | 71 | 5041 |  | 0.78085 | 71 | 5041
0.85447 | 69 | 4761 |  | 0.78085 | 69 | 4761
0.85447 | 70 | 4900 |  | 0.78085 | 70 | 4900
0.85447 | 80 | 6400 |  | 0.78085 | 80 | 6400
0.85545 | 63 | 3969 |  | 0.78184 | 63 | 3969
0.85844 | 66 | 4356 |  | 0.78489 | 66 | 4356
0.85941 | 46 | 2116 |  | 0.78589 | 46 | 2116
0.85941 | 66 | 4356 |  | 0.78589 | 66 | 4356
0.86038 | 62 | 3844 |  | 0.78688 | 62 | 3844
0.86136 | 75 | 5625 |  | 0.78788 | 75 | 5625
0.86136 | 72 | 5184 |  | 0.78788 | 72 | 5184
0.8624 | 75 | 5625 |  | 0.78894 | 75 | 5625
0.86337 | 70 | 4900 |  | 0.78994 | 70 | 4900
0.86337 | 64 | 4096 |  | 0.78994 | 64 | 4096
0.86434 | 44 | 1936 |  | 0.79093 | 44 | 1936
0.86434 | 59 | 3481 |  | 0.79093 | 59 | 3481
0.86434 | 71 | 5041 |  | 0.79093 | 71 | 5041
0.86434 | 79 | 6241 |  | 0.79093 | 79 | 6241
0.86434 | 72 | 5184 |  | 0.79093 | 72 | 5184
0.86532 | 73 | 5329 |  | 0.79193 | 73 | 5329
0.86532 | 81 | 6561 |  | 0.79193 | 81 | 6561
0.86532 | 79 | 6241 |  | 0.79193 | 79 | 6241
0.86635 | 45 | 2025 |  | 0.79299 | 45 | 2025
0.86635 | 69 | 4761 |  | 0.79299 | 69 | 4761
0.86635 | 64 | 4096 |  | 0.79299 | 64 | 4096
0.8683 | 68 | 4624 |  | 0.79498 | 68 | 4624
0.86927 | 51 | 2601 |  | 0.79598 | 51 | 2601
0.86927 | 65 | 4225 |  | 0.79598 | 65 | 4225
0.8703 | 43 | 1849 |  | 0.79704 | 43 | 1849
0.87127 | 45 | 2025 |  | 0.79804 | 45 | 2025
0.87127 | 80 | 6400 |  | 0.79804 | 80 | 6400
0.87225 | 58 | 3364 |  | 0.79904 | 58 | 3364
0.87225 | 63 | 3969 |  | 0.79904 | 63 | 3969
0.87225 | 73 | 5329 |  | 0.79904 | 73 | 5329
0.87328 | 48 | 2304 |  | 0.8001 | 48 | 2304
0.87328 | 80 | 6400 |  | 0.8001 | 80 | 6400
0.87522 | 74 | 5476 |  | 0.8021 | 74 | 5476
0.87522 | 71 | 5041 |  | 0.8021 | 71 | 5041
0.87619 | 51 | 2601 |  | 0.80309 | 51 | 2601
0.87619 | 45 | 2025 |  | 0.80309 | 45 | 2025
0.87619 | 42 | 1764 |  | 0.80309 | 42 | 1764
0.87619 | 62 | 3844 |  | 0.80309 | 62 | 3844
0.87722 | 43 | 1849 |  | 0.80416 | 43 | 1849
0.87722 | 58 | 3364 |  | 0.80416 | 58 | 3364
0.87819 | 43 | 1849 |  | 0.80515 | 43 | 1849
0.87819 | 45 | 2025 |  | 0.80515 | 45 | 2025
0.87819 | 46 | 2116 |  | 0.80515 | 46 | 2116
0.87819 | 55 | 3025 |  | 0.80515 | 55 | 3025
0.87819 | 66 | 4356 |  | 0.80515 | 66 | 4356
0.87819 | 70 | 4900 |  | 0.80515 | 70 | 4900
0.87916 | 41 | 1681 |  | 0.80615 | 41 | 1681
0.87916 | 65 | 4225 |  | 0.80615 | 65 | 4225
0.88013 | 43 | 1849 |  | 0.80715 | 43 | 1849
0.88013 | 40 | 1600 |  | 0.80715 | 40 | 1600
0.88013 | 51 | 2601 |  | 0.80715 | 51 | 2601
0.88013 | 66 | 4356 |  | 0.80715 | 66 | 4356
0.88013 | 64 | 4096 |  | 0.80715 | 64 | 4096
0.88116 | 56 | 3136 |  | 0.80821 | 56 | 3136
0.88116 | 57 | 3249 |  | 0.80821 | 57 | 3249
0.88116 | 81 | 6561 |  | 0.80821 | 81 | 6561
0.88116 | 63 | 3969 |  | 0.80821 | 63 | 3969
0.88213 | 44 | 1936 |  | 0.80921 | 44 | 1936
0.88213 | 84 | 7056 |  | 0.80921 | 84 | 7056
0.88213 | 57 | 3249 |  | 0.80921 | 57 | 3249
0.88213 | 65 | 4225 |  | 0.80921 | 65 | 4225
0.88213 | 65 | 4225 |  | 0.80921 | 65 | 4225
0.8831 | 53 | 2809 |  | 0.81021 | 53 | 2809
0.8831 | 46 | 2116 |  | 0.81021 | 46 | 2116
0.8851 | 48 | 2304 |  | 0.81227 | 48 | 2304
0.8851 | 41 | 1681 |  | 0.81227 | 41 | 1681
0.8851 | 46 | 2116 |  | 0.81227 | 46 | 2116
0.8851 | 52 | 2704 |  | 0.81227 | 52 | 2704
0.8851 | 61 | 3721 |  | 0.81227 | 61 | 3721
0.88606 | 58 | 3364 |  | 0.81327 | 58 | 3364
0.88606 | 41 | 1681 |  | 0.81327 | 41 | 1681
0.88606 | 43 | 1849 |  | 0.81327 | 43 | 1849
0.88606 | 59 | 3481 |  | 0.81327 | 59 | 3481
0.88606 | 59 | 3481 |  | 0.81327 | 59 | 3481
0.88703 | 58 | 3364 |  | 0.81427 | 58 | 3364
0.888 | 45 | 2025 |  | 0.81527 | 45 | 2025
0.888 | 43 | 1849 |  | 0.81527 | 43 | 1849
0.888 | 69 | 4761 |  | 0.81527 | 69 | 4761
0.88903 | 44 | 1936 |  | 0.81634 | 44 | 1936
0.88903 | 43 | 1849 |  | 0.81634 | 43 | 1849
0.88903 | 39 | 1521 |  | 0.81634 | 39 | 1521
0.88903 | 44 | 1936 |  | 0.81634 | 44 | 1936
0.88903 | 82 | 6724 |  | 0.81634 | 82 | 6724
0.88903 | 63 | 3969 |  | 0.81634 | 63 | 3969
0.88999 | 43 | 1849 |  | 0.81733 | 43 | 1849
0.88999 | 50 | 2500 |  | 0.81733 | 50 | 2500
0.88999 | 55 | 3025 |  | 0.81733 | 55 | 3025
0.89096 | 51 | 2601 |  | 0.81833 | 51 | 2601
0.89096 | 40 | 1600 |  | 0.81833 | 40 | 1600
0.89096 | 62 | 3844 |  | 0.81833 | 62 | 3844
0.89192 | 45 | 2025 |  | 0.81933 | 45 | 2025
0.89192 | 40 | 1600 |  | 0.81933 | 40 | 1600
0.89192 | 69 | 4761 |  | 0.81933 | 69 | 4761
0.89295 | 42 | 1764 |  | 0.8204 | 42 | 1764
0.89392 | 41 | 1681 |  | 0.8214 | 41 | 1681
0.89392 | 40 | 1600 |  | 0.8214 | 40 | 1600
0.89392 | 50 | 2500 |  | 0.8214 | 50 | 2500
0.89392 | 50 | 2500 |  | 0.8214 | 50 | 2500
0.89392 | 86 | 7396 |  | 0.8214 | 86 | 7396
0.89392 | 67 | 4489 |  | 0.8214 | 67 | 4489
0.89488 | 44 | 1936 |  | 0.8224 | 44 | 1936
0.89488 | 61 | 3721 |  | 0.8224 | 61 | 3721
0.89488 | 59 | 3481 |  | 0.8224 | 59 | 3481
0.89585 | 41 | 1681 |  | 0.8234 | 41 | 1681
0.89585 | 54 | 2916 |  | 0.8234 | 54 | 2916
0.89585 | 54 | 2916 |  | 0.8234 | 54 | 2916
0.89585 | 54 | 2916 |  | 0.8234 | 54 | 2916
0.89585 | 57 | 3249 |  | 0.8234 | 57 | 3249
0.89585 | 59 | 3481 |  | 0.8234 | 59 | 3481
0.89687 | 62 | 3844 |  | 0.82446 | 62 | 3844
0.89784 | 48 | 2304 |  | 0.82546 | 48 | 2304
0.89784 | 42 | 1764 |  | 0.82546 | 42 | 1764
0.89784 | 51 | 2601 |  | 0.82546 | 51 | 2601
0.89784 | 73 | 5329 |  | 0.82546 | 73 | 5329
0.8988 | 46 | 2116 |  | 0.82646 | 46 | 2116
0.8988 | 51 | 2601 |  | 0.82646 | 51 | 2601
0.8988 | 52 | 2704 |  | 0.82646 | 52 | 2704
0.8988 | 66 | 4356 |  | 0.82646 | 66 | 4356
0.89983 | 46 | 2116 |  | 0.82753 | 46 | 2116
0.89983 | 42 | 1764 |  | 0.82753 | 42 | 1764
0.89983 | 52 | 2704 |  | 0.82753 | 52 | 2704
0.89983 | 51 | 2601 |  | 0.82753 | 51 | 2601
0.89983 | 40 | 1600 |  | 0.82753 | 40 | 1600
0.89983 | 56 | 3136 |  | 0.82753 | 56 | 3136
0.89983 | 58 | 3364 |  | 0.82753 | 58 | 3364
0.90079 | 45 | 2025 |  | 0.82853 | 45 | 2025
0.90079 | 66 | 4356 |  | 0.82853 | 66 | 4356
0.90175 | 47 | 2209 |  | 0.82953 | 47 | 2209
0.90175 | 39 | 1521 |  | 0.82953 | 39 | 1521
0.90175 | 42 | 1764 |  | 0.82953 | 42 | 1764
0.90175 | 50 | 2500 |  | 0.82953 | 50 | 2500
0.90175 | 43 | 1849 |  | 0.82953 | 43 | 1849
0.90175 | 45 | 2025 |  | 0.82953 | 45 | 2025
0.90175 | 46 | 2116 |  | 0.82953 | 46 | 2116
0.90175 | 63 | 3969 |  | 0.82953 | 63 | 3969
0.90272 | 58 | 3364 |  | 0.83053 | 58 | 3364
0.90272 | 71 | 5041 |  | 0.83053 | 71 | 5041
0.90272 | 66 | 4356 |  | 0.83053 | 66 | 4356
0.90374 | 40 | 1600 |  | 0.8316 | 40 | 1600
0.90374 | 68 | 4624 |  | 0.8316 | 68 | 4624
0.90374 | 54 | 2916 |  | 0.8316 | 54 | 2916
0.9047 | 51 | 2601 |  | 0.8326 | 51 | 2601
0.9047 | 48 | 2304 |  | 0.8326 | 48 | 2304
0.90567 | 50 | 2500 |  | 0.8336 | 50 | 2500
0.90567 | 47 | 2209 |  | 0.8336 | 47 | 2209
0.90663 | 44 | 1936 |  | 0.8346 | 44 | 1936
0.90765 | 47 | 2209 |  | 0.83567 | 47 | 2209
0.90765 | 64 | 4096 |  | 0.83567 | 64 | 4096
0.90861 | 48 | 2304 |  | 0.83667 | 48 | 2304
0.90861 | 40 | 1600 |  | 0.83667 | 40 | 1600
0.90861 | 45 | 2025 |  | 0.83667 | 45 | 2025
0.90861 | 47 | 2209 |  | 0.83667 | 47 | 2209
0.90861 | 55 | 3025 |  | 0.83667 | 55 | 3025
0.90861 | 55 | 3025 |  | 0.83667 | 55 | 3025
0.90861 | 62 | 3844 |  | 0.83667 | 62 | 3844
0.90957 | 46 | 2116 |  | 0.83767 | 46 | 2116
0.90957 | 68 | 4624 |  | 0.83767 | 68 | 4624
0.90957 | 63 | 3969 |  | 0.83767 | 63 | 3969
0.91053 | 41 | 1681 |  | 0.83867 | 41 | 1681
0.91053 | 48 | 2304 |  | 0.83867 | 48 | 2304
0.91053 | 47 | 2209 |  | 0.83867 | 47 | 2209
0.91053 | 58 | 3364 |  | 0.83867 | 58 | 3364
0.91156 | 41 | 1681 |  | 0.83974 | 41 | 1681
0.91156 | 47 | 2209 |  | 0.83974 | 47 | 2209
0.91156 | 56 | 3136 |  | 0.83974 | 56 | 3136
0.91252 | 48 | 2304 |  | 0.84074 | 48 | 2304
0.91348 | 45 | 2025 |  | 0.84175 | 45 | 2025
0.91348 | 47 | 2209 |  | 0.84175 | 47 | 2209
0.91348 | 52 | 2704 |  | 0.84175 | 52 | 2704
0.91348 | 59 | 3481 |  | 0.84175 | 59 | 3481
0.91444 | 40 | 1600 |  | 0.84275 | 40 | 1600
0.91444 | 67 | 4489 |  | 0.84275 | 67 | 4489
0.91546 | 59 | 3481 |  | 0.84382 | 59 | 3481
0.91546 | 58 | 3364 |  | 0.84382 | 58 | 3364
0.91642 | 73 | 5329 |  | 0.84482 | 73 | 5329
0.91642 | 57 | 3249 |  | 0.84482 | 57 | 3249
0.91642 | 67 | 4489 |  | 0.84482 | 67 | 4489
0.91738 | 56 | 3136 |  | 0.84582 | 56 | 3136
0.91738 | 64 | 4096 |  | 0.84582 | 64 | 4096
0.91833 | 54 | 2916 |  | 0.84682 | 54 | 2916
0.91833 | 54 | 2916 |  | 0.84682 | 54 | 2916
0.91833 | 74 | 5476 |  | 0.84682 | 74 | 5476
0.91936 | 39 | 1521 |  | 0.84789 | 39 | 1521
0.91936 | 68 | 4624 |  | 0.84789 | 68 | 4624
0.92031 | 68 | 4624 |  | 0.8489 | 68 | 4624
0.92031 | 67 | 4489 |  | 0.8489 | 67 | 4489
0.92127 | 47 | 2209 |  | 0.8499 | 47 | 2209
0.92127 | 56 | 3136 |  | 0.8499 | 56 | 3136
0.92223 | 39 | 1521 |  | 0.8509 | 39 | 1521
0.92223 | 58 | 3364 |  | 0.8509 | 58 | 3364
0.92223 | 55 | 3025 |  | 0.8509 | 55 | 3025
0.92223 | 68 | 4624 |  | 0.8509 | 68 | 4624
0.92325 | 50 | 2500 |  | 0.85197 | 50 | 2500
0.9242 | 47 | 2209 |  | 0.85297 | 47 | 2209
0.9242 | 65 | 4225 |  | 0.85297 | 65 | 4225
0.9242 | 62 | 3844 |  | 0.85297 | 62 | 3844
0.92516 | 47 | 2209 |  | 0.85398 | 47 | 2209
0.92516 | 54 | 2916 |  | 0.85398 | 54 | 2916
0.92618 | 66 | 4356 |  | 0.85505 | 66 | 4356
0.92714 | 40 | 1600 |  | 0.85605 | 40 | 1600
0.92714 | 56 | 3136 |  | 0.85605 | 56 | 3136
0.92809 | 89 | 7921 |  | 0.85705 | 89 | 7921
0.92809 | 66 | 4356 |  | 0.85705 | 66 | 4356
0.92809 | 73 | 5329 |  | 0.85705 | 73 | 5329
0.92905 | 44 | 1936 |  | 0.85806 | 44 | 1936
0.92905 | 54 | 2916 |  | 0.85806 | 54 | 2916
0.93102 | 60 | 3600 |  | 0.86013 | 60 | 3600
0.93102 | 67 | 4489 |  | 0.86013 | 67 | 4489
0.93198 | 44 | 1936 |  | 0.86114 | 44 | 1936
0.93198 | 58 | 3364 |  | 0.86114 | 58 | 3364
0.93395 | 61 | 3721 |  | 0.86321 | 61 | 3721
0.93395 | 54 | 2916 |  | 0.86321 | 54 | 2916
0.93395 | 68 | 4624 |  | 0.86321 | 68 | 4624
0.9349 | 54 | 2916 |  | 0.86422 | 54 | 2916
0.93681 | 50 | 2500 |  | 0.86623 | 50 | 2500
0.93681 | 61 | 3721 |  | 0.86623 | 61 | 3721
0.93783 | 49 | 2401 |  | 0.8673 | 49 | 2401
0.93878 | 55 | 3025 |  | 0.8683 | 55 | 3025
0.94068 | 61 | 3721 |  | 0.87031 | 61 | 3721
0.9417 | 67 | 4489 |  | 0.87138 | 67 | 4489
0.94265 | 48 | 2304 |  | 0.87239 | 48 | 2304
0.9436 | 57 | 3249 |  | 0.87339 | 57 | 3249
0.94652 | 50 | 2500 |  | 0.87648 | 50 | 2500
0.94842 | 54 | 2916 |  | 0.87849 | 54 | 2916
0.9533 | 90 | 8100 |  | 0.88365 | 90 | 8100
0.95425 | 52 | 2704 |  | 0.88466 | 52 | 2704
0.95621 | 47 | 2209 |  | 0.88674 | 47 | 2209
0.95621 | 68 | 4624 |  | 0.88674 | 68 | 4624
0.95716 | 49 | 2401 |  | 0.88775 | 49 | 2401
0.96006 | 61 | 3721 |  | 0.89083 | 61 | 3721
0.96006 | 59 | 3481 |  | 0.89083 | 59 | 3481
0.96196 | 49 | 2401 |  | 0.89285 | 49 | 2401
0.96291 | 60 | 3600 |  | 0.89386 | 60 | 3600
0.96776 | 60 | 3600 |  | 0.89903 | 60 | 3600
0.9706 | 59 | 3481 |  | 0.90205 | 59 | 3481
0.9706 | 70 | 4900 |  | 0.90205 | 70 | 4900
0.97161 | 60 | 3600 |  | 0.90313 | 60 | 3600
0.97444 | 60 | 3600 |  | 0.90615 | 60 | 3600
0.97734 | 56 | 3136 |  | 0.90925 | 56 | 3136
0.98023 | 52 | 2704 |  | 0.91234 | 52 | 2704
0.98218 | 59 | 3481 |  | 0.91443 | 59 | 3481
0.98218 | 57 | 3249 |  | 0.91443 | 57 | 3249
0.985 | 58 | 3364 |  | 0.91745 | 58 | 3364
0.98601 | 59 | 3481 |  | 0.91853 | 59 | 3481
0.98984 | 52 | 2704 |  | 0.92264 | 52 | 2704
0.99366 | 59 | 3481 |  | 0.92675 | 59 | 3481
1.0051 | 61 | 3721 |  | 0.93908 | 61 | 3721
1.0582 | 66 | 4356 |  | 0.99677 | 66 | 4356
1.1173 | 70 | 4900 |  | 1.062 | 70 | 4900
1.1312 | 70 | 4900 |  | 1.0774 | 70 | 4900
1.1322 | 71 | 5041 |  | 1.0785 | 71 | 5041
1.1387 | 68 | 4624 |  | 1.0858 | 68 | 4624
1.1451 | 70 | 4900 |  | 1.093 | 70 | 4900
1.1516 | 68 | 4624 |  | 1.1002 | 68 | 4624
1.1553 | 71 | 5041 |  | 1.1044 | 71 | 5041
1.1572 | 70 | 4900 |  | 1.1065 | 70 | 4900
1.1664 | 75 | 5625 |  | 1.1168 | 75 | 5625
1.1664 | 73 | 5329 |  | 1.1168 | 73 | 5329
1.1738 | 69 | 4761 |  | 1.125 | 69 | 4761
1.1886 | 75 | 5625 |  | 1.1416 | 75 | 5625
1.196 | 61 | 3721 |  | 1.1499 | 61 | 3721
1.207 | 63 | 3969 |  | 1.1623 | 63 | 3969
1.2144 | 61 | 3721 |  | 1.1705 | 61 | 3721
1.2153 | 62 | 3844 |  | 1.1716 | 62 | 3844
1.2226 | 71 | 5041 |  | 1.1798 | 71 | 5041
1.2235 | 63 | 3969 |  | 1.1808 | 63 | 3969
1.2245 | 62 | 3844 |  | 1.1819 | 62 | 3844
1.2291 | 63 | 3969 |  | 1.187 | 63 | 3969
1.23 | 72 | 5184 |  | 1.1881 | 72 | 5184
1.2309 | 73 | 5329 |  | 1.1891 | 73 | 5329
1.2309 | 62 | 3844 |  | 1.1891 | 62 | 3844
1.2345 | 62 | 3844 |  | 1.1932 | 62 | 3844
1.2345 | 64 | 4096 |  | 1.1932 | 64 | 4096
1.2364 | 66 | 4356 |  | 1.1953 | 66 | 4356
1.2419 | 66 | 4356 |  | 1.2015 | 66 | 4356
1.2437 | 63 | 3969 |  | 1.2035 | 63 | 3969
1.2437 | 62 | 3844 |  | 1.2035 | 62 | 3844
1.2446 | 70 | 4900 |  | 1.2045 | 70 | 4900
1.2456 | 74 | 5476 |  | 1.2056 | 74 | 5476
1.2474 | 74 | 5476 |  | 1.2076 | 74 | 5476
1.2483 | 72 | 5184 |  | 1.2086 | 72 | 5184
1.2493 | 64 | 4096 |  | 1.2097 | 64 | 4096
1.2493 | 64 | 4096 |  | 1.2097 | 64 | 4096
1.2493 | 74 | 5476 |  | 1.2097 | 74 | 5476
1.2502 | 62 | 3844 |  | 1.2107 | 62 | 3844
1.2502 | 72 | 5184 |  | 1.2107 | 72 | 5184
1.2511 | 69 | 4761 |  | 1.2118 | 69 | 4761
1.2519 | 54 | 2916 |  | 1.2128 | 54 | 2916
1.2529 | 55 | 3025 |  | 1.2138 | 55 | 3025
1.2529 | 64 | 4096 |  | 1.2138 | 64 | 4096
1.2538 | 63 | 3969 |  | 1.2149 | 63 | 3969
1.2538 | 65 | 4225 |  | 1.2149 | 65 | 4225
1.2547 | 64 | 4096 |  | 1.2159 | 64 | 4096
1.2547 | 58 | 3364 |  | 1.2159 | 58 | 3364
1.2547 | 53 | 2809 |  | 1.2159 | 53 | 2809
1.2547 | 57 | 3249 |  | 1.2159 | 57 | 3249
1.2547 | 61 | 3721 |  | 1.2159 | 61 | 3721
1.2547 | 69 | 4761 |  | 1.2159 | 69 | 4761
1.2566 | 64 | 4096 |  | 1.218 | 64 | 4096
1.2584 | 64 | 4096 |  | 1.22 | 64 | 4096
1.2584 | 71 | 5041 |  | 1.22 | 71 | 5041
1.2593 | 66 | 4356 |  | 1.221 | 66 | 4356
1.2593 | 73 | 5329 |  | 1.221 | 73 | 5329
1.2593 | 65 | 4225 |  | 1.221 | 65 | 4225
1.2602 | 54 | 2916 |  | 1.2221 | 54 | 2916
1.2611 | 71 | 5041 |  | 1.2231 | 71 | 5041
1.263 | 67 | 4489 |  | 1.2252 | 67 | 4489
1.2648 | 52 | 2704 |  | 1.2272 | 52 | 2704
1.2648 | 67 | 4489 |  | 1.2272 | 67 | 4489
1.2666 | 63 | 3969 |  | 1.2293 | 63 | 3969
1.2666 | 63 | 3969 |  | 1.2293 | 63 | 3969
1.2675 | 72 | 5184 |  | 1.2303 | 72 | 5184
1.2684 | 61 | 3721 |  | 1.2313 | 61 | 3721
1.2684 | 70 | 4900 |  | 1.2313 | 70 | 4900
1.2703 | 61 | 3721 |  | 1.2334 | 61 | 3721
1.2703 | 56 | 3136 |  | 1.2334 | 56 | 3136
1.2748 | 70 | 4900 |  | 1.2385 | 70 | 4900
1.2757 | 74 | 5476 |  | 1.2395 | 74 | 5476
1.2766 | 59 | 3481 |  | 1.2405 | 59 | 3481
1.2785 | 59 | 3481 |  | 1.2426 | 59 | 3481
1.2785 | 63 | 3969 |  | 1.2426 | 63 | 3969
1.2794 | 63 | 3969 |  | 1.2436 | 63 | 3969
1.2803 | 65 | 4225 |  | 1.2446 | 65 | 4225
1.2803 | 65 | 4225 |  | 1.2446 | 65 | 4225
1.2812 | 59 | 3481 |  | 1.2457 | 59 | 3481
1.2812 | 64 | 4096 |  | 1.2457 | 64 | 4096
1.2812 | 66 | 4356 |  | 1.2457 | 66 | 4356
1.2812 | 72 | 5184 |  | 1.2457 | 72 | 5184
1.2812 | 72 | 5184 |  | 1.2457 | 72 | 5184
1.2821 | 63 | 3969 |  | 1.2467 | 63 | 3969
1.2849 | 63 | 3969 |  | 1.2498 | 63 | 3969
1.2858 | 64 | 4096 |  | 1.2508 | 64 | 4096
1.2858 | 67 | 4489 |  | 1.2508 | 67 | 4489
1.2867 | 51 | 2601 |  | 1.2518 | 51 | 2601
1.2867 | 73 | 5329 |  | 1.2518 | 73 | 5329
1.2876 | 69 | 4761 |  | 1.2528 | 69 | 4761
1.2885 | 57 | 3249 |  | 1.2539 | 57 | 3249
1.2885 | 57 | 3249 |  | 1.2539 | 57 | 3249
1.2903 | 66 | 4356 |  | 1.2559 | 66 | 4356
1.2922 | 64 | 4096 |  | 1.258 | 64 | 4096
1.2922 | 73 | 5329 |  | 1.258 | 73 | 5329
1.2931 | 66 | 4356 |  | 1.259 | 66 | 4356
1.2939 | 53 | 2809 |  | 1.26 | 53 | 2809
1.2939 | 50 | 2500 |  | 1.26 | 50 | 2500
1.2958 | 57 | 3249 |  | 1.2621 | 57 | 3249
1.2967 | 55 | 3025 |  | 1.2631 | 55 | 3025
1.2967 | 40 | 1600 |  | 1.2631 | 40 | 1600
1.2976 | 55 | 3025 |  | 1.2641 | 55 | 3025
1.2976 | 45 | 2025 |  | 1.2641 | 45 | 2025
1.2976 | 39 | 1521 |  | 1.2641 | 39 | 1521
1.2994 | 54 | 2916 |  | 1.2662 | 54 | 2916
1.3003 | 63 | 3969 |  | 1.2672 | 63 | 3969
1.3003 | 56 | 3136 |  | 1.2672 | 56 | 3136
1.3012 | 53 | 2809 |  | 1.2682 | 53 | 2809
1.3012 | 45 | 2025 |  | 1.2682 | 45 | 2025
1.3022 | 45 | 2025 |  | 1.2692 | 45 | 2025
1.304 | 51 | 2601 |  | 1.2713 | 51 | 2601
1.304 | 50 | 2500 |  | 1.2713 | 50 | 2500
1.3058 | 50 | 2500 |  | 1.2733 | 50 | 2500
1.3067 | 45 | 2025 |  | 1.2743 | 45 | 2025
1.3067 | 49 | 2401 |  | 1.2743 | 49 | 2401
1.3076 | 61 | 3721 |  | 1.2753 | 61 | 3721
1.3085 | 41 | 1681 |  | 1.2763 | 41 | 1681
1.3085 | 38 | 1444 |  | 1.2763 | 38 | 1444
1.3121 | 62 | 3844 |  | 1.2804 | 62 | 3844
1.3121 | 50 | 2500 |  | 1.2804 | 50 | 2500
1.3121 | 43 | 1849 |  | 1.2804 | 43 | 1849
1.3131 | 62 | 3844 |  | 1.2815 | 62 | 3844
1.3131 | 51 | 2601 |  | 1.2815 | 51 | 2601
1.314 | 46 | 2116 |  | 1.2825 | 46 | 2116
1.3149 | 38 | 1444 |  | 1.2835 | 38 | 1444
1.3167 | 50 | 2500 |  | 1.2856 | 50 | 2500
1.3185 | 45 | 2025 |  | 1.2876 | 45 | 2025
1.3185 | 48 | 2304 |  | 1.2876 | 48 | 2304
1.3195 | 62 | 3844 |  | 1.2887 | 62 | 3844
1.3195 | 57 | 3249 |  | 1.2887 | 57 | 3249
1.3195 | 45 | 2025 |  | 1.2887 | 45 | 2025
1.3204 | 51 | 2601 |  | 1.2897 | 51 | 2601
1.3222 | 44 | 1936 |  | 1.2917 | 44 | 1936
1.3222 | 49 | 2401 |  | 1.2917 | 49 | 2401
1.324 | 54 | 2916 |  | 1.2937 | 54 | 2916
1.3249 | 48 | 2304 |  | 1.2947 | 48 | 2304
1.3267 | 68 | 4624 |  | 1.2968 | 68 | 4624
1.3276 | 51 | 2601 |  | 1.2978 | 51 | 2601
1.3285 | 47 | 2209 |  | 1.2988 | 47 | 2209
1.3285 | 46 | 2116 |  | 1.2988 | 46 | 2116
1.3304 | 54 | 2916 |  | 1.3009 | 54 | 2916
1.3322 | 62 | 3844 |  | 1.3029 | 62 | 3844
1.3322 | 60 | 3600 |  | 1.3029 | 60 | 3600
1.3322 | 55 | 3025 |  | 1.3029 | 55 | 3025
1.333 | 63 | 3969 |  | 1.3039 | 63 | 3969
1.3349 | 48 | 2304 |  | 1.3059 | 48 | 2304
1.3349 | 45 | 2025 |  | 1.3059 | 45 | 2025
1.3349 | 41 | 1681 |  | 1.3059 | 41 | 1681
1.3385 | 49 | 2401 |  | 1.31 | 49 | 2401
1.3394 | 58 | 3364 |  | 1.311 | 58 | 3364
1.3394 | 48 | 2304 |  | 1.311 | 48 | 2304
1.3413 | 47 | 2209 |  | 1.3131 | 47 | 2209
1.3449 | 49 | 2401 |  | 1.3171 | 49 | 2401
1.3485 | 53 | 2809 |  | 1.3212 | 53 | 2809
1.3485 | 43 | 1849 |  | 1.3212 | 43 | 1849
1.3494 | 66 | 4356 |  | 1.3222 | 66 | 4356
1.3503 | 43 | 1849 |  | 1.3232 | 43 | 1849
1.3521 | 44 | 1936 |  | 1.3252 | 44 | 1936
1.3558 | 46 | 2116 |  | 1.3293 | 46 | 2116
1.3621 | 49 | 2401 |  | 1.3364 | 49 | 2401
1.6087 | 63 | 3969 |  | 1.6027 | 63 | 3969
1.6142 | 64 | 4096 |  | 1.6083 | 64 | 4096
1.6169 | 79 | 6241 |  | 1.6111 | 79 | 6241
1.6205 | 58 | 3364 |  | 1.6148 | 58 | 3364
1.6205 | 55 | 3025 |  | 1.6148 | 55 | 3025
1.6214 | 60 | 3600 |  | 1.6157 | 60 | 3600
1.6232 | 57 | 3249 |  | 1.6176 | 57 | 3249
1.6241 | 59 | 3481 |  | 1.6185 | 59 | 3481
1.625 | 57 | 3249 |  | 1.6194 | 57 | 3249
1.6268 | 56 | 3136 |  | 1.6212 | 56 | 3136
1.6277 | 79 | 6241 |  | 1.6222 | 79 | 6241
1.6277 | 75 | 5625 |  | 1.6222 | 75 | 5625
1.6286 | 60 | 3600 |  | 1.6231 | 60 | 3600
1.6286 | 73 | 5329 |  | 1.6231 | 73 | 5329
1.6313 | 60 | 3600 |  | 1.6258 | 60 | 3600
1.6313 | 61 | 3721 |  | 1.6258 | 61 | 3721
1.6322 | 71 | 5041 |  | 1.6267 | 71 | 5041
1.6331 | 76 | 5776 |  | 1.6276 | 76 | 5776
1.6341 | 87 | 7569 |  | 1.6286 | 87 | 7569
1.635 | 58 | 3364 |  | 1.6295 | 58 | 3364
1.635 | 78 | 6084 |  | 1.6295 | 78 | 6084
1.6367 | 59 | 3481 |  | 1.6313 | 59 | 3481
1.6367 | 60 | 3600 |  | 1.6313 | 60 | 3600
1.6377 | 62 | 3844 |  | 1.6323 | 62 | 3844
1.6386 | 60 | 3600 |  | 1.6332 | 60 | 3600
1.6386 | 61 | 3721 |  | 1.6332 | 61 | 3721
1.6386 | 60 | 3600 |  | 1.6332 | 60 | 3600
1.6395 | 58 | 3364 |  | 1.6341 | 58 | 3364
1.6404 | 62 | 3844 |  | 1.635 | 62 | 3844
1.6413 | 61 | 3721 |  | 1.6359 | 61 | 3721
1.6413 | 56 | 3136 |  | 1.6359 | 56 | 3136
1.6413 | 83 | 6889 |  | 1.6359 | 83 | 6889
1.6413 | 77 | 5929 |  | 1.6359 | 77 | 5929
1.6431 | 60 | 3600 |  | 1.6377 | 60 | 3600
1.644 | 58 | 3364 |  | 1.6387 | 58 | 3364
1.644 | 60 | 3600 |  | 1.6387 | 60 | 3600
1.6449 | 59 | 3481 |  | 1.6396 | 59 | 3481
1.6449 | 58 | 3364 |  | 1.6396 | 58 | 3364
1.6458 | 58 | 3364 |  | 1.6405 | 58 | 3364
1.6467 | 60 | 3600 |  | 1.6414 | 60 | 3600
1.6467 | 64 | 4096 |  | 1.6414 | 64 | 4096
1.6476 | 63 | 3969 |  | 1.6424 | 63 | 3969
1.6494 | 62 | 3844 |  | 1.6441 | 62 | 3844
1.6494 | 64 | 4096 |  | 1.6441 | 64 | 4096
1.6503 | 69 | 4761 |  | 1.645 | 69 | 4761
1.6503 | 57 | 3249 |  | 1.645 | 57 | 3249
1.653 | 66 | 4356 |  | 1.6478 | 66 | 4356
1.6539 | 68 | 4624 |  | 1.6487 | 68 | 4624
1.6549 | 58 | 3364 |  | 1.6496 | 58 | 3364
1.6549 | 59 | 3481 |  | 1.6496 | 59 | 3481
1.6567 | 58 | 3364 |  | 1.6514 | 58 | 3364
1.6575 | 59 | 3481 |  | 1.6523 | 59 | 3481
1.6575 | 70 | 4900 |  | 1.6523 | 70 | 4900
1.6575 | 70 | 4900 |  | 1.6523 | 70 | 4900
1.6594 | 61 | 3721 |  | 1.6542 | 61 | 3721
1.6612 | 67 | 4489 |  | 1.6559 | 67 | 4489
1.6639 | 59 | 3481 |  | 1.6587 | 59 | 3481
1.6639 | 67 | 4489 |  | 1.6587 | 67 | 4489
1.6639 | 81 | 6561 |  | 1.6587 | 81 | 6561
1.6648 | 59 | 3481 |  | 1.6596 | 59 | 3481
1.6657 | 65 | 4225 |  | 1.6605 | 65 | 4225
1.6666 | 61 | 3721 |  | 1.6614 | 61 | 3721
1.6694 | 65 | 4225 |  | 1.6641 | 65 | 4225
1.6711 | 59 | 3481 |  | 1.6659 | 59 | 3481
1.6721 | 58 | 3364 |  | 1.6668 | 58 | 3364
1.6721 | 68 | 4624 |  | 1.6668 | 68 | 4624
1.6766 | 59 | 3481 |  | 1.6713 | 59 | 3481
1.6784 | 68 | 4624 |  | 1.6731 | 68 | 4624
1.6802 | 64 | 4096 |  | 1.6749 | 64 | 4096
1.6838 | 68 | 4624 |  | 1.6785 | 68 | 4624
1.6875 | 84 | 7056 |  | 1.6821 | 84 | 7056
1.9259 | 72 | 5184 |  | 1.8987 | 72 | 5184
1.9388 | 70 | 4900 |  | 1.9093 | 70 | 4900
1.9415 | 71 | 5041 |  | 1.9116 | 71 | 5041
1.9434 | 77 | 5929 |  | 1.9131 | 77 | 5929
1.9452 | 70 | 4900 |  | 1.9146 | 70 | 4900
1.9471 | 74 | 5476 |  | 1.9161 | 74 | 5476
1.9535 | 71 | 5041 |  | 1.9213 | 71 | 5041
1.9591 | 79 | 6241 |  | 1.9258 | 79 | 6241
1.96 | 78 | 6084 |  | 1.9265 | 78 | 6084
1.9609 | 71 | 5041 |  | 1.9272 | 71 | 5041
1.9609 | 68 | 4624 |  | 1.9272 | 68 | 4624
1.9646 | 76 | 5776 |  | 1.9302 | 76 | 5776
1.9656 | 68 | 4624 |  | 1.931 | 68 | 4624
1.9656 | 70 | 4900 |  | 1.931 | 70 | 4900
1.9674 | 79 | 6241 |  | 1.9324 | 79 | 6241
1.9674 | 75 | 5625 |  | 1.9324 | 75 | 5625
1.9684 | 70 | 4900 |  | 1.9332 | 70 | 4900
1.9693 | 77 | 5929 |  | 1.9339 | 77 | 5929
1.9693 | 84 | 7056 |  | 1.9339 | 84 | 7056
1.9702 | 72 | 5184 |  | 1.9346 | 72 | 5184
1.9702 | 78 | 6084 |  | 1.9346 | 78 | 6084
1.9711 | 74 | 5476 |  | 1.9354 | 74 | 5476
1.9711 | 76 | 5776 |  | 1.9354 | 76 | 5776
1.9739 | 73 | 5329 |  | 1.9376 | 73 | 5329
1.9748 | 86 | 7396 |  | 1.9383 | 86 | 7396
1.9758 | 65 | 4225 |  | 1.939 | 65 | 4225
1.9767 | 77 | 5929 |  | 1.9398 | 77 | 5929
1.9776 | 79 | 6241 |  | 1.9405 | 79 | 6241
1.9776 | 79 | 6241 |  | 1.9405 | 79 | 6241
1.9785 | 78 | 6084 |  | 1.9412 | 78 | 6084
1.9795 | 77 | 5929 |  | 1.942 | 77 | 5929
1.9795 | 74 | 5476 |  | 1.942 | 74 | 5476
1.9804 | 73 | 5329 |  | 1.9427 | 73 | 5329
1.9804 | 71 | 5041 |  | 1.9427 | 71 | 5041
1.9804 | 69 | 4761 |  | 1.9427 | 69 | 4761
1.9804 | 68 | 4624 |  | 1.9427 | 68 | 4624
1.9813 | 77 | 5929 |  | 1.9434 | 77 | 5929
1.9813 | 79 | 6241 |  | 1.9434 | 79 | 6241
1.9822 | 66 | 4356 |  | 1.9441 | 66 | 4356
1.9832 | 65 | 4225 |  | 1.9449 | 65 | 4225
1.9832 | 78 | 6084 |  | 1.9449 | 78 | 6084
1.9832 | 70 | 4900 |  | 1.9449 | 70 | 4900
1.9841 | 66 | 4356 |  | 1.9456 | 66 | 4356
1.9841 | 79 | 6241 |  | 1.9456 | 79 | 6241
1.9841 | 70 | 4900 |  | 1.9456 | 70 | 4900
1.9841 | 72 | 5184 |  | 1.9456 | 72 | 5184
1.985 | 67 | 4489 |  | 1.9463 | 67 | 4489
1.985 | 67 | 4489 |  | 1.9463 | 67 | 4489
1.985 | 76 | 5776 |  | 1.9463 | 76 | 5776
1.985 | 76 | 5776 |  | 1.9463 | 76 | 5776
1.985 | 66 | 4356 |  | 1.9463 | 66 | 4356
1.9859 | 75 | 5625 |  | 1.947 | 75 | 5625
1.9859 | 79 | 6241 |  | 1.947 | 79 | 6241
1.9869 | 69 | 4761 |  | 1.9478 | 69 | 4761
1.9869 | 78 | 6084 |  | 1.9478 | 78 | 6084
1.9869 | 73 | 5329 |  | 1.9478 | 73 | 5329
1.9869 | 66 | 4356 |  | 1.9478 | 66 | 4356
1.9878 | 66 | 4356 |  | 1.9485 | 66 | 4356
1.9878 | 72 | 5184 |  | 1.9485 | 72 | 5184
1.9887 | 65 | 4225 |  | 1.9492 | 65 | 4225
1.9887 | 77 | 5929 |  | 1.9492 | 77 | 5929
1.9887 | 74 | 5476 |  | 1.9492 | 74 | 5476
1.9887 | 73 | 5329 |  | 1.9492 | 73 | 5329
1.9887 | 79 | 6241 |  | 1.9492 | 79 | 6241
1.9896 | 72 | 5184 |  | 1.9499 | 72 | 5184
1.9896 | 68 | 4624 |  | 1.9499 | 68 | 4624
1.9906 | 70 | 4900 |  | 1.9507 | 70 | 4900
1.9906 | 67 | 4489 |  | 1.9507 | 67 | 4489
1.9915 | 72 | 5184 |  | 1.9514 | 72 | 5184
1.9915 | 69 | 4761 |  | 1.9514 | 69 | 4761
1.9915 | 74 | 5476 |  | 1.9514 | 74 | 5476
1.9915 | 82 | 6724 |  | 1.9514 | 82 | 6724
1.9915 | 69 | 4761 |  | 1.9514 | 69 | 4761
1.9915 | 72 | 5184 |  | 1.9514 | 72 | 5184
1.9915 | 80 | 6400 |  | 1.9514 | 80 | 6400
1.9915 | 67 | 4489 |  | 1.9514 | 67 | 4489
1.9924 | 68 | 4624 |  | 1.9521 | 68 | 4624
1.9924 | 80 | 6400 |  | 1.9521 | 80 | 6400
1.9933 | 81 | 6561 |  | 1.9528 | 81 | 6561
1.9933 | 69 | 4761 |  | 1.9528 | 69 | 4761
1.9933 | 72 | 5184 |  | 1.9528 | 72 | 5184
1.9933 | 66 | 4356 |  | 1.9528 | 66 | 4356
1.9933 | 68 | 4624 |  | 1.9528 | 68 | 4624
1.9943 | 70 | 4900 |  | 1.9536 | 70 | 4900
1.9943 | 76 | 5776 |  | 1.9536 | 76 | 5776
1.9943 | 68 | 4624 |  | 1.9536 | 68 | 4624
1.9943 | 77 | 5929 |  | 1.9536 | 77 | 5929
1.9952 | 67 | 4489 |  | 1.9543 | 67 | 4489
1.9952 | 69 | 4761 |  | 1.9543 | 69 | 4761
1.9952 | 83 | 6889 |  | 1.9543 | 83 | 6889
1.9952 | 82 | 6724 |  | 1.9543 | 82 | 6724
1.9952 | 72 | 5184 |  | 1.9543 | 72 | 5184
1.9952 | 80 | 6400 |  | 1.9543 | 80 | 6400
1.9952 | 71 | 5041 |  | 1.9543 | 71 | 5041
1.9961 | 69 | 4761 |  | 1.955 | 69 | 4761
1.9961 | 71 | 5041 |  | 1.955 | 71 | 5041
1.9961 | 75 | 5625 |  | 1.955 | 75 | 5625
1.9961 | 83 | 6889 |  | 1.955 | 83 | 6889
1.9961 | 81 | 6561 |  | 1.955 | 81 | 6561
1.9971 | 73 | 5329 |  | 1.9557 | 73 | 5329
1.9971 | 86 | 7396 |  | 1.9557 | 86 | 7396
1.9971 | 73 | 5329 |  | 1.9557 | 73 | 5329
1.9971 | 71 | 5041 |  | 1.9557 | 71 | 5041
1.9971 | 72 | 5184 |  | 1.9557 | 72 | 5184
1.998 | 74 | 5476 |  | 1.9564 | 74 | 5476
1.998 | 66 | 4356 |  | 1.9564 | 66 | 4356
1.998 | 81 | 6561 |  | 1.9564 | 81 | 6561
1.998 | 71 | 5041 |  | 1.9564 | 71 | 5041
1.998 | 71 | 5041 |  | 1.9564 | 71 | 5041
1.998 | 70 | 4900 |  | 1.9564 | 70 | 4900
1.998 | 84 | 7056 |  | 1.9564 | 84 | 7056
1.9989 | 82 | 6724 |  | 1.9571 | 82 | 6724
1.9989 | 73 | 5329 |  | 1.9571 | 73 | 5329
1.9999 | 79 | 6241 |  | 1.9578 | 79 | 6241
1.9999 | 69 | 4761 |  | 1.9578 | 69 | 4761
1.9999 | 78 | 6084 |  | 1.9578 | 78 | 6084
2.0008 | 71 | 5041 |  | 1.9586 | 71 | 5041
2.0017 | 72 | 5184 |  | 1.9593 | 72 | 5184
2.0017 | 71 | 5041 |  | 1.9593 | 71 | 5041
2.0017 | 85 | 7225 |  | 1.9593 | 85 | 7225
2.0027 | 74 | 5476 |  | 1.96 | 74 | 5476
2.0027 | 84 | 7056 |  | 1.96 | 84 | 7056
2.0027 | 83 | 6889 |  | 1.96 | 83 | 6889
2.0027 | 73 | 5329 |  | 1.96 | 73 | 5329
2.0027 | 73 | 5329 |  | 1.96 | 73 | 5329
2.0027 | 82 | 6724 |  | 1.96 | 82 | 6724
2.0036 | 77 | 5929 |  | 1.9607 | 77 | 5929
2.0036 | 78 | 6084 |  | 1.9607 | 78 | 6084
2.0036 | 75 | 5625 |  | 1.9607 | 75 | 5625
2.0036 | 70 | 4900 |  | 1.9607 | 70 | 4900
2.0036 | 73 | 5329 |  | 1.9607 | 73 | 5329
2.0036 | 79 | 6241 |  | 1.9607 | 79 | 6241
2.0045 | 71 | 5041 |  | 1.9614 | 71 | 5041
2.0045 | 74 | 5476 |  | 1.9614 | 74 | 5476
2.0045 | 73 | 5329 |  | 1.9614 | 73 | 5329
2.0055 | 68 | 4624 |  | 1.9621 | 68 | 4624
2.0055 | 68 | 4624 |  | 1.9621 | 68 | 4624
2.0055 | 82 | 6724 |  | 1.9621 | 82 | 6724
2.0055 | 69 | 4761 |  | 1.9621 | 69 | 4761
2.0064 | 82 | 6724 |  | 1.9628 | 82 | 6724
2.0064 | 83 | 6889 |  | 1.9628 | 83 | 6889
2.0064 | 70 | 4900 |  | 1.9628 | 70 | 4900
2.0064 | 75 | 5625 |  | 1.9628 | 75 | 5625
2.0064 | 68 | 4624 |  | 1.9628 | 68 | 4624
2.0073 | 84 | 7056 |  | 1.9636 | 84 | 7056
2.0073 | 77 | 5929 |  | 1.9636 | 77 | 5929
2.0073 | 83 | 6889 |  | 1.9636 | 83 | 6889
2.0073 | 82 | 6724 |  | 1.9636 | 82 | 6724
2.0083 | 74 | 5476 |  | 1.9643 | 74 | 5476
2.0083 | 82 | 6724 |  | 1.9643 | 82 | 6724
2.0092 | 77 | 5929 |  | 1.965 | 77 | 5929
2.0092 | 81 | 6561 |  | 1.965 | 81 | 6561
2.0092 | 79 | 6241 |  | 1.965 | 79 | 6241
2.0092 | 72 | 5184 |  | 1.965 | 72 | 5184
2.0092 | 74 | 5476 |  | 1.965 | 74 | 5476
2.0092 | 84 | 7056 |  | 1.965 | 84 | 7056
2.0092 | 81 | 6561 |  | 1.965 | 81 | 6561
2.0101 | 67 | 4489 |  | 1.9657 | 67 | 4489
2.0101 | 82 | 6724 |  | 1.9657 | 82 | 6724
2.0101 | 68 | 4624 |  | 1.9657 | 68 | 4624
2.0101 | 77 | 5929 |  | 1.9657 | 77 | 5929
2.0101 | 82 | 6724 |  | 1.9657 | 82 | 6724
2.0101 | 74 | 5476 |  | 1.9657 | 74 | 5476
2.011 | 70 | 4900 |  | 1.9664 | 70 | 4900
2.011 | 72 | 5184 |  | 1.9664 | 72 | 5184
2.011 | 66 | 4356 |  | 1.9664 | 66 | 4356
2.012 | 72 | 5184 |  | 1.9671 | 72 | 5184
2.012 | 73 | 5329 |  | 1.9671 | 73 | 5329
2.012 | 79 | 6241 |  | 1.9671 | 79 | 6241
2.012 | 79 | 6241 |  | 1.9671 | 79 | 6241
2.0129 | 68 | 4624 |  | 1.9678 | 68 | 4624
2.0129 | 70 | 4900 |  | 1.9678 | 70 | 4900
2.0138 | 79 | 6241 |  | 1.9685 | 79 | 6241
2.0138 | 70 | 4900 |  | 1.9685 | 70 | 4900
2.0138 | 71 | 5041 |  | 1.9685 | 71 | 5041
2.0138 | 70 | 4900 |  | 1.9685 | 70 | 4900
2.0138 | 73 | 5329 |  | 1.9685 | 73 | 5329
2.0138 | 72 | 5184 |  | 1.9685 | 72 | 5184
2.0147 | 73 | 5329 |  | 1.9692 | 73 | 5329
2.0147 | 73 | 5329 |  | 1.9692 | 73 | 5329
2.0147 | 84 | 7056 |  | 1.9692 | 84 | 7056
2.0147 | 73 | 5329 |  | 1.9692 | 73 | 5329
2.0147 | 81 | 6561 |  | 1.9692 | 81 | 6561
2.0157 | 86 | 7396 |  | 1.97 | 86 | 7396
2.0157 | 80 | 6400 |  | 1.97 | 80 | 6400
2.0157 | 67 | 4489 |  | 1.97 | 67 | 4489
2.0157 | 76 | 5776 |  | 1.97 | 76 | 5776
2.0175 | 84 | 7056 |  | 1.9714 | 84 | 7056
2.0175 | 72 | 5184 |  | 1.9714 | 72 | 5184
2.0175 | 67 | 4489 |  | 1.9714 | 67 | 4489
2.0184 | 86 | 7396 |  | 1.972 | 86 | 7396
2.0184 | 86 | 7396 |  | 1.972 | 86 | 7396
2.0184 | 74 | 5476 |  | 1.972 | 74 | 5476
2.0194 | 70 | 4900 |  | 1.9728 | 70 | 4900
2.0203 | 68 | 4624 |  | 1.9735 | 68 | 4624
2.0203 | 74 | 5476 |  | 1.9735 | 74 | 5476
2.0203 | 66 | 4356 |  | 1.9735 | 66 | 4356
2.0203 | 65 | 4225 |  | 1.9735 | 65 | 4225
2.0203 | 77 | 5929 |  | 1.9735 | 77 | 5929
2.0203 | 72 | 5184 |  | 1.9735 | 72 | 5184
2.0203 | 67 | 4489 |  | 1.9735 | 67 | 4489
2.0212 | 69 | 4761 |  | 1.9742 | 69 | 4761
2.0212 | 73 | 5329 |  | 1.9742 | 73 | 5329
2.0212 | 74 | 5476 |  | 1.9742 | 74 | 5476
2.0212 | 71 | 5041 |  | 1.9742 | 71 | 5041
2.0222 | 77 | 5929 |  | 1.9749 | 77 | 5929
2.0222 | 83 | 6889 |  | 1.9749 | 83 | 6889
2.0222 | 66 | 4356 |  | 1.9749 | 66 | 4356
2.0231 | 71 | 5041 |  | 1.9756 | 71 | 5041
2.024 | 86 | 7396 |  | 1.9763 | 86 | 7396
2.024 | 80 | 6400 |  | 1.9763 | 80 | 6400
2.024 | 72 | 5184 |  | 1.9763 | 72 | 5184
2.024 | 72 | 5184 |  | 1.9763 | 72 | 5184
2.024 | 72 | 5184 |  | 1.9763 | 72 | 5184
2.0249 | 69 | 4761 |  | 1.977 | 69 | 4761
2.0259 | 73 | 5329 |  | 1.9777 | 73 | 5329
2.0259 | 69 | 4761 |  | 1.9777 | 69 | 4761
2.0259 | 75 | 5625 |  | 1.9777 | 75 | 5625
2.0259 | 76 | 5776 |  | 1.9777 | 76 | 5776
2.0268 | 87 | 7569 |  | 1.9784 | 87 | 7569
2.0268 | 69 | 4761 |  | 1.9784 | 69 | 4761
2.0278 | 78 | 6084 |  | 1.9791 | 78 | 6084
2.0278 | 78 | 6084 |  | 1.9791 | 78 | 6084
2.0278 | 67 | 4489 |  | 1.9791 | 67 | 4489
2.0287 | 69 | 4761 |  | 1.9798 | 69 | 4761
2.0287 | 82 | 6724 |  | 1.9798 | 82 | 6724
2.0306 | 69 | 4761 |  | 1.9812 | 69 | 4761
2.0315 | 72 | 5184 |  | 1.9819 | 72 | 5184
2.0324 | 72 | 5184 |  | 1.9826 | 72 | 5184
2.0343 | 82 | 6724 |  | 1.984 | 82 | 6724
2.0352 | 80 | 6400 |  | 1.9847 | 80 | 6400
2.0352 | 71 | 5041 |  | 1.9847 | 71 | 5041
2.0352 | 85 | 7225 |  | 1.9847 | 85 | 7225
2.0361 | 71 | 5041 |  | 1.9853 | 71 | 5041
2.0361 | 76 | 5776 |  | 1.9853 | 76 | 5776
2.0361 | 79 | 6241 |  | 1.9853 | 79 | 6241
2.0371 | 73 | 5329 |  | 1.9861 | 73 | 5329
2.038 | 73 | 5329 |  | 1.9868 | 73 | 5329
2.0389 | 79 | 6241 |  | 1.9874 | 79 | 6241
2.0389 | 79 | 6241 |  | 1.9874 | 79 | 6241
2.0398 | 75 | 5625 |  | 1.9881 | 75 | 5625
2.0408 | 72 | 5184 |  | 1.9888 | 72 | 5184
2.0417 | 70 | 4900 |  | 1.9895 | 70 | 4900
2.0427 | 75 | 5625 |  | 1.9902 | 75 | 5625
2.0427 | 79 | 6241 |  | 1.9902 | 79 | 6241
2.0464 | 79 | 6241 |  | 1.993 | 79 | 6241
2.0464 | 73 | 5329 |  | 1.993 | 73 | 5329
2.0464 | 79 | 6241 |  | 1.993 | 79 | 6241
2.0483 | 84 | 7056 |  | 1.9944 | 84 | 7056
2.0483 | 73 | 5329 |  | 1.9944 | 73 | 5329
2.0492 | 73 | 5329 |  | 1.995 | 73 | 5329
2.0548 | 80 | 6400 |  | 1.9992 | 80 | 6400
2.0557 | 72 | 5184 |  | 1.9998 | 72 | 5184
2.0567 | 77 | 5929 |  | 2.0005 | 77 | 5929
2.0576 | 79 | 6241 |  | 2.0012 | 79 | 6241
2.0595 | 72 | 5184 |  | 2.0025 | 72 | 5184
2.0595 | 74 | 5476 |  | 2.0025 | 74 | 5476
2.0613 | 72 | 5184 |  | 2.0039 | 72 | 5184
2.0613 | 74 | 5476 |  | 2.0039 | 74 | 5476
2.0641 | 69 | 4761 |  | 2.0059 | 69 | 4761
2.0688 | 73 | 5329 |  | 2.0093 | 73 | 5329
2.0847 | 76 | 5776 |  | 2.0207 | 76 | 5776
2.0885 | 77 | 5929 |  | 2.0233 | 77 | 5929
2.0885 | 76 | 5776 |  | 2.0233 | 76 | 5776
2.0988 | 81 | 6561 |  | 2.0306 | 81 | 6561
2.0988 | 79 | 6241 |  | 2.0306 | 79 | 6241
2.0988 | 78 | 6084 |  | 2.0306 | 78 | 6084
2.1016 | 77 | 5929 |  | 2.0326 | 77 | 5929
2.1016 | 78 | 6084 |  | 2.0326 | 78 | 6084
2.1109 | 78 | 6084 |  | 2.039 | 78 | 6084
2.1204 | 79 | 6241 |  | 2.0455 | 79 | 6241
2.1307 | 48 | 2304 |  | 2.0525 | 48 | 2304
2.1467 | 48 | 2304 |  | 2.0632 | 48 | 2304
2.4501 | 50 | 2500 |  | 2.2325 | 50 | 2500
2.7142 | 49 | 2401 |  | 2.3335 | 49 | 2401
2.7152 | 57 | 3249 |  | 2.3338 | 57 | 3249
2.7231 | 78 | 6084 |  | 2.3363 | 78 | 6084
2.7251 | 62 | 3844 |  | 2.3369 | 62 | 3844
2.7281 | 67 | 4489 |  | 2.3378 | 67 | 4489
2.7301 | 50 | 2500 |  | 2.3384 | 50 | 2500
2.7301 | 64 | 4096 |  | 2.3384 | 64 | 4096
2.7301 | 69 | 4761 |  | 2.3384 | 69 | 4761
2.7311 | 64 | 4096 |  | 2.3387 | 64 | 4096
2.7331 | 68 | 4624 |  | 2.3393 | 68 | 4624
2.7351 | 69 | 4761 |  | 2.3399 | 69 | 4761
2.7371 | 64 | 4096 |  | 2.3405 | 64 | 4096
2.7381 | 62 | 3844 |  | 2.3408 | 62 | 3844
2.7391 | 67 | 4489 |  | 2.3411 | 67 | 4489
2.7391 | 69 | 4761 |  | 2.3411 | 69 | 4761
2.7401 | 71 | 5041 |  | 2.3414 | 71 | 5041
2.7411 | 70 | 4900 |  | 2.3417 | 70 | 4900
2.7411 | 66 | 4356 |  | 2.3417 | 66 | 4356
2.7421 | 54 | 2916 |  | 2.342 | 54 | 2916
2.7421 | 72 | 5184 |  | 2.342 | 72 | 5184
2.7431 | 44 | 1936 |  | 2.3423 | 44 | 1936
2.7451 | 64 | 4096 |  | 2.3429 | 64 | 4096
2.7491 | 68 | 4624 |  | 2.3441 | 68 | 4624
2.7491 | 67 | 4489 |  | 2.3441 | 67 | 4489
2.7491 | 69 | 4761 |  | 2.3441 | 69 | 4761
2.7501 | 61 | 3721 |  | 2.3444 | 61 | 3721
2.7511 | 47 | 2209 |  | 2.3447 | 47 | 2209
2.7511 | 73 | 5329 |  | 2.3447 | 73 | 5329
2.7521 | 72 | 5184 |  | 2.345 | 72 | 5184
2.7531 | 70 | 4900 |  | 2.3453 | 70 | 4900
2.7531 | 66 | 4356 |  | 2.3453 | 66 | 4356
2.7541 | 70 | 4900 |  | 2.3456 | 70 | 4900
2.7551 | 71 | 5041 |  | 2.3459 | 71 | 5041
2.7561 | 65 | 4225 |  | 2.3462 | 65 | 4225
2.7561 | 71 | 5041 |  | 2.3462 | 71 | 5041
2.7561 | 66 | 4356 |  | 2.3462 | 66 | 4356
2.7571 | 77 | 5929 |  | 2.3465 | 77 | 5929
2.7571 | 61 | 3721 |  | 2.3465 | 61 | 3721
2.7571 | 68 | 4624 |  | 2.3465 | 68 | 4624
2.7581 | 67 | 4489 |  | 2.3468 | 67 | 4489
2.7581 | 69 | 4761 |  | 2.3468 | 69 | 4761
2.7601 | 52 | 2704 |  | 2.3474 | 52 | 2704
2.7601 | 70 | 4900 |  | 2.3474 | 70 | 4900
2.7601 | 70 | 4900 |  | 2.3474 | 70 | 4900
2.7611 | 72 | 5184 |  | 2.3477 | 72 | 5184
2.7611 | 71 | 5041 |  | 2.3477 | 71 | 5041
2.7611 | 70 | 4900 |  | 2.3477 | 70 | 4900
2.7611 | 69 | 4761 |  | 2.3477 | 69 | 4761
2.7611 | 69 | 4761 |  | 2.3477 | 69 | 4761
2.7621 | 66 | 4356 |  | 2.348 | 66 | 4356
2.7621 | 62 | 3844 |  | 2.348 | 62 | 3844
2.7631 | 64 | 4096 |  | 2.3483 | 64 | 4096
2.7641 | 71 | 5041 |  | 2.3485 | 71 | 5041
2.7651 | 82 | 6724 |  | 2.3488 | 82 | 6724
2.7651 | 62 | 3844 |  | 2.3488 | 62 | 3844
2.7651 | 66 | 4356 |  | 2.3488 | 66 | 4356
2.7661 | 55 | 3025 |  | 2.3491 | 55 | 3025
2.7661 | 66 | 4356 |  | 2.3491 | 66 | 4356
2.7671 | 67 | 4489 |  | 2.3494 | 67 | 4489
2.7671 | 69 | 4761 |  | 2.3494 | 69 | 4761
2.7671 | 67 | 4489 |  | 2.3494 | 67 | 4489
2.7681 | 69 | 4761 |  | 2.3497 | 69 | 4761
2.7691 | 73 | 5329 |  | 2.35 | 73 | 5329
2.7701 | 70 | 4900 |  | 2.3503 | 70 | 4900
2.7701 | 78 | 6084 |  | 2.3503 | 78 | 6084
2.7701 | 71 | 5041 |  | 2.3503 | 71 | 5041
2.7701 | 58 | 3364 |  | 2.3503 | 58 | 3364
2.7711 | 78 | 6084 |  | 2.3506 | 78 | 6084
2.7711 | 71 | 5041 |  | 2.3506 | 71 | 5041
2.7711 | 67 | 4489 |  | 2.3506 | 67 | 4489
2.7722 | 72 | 5184 |  | 2.3509 | 72 | 5184
2.7731 | 77 | 5929 |  | 2.3512 | 77 | 5929
2.7731 | 67 | 4489 |  | 2.3512 | 67 | 4489
2.7731 | 60 | 3600 |  | 2.3512 | 60 | 3600
2.7731 | 71 | 5041 |  | 2.3512 | 71 | 5041
2.7731 | 65 | 4225 |  | 2.3512 | 65 | 4225
2.7731 | 65 | 4225 |  | 2.3512 | 65 | 4225
2.7741 | 69 | 4761 |  | 2.3514 | 69 | 4761
2.7741 | 70 | 4900 |  | 2.3514 | 70 | 4900
2.7751 | 42 | 1764 |  | 2.3517 | 42 | 1764
2.7751 | 66 | 4356 |  | 2.3517 | 66 | 4356
2.7751 | 73 | 5329 |  | 2.3517 | 73 | 5329
2.7751 | 72 | 5184 |  | 2.3517 | 72 | 5184
2.7751 | 63 | 3969 |  | 2.3517 | 63 | 3969
2.7762 | 71 | 5041 |  | 2.352 | 71 | 5041
2.7762 | 67 | 4489 |  | 2.352 | 67 | 4489
2.7762 | 69 | 4761 |  | 2.352 | 69 | 4761
2.7781 | 67 | 4489 |  | 2.3526 | 67 | 4489
2.7791 | 69 | 4761 |  | 2.3529 | 69 | 4761
2.7791 | 72 | 5184 |  | 2.3529 | 72 | 5184
2.7791 | 69 | 4761 |  | 2.3529 | 69 | 4761
2.7791 | 73 | 5329 |  | 2.3529 | 73 | 5329
2.7802 | 65 | 4225 |  | 2.3532 | 65 | 4225
2.7802 | 66 | 4356 |  | 2.3532 | 66 | 4356
2.7802 | 72 | 5184 |  | 2.3532 | 72 | 5184
2.7812 | 74 | 5476 |  | 2.3534 | 74 | 5476
2.7812 | 73 | 5329 |  | 2.3534 | 73 | 5329
2.7812 | 67 | 4489 |  | 2.3534 | 67 | 4489
2.7821 | 68 | 4624 |  | 2.3537 | 68 | 4624
2.7821 | 70 | 4900 |  | 2.3537 | 70 | 4900
2.7831 | 65 | 4225 |  | 2.354 | 65 | 4225
2.7831 | 63 | 3969 |  | 2.354 | 63 | 3969
2.7831 | 71 | 5041 |  | 2.354 | 71 | 5041
2.7842 | 70 | 4900 |  | 2.3543 | 70 | 4900
2.7842 | 60 | 3600 |  | 2.3543 | 60 | 3600
2.7842 | 66 | 4356 |  | 2.3543 | 66 | 4356
2.7842 | 71 | 5041 |  | 2.3543 | 71 | 5041
2.7842 | 69 | 4761 |  | 2.3543 | 69 | 4761
2.7852 | 63 | 3969 |  | 2.3546 | 63 | 3969
2.7852 | 72 | 5184 |  | 2.3546 | 72 | 5184
2.7871 | 42 | 1764 |  | 2.3551 | 42 | 1764
2.7871 | 63 | 3969 |  | 2.3551 | 63 | 3969
2.7871 | 60 | 3600 |  | 2.3551 | 60 | 3600
2.7882 | 69 | 4761 |  | 2.3554 | 69 | 4761
2.7892 | 61 | 3721 |  | 2.3557 | 61 | 3721
2.7892 | 67 | 4489 |  | 2.3557 | 67 | 4489
2.7902 | 63 | 3969 |  | 2.356 | 63 | 3969
2.7902 | 68 | 4624 |  | 2.356 | 68 | 4624
2.7912 | 62 | 3844 |  | 2.3562 | 62 | 3844
2.7912 | 73 | 5329 |  | 2.3562 | 73 | 5329
2.7922 | 80 | 6400 |  | 2.3565 | 80 | 6400
2.7922 | 62 | 3844 |  | 2.3565 | 62 | 3844
2.7932 | 70 | 4900 |  | 2.3568 | 70 | 4900
2.7942 | 64 | 4096 |  | 2.3571 | 64 | 4096
2.7942 | 71 | 5041 |  | 2.3571 | 71 | 5041
2.7952 | 72 | 5184 |  | 2.3574 | 72 | 5184
2.7952 | 68 | 4624 |  | 2.3574 | 68 | 4624
2.7962 | 66 | 4356 |  | 2.3577 | 66 | 4356
2.7962 | 76 | 5776 |  | 2.3577 | 76 | 5776
2.7972 | 46 | 2116 |  | 2.3579 | 46 | 2116
2.7972 | 63 | 3969 |  | 2.3579 | 63 | 3969
2.7972 | 76 | 5776 |  | 2.3579 | 76 | 5776
2.7972 | 66 | 4356 |  | 2.3579 | 66 | 4356
2.7972 | 65 | 4225 |  | 2.3579 | 65 | 4225
2.7982 | 69 | 4761 |  | 2.3582 | 69 | 4761
2.7992 | 61 | 3721 |  | 2.3585 | 61 | 3721
2.7992 | 72 | 5184 |  | 2.3585 | 72 | 5184
2.7992 | 65 | 4225 |  | 2.3585 | 65 | 4225
2.7992 | 57 | 3249 |  | 2.3585 | 57 | 3249
2.7992 | 68 | 4624 |  | 2.3585 | 68 | 4624
2.8002 | 66 | 4356 |  | 2.3588 | 66 | 4356
2.8002 | 56 | 3136 |  | 2.3588 | 56 | 3136
2.8002 | 70 | 4900 |  | 2.3588 | 70 | 4900
2.8002 | 69 | 4761 |  | 2.3588 | 69 | 4761
2.8012 | 60 | 3600 |  | 2.359 | 60 | 3600
2.8012 | 67 | 4489 |  | 2.359 | 67 | 4489
2.8012 | 69 | 4761 |  | 2.359 | 69 | 4761
2.8022 | 78 | 6084 |  | 2.3593 | 78 | 6084
2.8033 | 69 | 4761 |  | 2.3596 | 69 | 4761
2.8033 | 59 | 3481 |  | 2.3596 | 59 | 3481
2.8033 | 59 | 3481 |  | 2.3596 | 59 | 3481
2.8033 | 64 | 4096 |  | 2.3596 | 64 | 4096
2.8033 | 67 | 4489 |  | 2.3596 | 67 | 4489
2.8042 | 41 | 1681 |  | 2.3599 | 41 | 1681
2.8042 | 79 | 6241 |  | 2.3599 | 79 | 6241
2.8042 | 74 | 5476 |  | 2.3599 | 74 | 5476
2.8042 | 63 | 3969 |  | 2.3599 | 63 | 3969
2.8042 | 68 | 4624 |  | 2.3599 | 68 | 4624
2.8042 | 74 | 5476 |  | 2.3599 | 74 | 5476
2.8042 | 68 | 4624 |  | 2.3599 | 68 | 4624
2.8052 | 72 | 5184 |  | 2.3601 | 72 | 5184
2.8052 | 69 | 4761 |  | 2.3601 | 69 | 4761
2.8062 | 70 | 4900 |  | 2.3604 | 70 | 4900
2.8062 | 71 | 5041 |  | 2.3604 | 71 | 5041
2.8062 | 70 | 4900 |  | 2.3604 | 70 | 4900
2.8073 | 72 | 5184 |  | 2.3607 | 72 | 5184
2.8073 | 66 | 4356 |  | 2.3607 | 66 | 4356
2.8073 | 69 | 4761 |  | 2.3607 | 69 | 4761
2.8073 | 72 | 5184 |  | 2.3607 | 72 | 5184
2.8073 | 73 | 5329 |  | 2.3607 | 73 | 5329
2.8083 | 71 | 5041 |  | 2.361 | 71 | 5041
2.8083 | 65 | 4225 |  | 2.361 | 65 | 4225
2.8083 | 68 | 4624 |  | 2.361 | 68 | 4624
2.8093 | 76 | 5776 |  | 2.3612 | 76 | 5776
2.8093 | 68 | 4624 |  | 2.3612 | 68 | 4624
2.8102 | 74 | 5476 |  | 2.3615 | 74 | 5476
2.8102 | 62 | 3844 |  | 2.3615 | 62 | 3844
2.8102 | 68 | 4624 |  | 2.3615 | 68 | 4624
2.8113 | 82 | 6724 |  | 2.3618 | 82 | 6724
2.8113 | 63 | 3969 |  | 2.3618 | 63 | 3969
2.8113 | 71 | 5041 |  | 2.3618 | 71 | 5041
2.8123 | 46 | 2116 |  | 2.362 | 46 | 2116
2.8123 | 64 | 4096 |  | 2.362 | 64 | 4096
2.8123 | 69 | 4761 |  | 2.362 | 69 | 4761
2.8133 | 61 | 3721 |  | 2.3623 | 61 | 3721
2.8133 | 61 | 3721 |  | 2.3623 | 61 | 3721
2.8133 | 67 | 4489 |  | 2.3623 | 67 | 4489
2.8133 | 79 | 6241 |  | 2.3623 | 79 | 6241
2.8133 | 68 | 4624 |  | 2.3623 | 68 | 4624
2.8133 | 68 | 4624 |  | 2.3623 | 68 | 4624
2.8143 | 67 | 4489 |  | 2.3626 | 67 | 4489
2.8143 | 63 | 3969 |  | 2.3626 | 63 | 3969
2.8143 | 63 | 3969 |  | 2.3626 | 63 | 3969
2.8153 | 69 | 4761 |  | 2.3629 | 69 | 4761
2.8153 | 64 | 4096 |  | 2.3629 | 64 | 4096
2.8163 | 76 | 5776 |  | 2.3631 | 76 | 5776
2.8163 | 71 | 5041 |  | 2.3631 | 71 | 5041
2.8173 | 69 | 4761 |  | 2.3634 | 69 | 4761
2.8173 | 72 | 5184 |  | 2.3634 | 72 | 5184
2.8173 | 71 | 5041 |  | 2.3634 | 71 | 5041
2.8173 | 69 | 4761 |  | 2.3634 | 69 | 4761
2.8183 | 65 | 4225 |  | 2.3637 | 65 | 4225
2.8183 | 73 | 5329 |  | 2.3637 | 73 | 5329
2.8193 | 70 | 4900 |  | 2.3639 | 70 | 4900
2.8193 | 64 | 4096 |  | 2.3639 | 64 | 4096
2.8203 | 60 | 3600 |  | 2.3642 | 60 | 3600
2.8203 | 64 | 4096 |  | 2.3642 | 64 | 4096
2.8203 | 72 | 5184 |  | 2.3642 | 72 | 5184
2.8203 | 69 | 4761 |  | 2.3642 | 69 | 4761
2.8213 | 65 | 4225 |  | 2.3645 | 65 | 4225
2.8213 | 70 | 4900 |  | 2.3645 | 70 | 4900
2.8223 | 62 | 3844 |  | 2.3647 | 62 | 3844
2.8223 | 65 | 4225 |  | 2.3647 | 65 | 4225
2.8223 | 60 | 3600 |  | 2.3647 | 60 | 3600
2.8234 | 63 | 3969 |  | 2.365 | 63 | 3969
2.8234 | 70 | 4900 |  | 2.365 | 70 | 4900
2.8234 | 67 | 4489 |  | 2.365 | 67 | 4489
2.8243 | 69 | 4761 |  | 2.3653 | 69 | 4761
2.8243 | 62 | 3844 |  | 2.3653 | 62 | 3844
2.8243 | 68 | 4624 |  | 2.3653 | 68 | 4624
2.8253 | 68 | 4624 |  | 2.3655 | 68 | 4624
2.8264 | 74 | 5476 |  | 2.3658 | 74 | 5476
2.8264 | 70 | 4900 |  | 2.3658 | 70 | 4900
2.8264 | 68 | 4624 |  | 2.3658 | 68 | 4624
2.8274 | 63 | 3969 |  | 2.3661 | 63 | 3969
2.8274 | 61 | 3721 |  | 2.3661 | 61 | 3721
2.8284 | 63 | 3969 |  | 2.3663 | 63 | 3969
2.8284 | 68 | 4624 |  | 2.3663 | 68 | 4624
2.8284 | 69 | 4761 |  | 2.3663 | 69 | 4761
2.8294 | 66 | 4356 |  | 2.3666 | 66 | 4356
2.8304 | 44 | 1936 |  | 2.3669 | 44 | 1936
2.8304 | 65 | 4225 |  | 2.3669 | 65 | 4225
2.8304 | 62 | 3844 |  | 2.3669 | 62 | 3844
2.8304 | 59 | 3481 |  | 2.3669 | 59 | 3481
2.8304 | 65 | 4225 |  | 2.3669 | 65 | 4225
2.8304 | 67 | 4489 |  | 2.3669 | 67 | 4489
2.8304 | 69 | 4761 |  | 2.3669 | 69 | 4761
2.8314 | 61 | 3721 |  | 2.3671 | 61 | 3721
2.8314 | 62 | 3844 |  | 2.3671 | 62 | 3844
2.8324 | 67 | 4489 |  | 2.3674 | 67 | 4489
2.8354 | 61 | 3721 |  | 2.3682 | 61 | 3721
2.8354 | 60 | 3600 |  | 2.3682 | 60 | 3600
2.8364 | 63 | 3969 |  | 2.3685 | 63 | 3969
2.8364 | 59 | 3481 |  | 2.3685 | 59 | 3481
2.8364 | 70 | 4900 |  | 2.3685 | 70 | 4900
2.8374 | 72 | 5184 |  | 2.3687 | 72 | 5184
2.8404 | 70 | 4900 |  | 2.3695 | 70 | 4900
2.8414 | 69 | 4761 |  | 2.3698 | 69 | 4761
2.8425 | 69 | 4761 |  | 2.37 | 69 | 4761
2.8435 | 63 | 3969 |  | 2.3703 | 63 | 3969
2.8435 | 69 | 4761 |  | 2.3703 | 69 | 4761
2.8445 | 71 | 5041 |  | 2.3705 | 71 | 5041
2.8445 | 66 | 4356 |  | 2.3705 | 66 | 4356
2.8445 | 66 | 4356 |  | 2.3705 | 66 | 4356
2.8445 | 68 | 4624 |  | 2.3705 | 68 | 4624
2.8455 | 67 | 4489 |  | 2.3708 | 67 | 4489
2.8475 | 75 | 5625 |  | 2.3713 | 75 | 5625
2.8475 | 64 | 4096 |  | 2.3713 | 64 | 4096
2.8475 | 65 | 4225 |  | 2.3713 | 65 | 4225
2.8485 | 64 | 4096 |  | 2.3716 | 64 | 4096
2.8495 | 60 | 3600 |  | 2.3718 | 60 | 3600
2.8506 | 71 | 5041 |  | 2.3721 | 71 | 5041
2.8506 | 59 | 3481 |  | 2.3721 | 59 | 3481
2.8506 | 75 | 5625 |  | 2.3721 | 75 | 5625
2.8506 | 68 | 4624 |  | 2.3721 | 68 | 4624
2.8515 | 55 | 3025 |  | 2.3723 | 55 | 3025
2.8515 | 67 | 4489 |  | 2.3723 | 67 | 4489
2.8536 | 59 | 3481 |  | 2.3729 | 59 | 3481
2.8536 | 67 | 4489 |  | 2.3729 | 67 | 4489
2.8536 | 76 | 5776 |  | 2.3729 | 76 | 5776
2.8536 | 67 | 4489 |  | 2.3729 | 67 | 4489
2.8536 | 69 | 4761 |  | 2.3729 | 69 | 4761
2.8556 | 67 | 4489 |  | 2.3734 | 67 | 4489
2.8566 | 79 | 6241 |  | 2.3736 | 79 | 6241
2.8566 | 71 | 5041 |  | 2.3736 | 71 | 5041
2.8576 | 70 | 4900 |  | 2.3739 | 70 | 4900
2.8586 | 74 | 5476 |  | 2.3741 | 74 | 5476
2.8586 | 65 | 4225 |  | 2.3741 | 65 | 4225
2.8586 | 69 | 4761 |  | 2.3741 | 69 | 4761
2.8586 | 67 | 4489 |  | 2.3741 | 67 | 4489
2.8596 | 59 | 3481 |  | 2.3744 | 59 | 3481
2.8596 | 66 | 4356 |  | 2.3744 | 66 | 4356
2.8606 | 42 | 1764 |  | 2.3746 | 42 | 1764
2.8606 | 56 | 3136 |  | 2.3746 | 56 | 3136
2.8606 | 54 | 2916 |  | 2.3746 | 54 | 2916
2.8606 | 60 | 3600 |  | 2.3746 | 60 | 3600
2.8606 | 63 | 3969 |  | 2.3746 | 63 | 3969
2.8617 | 65 | 4225 |  | 2.3749 | 65 | 4225
2.8617 | 67 | 4489 |  | 2.3749 | 67 | 4489
2.8617 | 69 | 4761 |  | 2.3749 | 69 | 4761
2.8617 | 69 | 4761 |  | 2.3749 | 69 | 4761
2.8636 | 43 | 1849 |  | 2.3754 | 43 | 1849
2.8646 | 66 | 4356 |  | 2.3756 | 66 | 4356
2.8657 | 64 | 4096 |  | 2.3759 | 64 | 4096
2.8657 | 86 | 7396 |  | 2.3759 | 86 | 7396
2.8667 | 57 | 3249 |  | 2.3762 | 57 | 3249
2.8667 | 61 | 3721 |  | 2.3762 | 61 | 3721
2.8667 | 59 | 3481 |  | 2.3762 | 59 | 3481
2.8677 | 48 | 2304 |  | 2.3764 | 48 | 2304
2.8677 | 78 | 6084 |  | 2.3764 | 78 | 6084
2.8677 | 76 | 5776 |  | 2.3764 | 76 | 5776
2.8687 | 60 | 3600 |  | 2.3766 | 60 | 3600
2.8687 | 67 | 4489 |  | 2.3766 | 67 | 4489
2.8697 | 72 | 5184 |  | 2.3769 | 72 | 5184
2.8707 | 60 | 3600 |  | 2.3772 | 60 | 3600
2.8717 | 77 | 5929 |  | 2.3774 | 77 | 5929
2.8717 | 64 | 4096 |  | 2.3774 | 64 | 4096
2.8717 | 67 | 4489 |  | 2.3774 | 67 | 4489
2.8727 | 60 | 3600 |  | 2.3776 | 60 | 3600
2.8738 | 63 | 3969 |  | 2.3779 | 63 | 3969
2.8738 | 62 | 3844 |  | 2.3779 | 62 | 3844
2.8748 | 63 | 3969 |  | 2.3781 | 63 | 3969
2.8767 | 77 | 5929 |  | 2.3786 | 77 | 5929
2.8767 | 71 | 5041 |  | 2.3786 | 71 | 5041
2.8767 | 67 | 4489 |  | 2.3786 | 67 | 4489
2.8778 | 64 | 4096 |  | 2.3789 | 64 | 4096
2.8798 | 77 | 5929 |  | 2.3794 | 77 | 5929
2.8818 | 64 | 4096 |  | 2.3799 | 64 | 4096
2.8828 | 77 | 5929 |  | 2.3801 | 77 | 5929
2.8828 | 67 | 4489 |  | 2.3801 | 67 | 4489
2.8838 | 74 | 5476 |  | 2.3804 | 74 | 5476
2.8838 | 77 | 5929 |  | 2.3804 | 77 | 5929
2.8859 | 62 | 3844 |  | 2.3809 | 62 | 3844
2.8859 | 63 | 3969 |  | 2.3809 | 63 | 3969
2.8879 | 82 | 6724 |  | 2.3813 | 82 | 6724
2.8889 | 58 | 3364 |  | 2.3816 | 58 | 3364
2.8889 | 71 | 5041 |  | 2.3816 | 71 | 5041
2.8899 | 56 | 3136 |  | 2.3818 | 56 | 3136
2.8909 | 73 | 5329 |  | 2.3821 | 73 | 5329
2.8909 | 64 | 4096 |  | 2.3821 | 64 | 4096
2.893 | 72 | 5184 |  | 2.3826 | 72 | 5184
2.894 | 63 | 3969 |  | 2.3828 | 63 | 3969
2.894 | 63 | 3969 |  | 2.3828 | 63 | 3969
2.895 | 72 | 5184 |  | 2.383 | 72 | 5184
2.896 | 41 | 1681 |  | 2.3833 | 41 | 1681
2.897 | 60 | 3600 |  | 2.3835 | 60 | 3600
2.898 | 62 | 3844 |  | 2.3838 | 62 | 3844
2.898 | 63 | 3969 |  | 2.3838 | 63 | 3969
2.898 | 61 | 3721 |  | 2.3838 | 61 | 3721
2.899 | 55 | 3025 |  | 2.384 | 55 | 3025
2.9021 | 54 | 2916 |  | 2.3847 | 54 | 2916
2.9021 | 74 | 5476 |  | 2.3847 | 74 | 5476
2.9021 | 70 | 4900 |  | 2.3847 | 70 | 4900
2.9031 | 77 | 5929 |  | 2.3849 | 77 | 5929
2.904 | 63 | 3969 |  | 2.3852 | 63 | 3969
2.904 | 63 | 3969 |  | 2.3852 | 63 | 3969
2.9061 | 61 | 3721 |  | 2.3857 | 61 | 3721
2.9081 | 41 | 1681 |  | 2.3861 | 41 | 1681
2.9081 | 65 | 4225 |  | 2.3861 | 65 | 4225
2.9142 | 64 | 4096 |  | 2.3875 | 64 | 4096
2.9142 | 62 | 3844 |  | 2.3875 | 62 | 3844
2.9183 | 75 | 5625 |  | 2.3885 | 75 | 5625
2.9233 | 63 | 3969 |  | 2.3896 | 63 | 3969
2.9244 | 62 | 3844 |  | 2.3899 | 62 | 3844
2.9244 | 62 | 3844 |  | 2.3899 | 62 | 3844
2.9284 | 53 | 2809 |  | 2.3908 | 53 | 2809
2.9314 | 63 | 3969 |  | 2.3915 | 63 | 3969
2.9325 | 62 | 3844 |  | 2.3917 | 62 | 3844
2.9325 | 60 | 3600 |  | 2.3917 | 60 | 3600
2.9365 | 54 | 2916 |  | 2.3926 | 54 | 2916
2.9456 | 62 | 3844 |  | 2.3946 | 62 | 3844
2.9487 | 69 | 4761 |  | 2.3953 | 69 | 4761
2.9518 | 54 | 2916 |  | 2.396 | 54 | 2916
2.9518 | 62 | 3844 |  | 2.396 | 62 | 3844
2.9528 | 41 | 1681 |  | 2.3962 | 41 | 1681
2.9609 | 41 | 1681 |  | 2.398 | 41 | 1681
2.9609 | 63 | 3969 |  | 2.398 | 63 | 3969
2.9649 | 62 | 3844 |  | 2.3988 | 62 | 3844
2.97 | 59 | 3481 |  | 2.3999 | 59 | 3481
2.97 | 53 | 2809 |  | 2.3999 | 53 | 2809
2.9721 | 58 | 3364 |  | 2.4004 | 58 | 3364
2.9731 | 62 | 3844 |  | 2.4006 | 62 | 3844
2.9741 | 56 | 3136 |  | 2.4008 | 56 | 3136
2.9822 | 63 | 3969 |  | 2.4025 | 63 | 3969
2.9975 | 63 | 3969 |  | 2.4056 | 63 | 3969
3.0046 | 41 | 1681 |  | 2.4071 | 41 | 1681
3.0138 | 54 | 2916 |  | 2.4089 | 54 | 2916
3.0169 | 54 | 2916 |  | 2.4095 | 54 | 2916
3.025 | 55 | 3025 |  | 2.4112 | 55 | 3025
3.0261 | 52 | 2704 |  | 2.4114 | 52 | 2704
3.0373 | 53 | 2809 |  | 2.4135 | 53 | 2809
3.0444 | 54 | 2916 |  | 2.4149 | 54 | 2916
3.0516 | 55 | 3025 |  | 2.4163 | 55 | 3025
3.067 | 53 | 2809 |  | 2.4191 | 53 | 2809
3.2035 | 59 | 3481 |  | 2.4421 | 59 | 3481
3.3306 | 65 | 4225 |  | 2.4605 | 65 | 4225
3.3929 | 71 | 5041 |  | 2.4688 | 71 | 5041
3.4573 | 46 | 2116 |  | 2.4771 | 46 | 2116
3.4614 | 46 | 2116 |  | 2.4776 | 46 | 2116
3.4687 | 46 | 2116 |  | 2.4786 | 46 | 2116
3.4687 | 48 | 2304 |  | 2.4786 | 48 | 2304
3.4759 | 44 | 1936 |  | 2.4795 | 44 | 1936
3.4843 | 44 | 1936 |  | 2.4806 | 44 | 1936
3.4915 | 42 | 1764 |  | 2.4815 | 42 | 1764
3.4937 | 46 | 2116 |  | 2.4817 | 46 | 2116
3.4999 | 49 | 2401 |  | 2.4825 | 49 | 2401
3.5113 | 47 | 2209 |  | 2.484 | 47 | 2209
3.5228 | 46 | 2116 |  | 2.4854 | 46 | 2116
3.5291 | 45 | 2025 |  | 2.4862 | 45 | 2025
3.5394 | 69 | 4761 |  | 2.4875 | 69 | 4761
3.5467 | 73 | 5329 |  | 2.4884 | 73 | 5329
3.5489 | 70 | 4900 |  | 2.4887 | 70 | 4900
3.5499 | 79 | 6241 |  | 2.4888 | 79 | 6241
3.554 | 77 | 5929 |  | 2.4894 | 77 | 5929
3.5592 | 73 | 5329 |  | 2.49 | 73 | 5329
3.5676 | 75 | 5625 |  | 2.4911 | 75 | 5625
3.5811 | 68 | 4624 |  | 2.4928 | 68 | 4624
3.5947 | 76 | 5776 |  | 2.4945 | 76 | 5776
3.6113 | 74 | 5476 |  | 2.4967 | 74 | 5476
3.6363 | 76 | 5776 |  | 2.4999 | 76 | 5776
3.925 | 50 | 2500 |  | 2.5429 | 50 | 2500
3.9582 | 66 | 4356 |  | 2.5489 | 66 | 4356
4.2602 | 72 | 5184 |  | 2.6201 | 72 | 5184
4.3605 | 41 | 1681 |  | 2.6526 | 41 | 1681
4.4663 | 64 | 4096 |  | 2.6934 | 64 | 4096
4.4683 | 78 | 6084 |  | 2.6942 | 78 | 6084
4.5088 | 63 | 3969 |  | 2.7119 | 63 | 3969
4.5088 | 59 | 3481 |  | 2.7119 | 59 | 3481
4.5098 | 59 | 3481 |  | 2.7123 | 59 | 3481
4.5128 | 60 | 3600 |  | 2.7137 | 60 | 3600
4.5149 | 62 | 3844 |  | 2.7146 | 62 | 3844
4.5601 | 60 | 3600 |  | 2.736 | 60 | 3600
4.5662 | 60 | 3600 |  | 2.739 | 60 | 3600
4.5692 | 63 | 3969 |  | 2.7405 | 63 | 3969
4.5732 | 68 | 4624 |  | 2.7425 | 68 | 4624
4.5783 | 66 | 4356 |  | 2.745 | 66 | 4356
4.5783 | 70 | 4900 |  | 2.745 | 70 | 4900
4.5813 | 68 | 4624 |  | 2.7465 | 68 | 4624
4.6053 | 49 | 2401 |  | 2.759 | 49 | 2401
4.6093 | 52 | 2704 |  | 2.7611 | 52 | 2704
4.6093 | 59 | 3481 |  | 2.7611 | 59 | 3481
4.6114 | 62 | 3844 |  | 2.7622 | 62 | 3844
4.6133 | 28 | 784 |  | 2.7632 | 28 | 784
4.6163 | 30 | 900 |  | 2.7648 | 30 | 900
4.6224 | 52 | 2704 |  | 2.7681 | 52 | 2704
4.6253 | 26 | 676 |  | 2.7697 | 26 | 676
4.6283 | 27 | 729 |  | 2.7713 | 27 | 729
4.6293 | 60 | 3600 |  | 2.7719 | 60 | 3600
4.6453 | 52 | 2704 |  | 2.7808 | 52 | 2704
4.6473 | 48 | 2304 |  | 2.7819 | 48 | 2304
4.6523 | 66 | 4356 |  | 2.7847 | 66 | 4356
4.6533 | 51 | 2601 |  | 2.7853 | 51 | 2601
4.6543 | 49 | 2401 |  | 2.7859 | 49 | 2401
4.6543 | 53 | 2809 |  | 2.7859 | 53 | 2809
4.6553 | 55 | 3025 |  | 2.7864 | 55 | 3025
4.6583 | 25 | 625 |  | 2.7882 | 25 | 625
4.6593 | 58 | 3364 |  | 2.7887 | 58 | 3364
4.6602 | 59 | 3481 |  | 2.7893 | 59 | 3481
4.6623 | 51 | 2601 |  | 2.7905 | 51 | 2601
4.6632 | 53 | 2809 |  | 2.791 | 53 | 2809
4.6662 | 53 | 2809 |  | 2.7928 | 53 | 2809
4.6662 | 56 | 3136 |  | 2.7928 | 56 | 3136
4.6692 | 54 | 2916 |  | 2.7945 | 54 | 2916
4.6722 | 53 | 2809 |  | 2.7963 | 53 | 2809
4.6742 | 69 | 4761 |  | 2.7974 | 69 | 4761
4.6752 | 73 | 5329 |  | 2.798 | 73 | 5329
4.6782 | 66 | 4356 |  | 2.7998 | 66 | 4356
4.6792 | 59 | 3481 |  | 2.8004 | 59 | 3481
4.6812 | 57 | 3249 |  | 2.8016 | 57 | 3249
4.6831 | 54 | 2916 |  | 2.8028 | 54 | 2916
4.6842 | 54 | 2916 |  | 2.8034 | 54 | 2916
4.6861 | 48 | 2304 |  | 2.8046 | 48 | 2304
4.6861 | 71 | 5041 |  | 2.8046 | 71 | 5041
4.6871 | 51 | 2601 |  | 2.8051 | 51 | 2601
4.6871 | 57 | 3249 |  | 2.8051 | 57 | 3249
4.6871 | 62 | 3844 |  | 2.8051 | 62 | 3844
4.6881 | 24 | 576 |  | 2.8058 | 24 | 576
4.6891 | 46 | 2116 |  | 2.8064 | 46 | 2116
4.6891 | 56 | 3136 |  | 2.8064 | 56 | 3136
4.6901 | 54 | 2916 |  | 2.807 | 54 | 2916
4.6921 | 41 | 1681 |  | 2.8082 | 41 | 1681
4.6921 | 64 | 4096 |  | 2.8082 | 64 | 4096
4.6931 | 59 | 3481 |  | 2.8088 | 59 | 3481
4.695 | 71 | 5041 |  | 2.81 | 71 | 5041
4.695 | 64 | 4096 |  | 2.81 | 64 | 4096
4.695 | 66 | 4356 |  | 2.81 | 66 | 4356
4.6961 | 61 | 3721 |  | 2.8106 | 61 | 3721
4.6971 | 56 | 3136 |  | 2.8112 | 56 | 3136
4.698 | 47 | 2209 |  | 2.8118 | 47 | 2209
4.698 | 52 | 2704 |  | 2.8118 | 52 | 2704
4.7001 | 53 | 2809 |  | 2.813 | 53 | 2809
4.702 | 51 | 2601 |  | 2.8142 | 51 | 2601
4.704 | 48 | 2304 |  | 2.8155 | 48 | 2304
4.704 | 58 | 3364 |  | 2.8155 | 58 | 3364
4.706 | 45 | 2025 |  | 2.8167 | 45 | 2025
4.707 | 41 | 1681 |  | 2.8173 | 41 | 1681
4.711 | 58 | 3364 |  | 2.8198 | 58 | 3364
4.7119 | 46 | 2116 |  | 2.8204 | 46 | 2116
4.7119 | 53 | 2809 |  | 2.8204 | 53 | 2809
4.7159 | 72 | 5184 |  | 2.8229 | 72 | 5184
4.7169 | 51 | 2601 |  | 2.8235 | 51 | 2601
4.7169 | 55 | 3025 |  | 2.8235 | 55 | 3025
4.7189 | 61 | 3721 |  | 2.8248 | 61 | 3721
4.7208 | 53 | 2809 |  | 2.826 | 53 | 2809
4.7218 | 55 | 3025 |  | 2.8267 | 55 | 3025
4.7238 | 42 | 1764 |  | 2.828 | 42 | 1764
4.7238 | 56 | 3136 |  | 2.828 | 56 | 3136
4.7238 | 51 | 2601 |  | 2.828 | 51 | 2601
4.7238 | 52 | 2704 |  | 2.828 | 52 | 2704
4.7238 | 61 | 3721 |  | 2.828 | 61 | 3721
4.7258 | 62 | 3844 |  | 2.8292 | 62 | 3844
4.7258 | 56 | 3136 |  | 2.8292 | 56 | 3136
4.7258 | 55 | 3025 |  | 2.8292 | 55 | 3025
4.7258 | 61 | 3721 |  | 2.8292 | 61 | 3721
4.7268 | 63 | 3969 |  | 2.8299 | 63 | 3969
4.7278 | 52 | 2704 |  | 2.8305 | 52 | 2704
4.7278 | 76 | 5776 |  | 2.8305 | 76 | 5776
4.7288 | 48 | 2304 |  | 2.8311 | 48 | 2304
4.7288 | 24 | 576 |  | 2.8311 | 24 | 576
4.7297 | 53 | 2809 |  | 2.8317 | 53 | 2809
4.7297 | 54 | 2916 |  | 2.8317 | 54 | 2916
4.7308 | 50 | 2500 |  | 2.8324 | 50 | 2500
4.7317 | 54 | 2916 |  | 2.833 | 54 | 2916
4.7317 | 52 | 2704 |  | 2.833 | 52 | 2704
4.7327 | 56 | 3136 |  | 2.8337 | 56 | 3136
4.7327 | 59 | 3481 |  | 2.8337 | 59 | 3481
4.7347 | 68 | 4624 |  | 2.835 | 68 | 4624
4.7357 | 54 | 2916 |  | 2.8356 | 54 | 2916
4.7357 | 53 | 2809 |  | 2.8356 | 53 | 2809
4.7367 | 68 | 4624 |  | 2.8363 | 68 | 4624
4.7387 | 51 | 2601 |  | 2.8376 | 51 | 2601
4.7387 | 57 | 3249 |  | 2.8376 | 57 | 3249
4.7396 | 55 | 3025 |  | 2.8382 | 55 | 3025
4.7396 | 48 | 2304 |  | 2.8382 | 48 | 2304
4.7396 | 42 | 1764 |  | 2.8382 | 42 | 1764
4.7396 | 59 | 3481 |  | 2.8382 | 59 | 3481
4.7396 | 71 | 5041 |  | 2.8382 | 71 | 5041
4.7406 | 45 | 2025 |  | 2.8388 | 45 | 2025
4.7406 | 61 | 3721 |  | 2.8388 | 61 | 3721
4.7416 | 54 | 2916 |  | 2.8395 | 54 | 2916
4.7426 | 47 | 2209 |  | 2.8402 | 47 | 2209
4.7426 | 59 | 3481 |  | 2.8402 | 59 | 3481
4.7426 | 72 | 5184 |  | 2.8402 | 72 | 5184
4.7436 | 50 | 2500 |  | 2.8408 | 50 | 2500
4.7436 | 46 | 2116 |  | 2.8408 | 46 | 2116
4.7446 | 60 | 3600 |  | 2.8414 | 60 | 3600
4.7446 | 72 | 5184 |  | 2.8414 | 72 | 5184
4.7456 | 42 | 1764 |  | 2.8421 | 42 | 1764
4.7456 | 54 | 2916 |  | 2.8421 | 54 | 2916
4.7466 | 58 | 3364 |  | 2.8428 | 58 | 3364
4.7475 | 72 | 5184 |  | 2.8434 | 72 | 5184
4.7485 | 71 | 5041 |  | 2.8441 | 71 | 5041
4.7495 | 47 | 2209 |  | 2.8448 | 47 | 2209
4.7525 | 53 | 2809 |  | 2.8467 | 53 | 2809
4.7525 | 45 | 2025 |  | 2.8467 | 45 | 2025
4.7525 | 65 | 4225 |  | 2.8467 | 65 | 4225
4.7535 | 49 | 2401 |  | 2.8474 | 49 | 2401
4.7545 | 55 | 3025 |  | 2.8481 | 55 | 3025
4.7545 | 52 | 2704 |  | 2.8481 | 52 | 2704
4.7574 | 54 | 2916 |  | 2.8501 | 54 | 2916
4.7574 | 53 | 2809 |  | 2.8501 | 53 | 2809
4.7584 | 52 | 2704 |  | 2.8507 | 52 | 2704
4.7584 | 42 | 1764 |  | 2.8507 | 42 | 1764
4.7584 | 43 | 1849 |  | 2.8507 | 43 | 1849
4.7584 | 63 | 3969 |  | 2.8507 | 63 | 3969
4.7594 | 57 | 3249 |  | 2.8514 | 57 | 3249
4.7614 | 54 | 2916 |  | 2.8527 | 54 | 2916
4.7623 | 51 | 2601 |  | 2.8534 | 51 | 2601
4.7623 | 50 | 2500 |  | 2.8534 | 50 | 2500
4.7623 | 56 | 3136 |  | 2.8534 | 56 | 3136
4.7633 | 49 | 2401 |  | 2.854 | 49 | 2401
4.7633 | 58 | 3364 |  | 2.854 | 58 | 3364
4.7653 | 62 | 3844 |  | 2.8554 | 62 | 3844
4.7663 | 55 | 3025 |  | 2.8561 | 55 | 3025
4.7663 | 54 | 2916 |  | 2.8561 | 54 | 2916
4.7663 | 47 | 2209 |  | 2.8561 | 47 | 2209
4.7683 | 53 | 2809 |  | 2.8575 | 53 | 2809
4.7683 | 52 | 2704 |  | 2.8575 | 52 | 2704
4.7693 | 49 | 2401 |  | 2.8581 | 49 | 2401
4.7693 | 54 | 2916 |  | 2.8581 | 54 | 2916
4.7702 | 49 | 2401 |  | 2.8588 | 49 | 2401
4.7702 | 55 | 3025 |  | 2.8588 | 55 | 3025
4.7742 | 54 | 2916 |  | 2.8615 | 54 | 2916
4.7751 | 46 | 2116 |  | 2.8622 | 46 | 2116
4.7762 | 53 | 2809 |  | 2.8629 | 53 | 2809
4.7762 | 53 | 2809 |  | 2.8629 | 53 | 2809
4.7762 | 63 | 3969 |  | 2.8629 | 63 | 3969
4.7771 | 58 | 3364 |  | 2.8636 | 58 | 3364
4.7771 | 50 | 2500 |  | 2.8636 | 50 | 2500
4.7771 | 50 | 2500 |  | 2.8636 | 50 | 2500
4.7771 | 56 | 3136 |  | 2.8636 | 56 | 3136
4.7771 | 68 | 4624 |  | 2.8636 | 68 | 4624
4.7781 | 55 | 3025 |  | 2.8643 | 55 | 3025
4.7801 | 58 | 3364 |  | 2.8657 | 58 | 3364
4.7801 | 52 | 2704 |  | 2.8657 | 52 | 2704
4.7811 | 51 | 2601 |  | 2.8663 | 51 | 2601
4.7811 | 49 | 2401 |  | 2.8663 | 49 | 2401
4.782 | 54 | 2916 |  | 2.867 | 54 | 2916
4.782 | 51 | 2601 |  | 2.867 | 51 | 2601
4.782 | 52 | 2704 |  | 2.867 | 52 | 2704
4.783 | 42 | 1764 |  | 2.8677 | 42 | 1764
4.784 | 56 | 3136 |  | 2.8684 | 56 | 3136
4.785 | 53 | 2809 |  | 2.8691 | 53 | 2809
4.785 | 53 | 2809 |  | 2.8691 | 53 | 2809
4.785 | 51 | 2601 |  | 2.8691 | 51 | 2601
4.786 | 44 | 1936 |  | 2.8698 | 44 | 1936
4.786 | 45 | 2025 |  | 2.8698 | 45 | 2025
4.787 | 53 | 2809 |  | 2.8705 | 53 | 2809
4.787 | 49 | 2401 |  | 2.8705 | 49 | 2401
4.787 | 49 | 2401 |  | 2.8705 | 49 | 2401
4.788 | 53 | 2809 |  | 2.8712 | 53 | 2809
4.788 | 45 | 2025 |  | 2.8712 | 45 | 2025
4.7889 | 53 | 2809 |  | 2.8719 | 53 | 2809
4.7889 | 48 | 2304 |  | 2.8719 | 48 | 2304
4.7889 | 58 | 3364 |  | 2.8719 | 58 | 3364
4.7889 | 58 | 3364 |  | 2.8719 | 58 | 3364
4.7899 | 52 | 2704 |  | 2.8726 | 52 | 2704
4.7899 | 42 | 1764 |  | 2.8726 | 42 | 1764
4.7899 | 55 | 3025 |  | 2.8726 | 55 | 3025
4.7909 | 56 | 3136 |  | 2.8733 | 56 | 3136
4.7909 | 46 | 2116 |  | 2.8733 | 46 | 2116
4.7909 | 49 | 2401 |  | 2.8733 | 49 | 2401
4.7919 | 24 | 576 |  | 2.874 | 24 | 576
4.7919 | 55 | 3025 |  | 2.874 | 55 | 3025
4.7919 | 48 | 2304 |  | 2.874 | 48 | 2304
4.7928 | 45 | 2025 |  | 2.8747 | 45 | 2025
4.7928 | 46 | 2116 |  | 2.8747 | 46 | 2116
4.7938 | 60 | 3600 |  | 2.8754 | 60 | 3600
4.7938 | 49 | 2401 |  | 2.8754 | 49 | 2401
4.7948 | 53 | 2809 |  | 2.8761 | 53 | 2809
4.7948 | 53 | 2809 |  | 2.8761 | 53 | 2809
4.7948 | 46 | 2116 |  | 2.8761 | 46 | 2116
4.7948 | 53 | 2809 |  | 2.8761 | 53 | 2809
4.7948 | 44 | 1936 |  | 2.8761 | 44 | 1936
4.7948 | 35 | 1225 |  | 2.8761 | 35 | 1225
4.7948 | 73 | 5329 |  | 2.8761 | 73 | 5329
4.7948 | 69 | 4761 |  | 2.8761 | 69 | 4761
4.7958 | 45 | 2025 |  | 2.8768 | 45 | 2025
4.7958 | 51 | 2601 |  | 2.8768 | 51 | 2601
4.7958 | 52 | 2704 |  | 2.8768 | 52 | 2704
4.7958 | 50 | 2500 |  | 2.8768 | 50 | 2500
4.7958 | 48 | 2304 |  | 2.8768 | 48 | 2304
4.7988 | 45 | 2025 |  | 2.8789 | 45 | 2025
4.7988 | 55 | 3025 |  | 2.8789 | 55 | 3025
4.7997 | 50 | 2500 |  | 2.8796 | 50 | 2500
4.8007 | 35 | 1225 |  | 2.8803 | 35 | 1225
4.8007 | 35 | 1225 |  | 2.8803 | 35 | 1225
4.8017 | 37 | 1369 |  | 2.881 | 37 | 1369
4.8017 | 42 | 1764 |  | 2.881 | 42 | 1764
4.8027 | 59 | 3481 |  | 2.8818 | 59 | 3481
4.8046 | 44 | 1936 |  | 2.8832 | 44 | 1936
4.8046 | 48 | 2304 |  | 2.8832 | 48 | 2304
4.8066 | 44 | 1936 |  | 2.8846 | 44 | 1936
4.8066 | 49 | 2401 |  | 2.8846 | 49 | 2401
4.8076 | 59 | 3481 |  | 2.8854 | 59 | 3481
4.8085 | 45 | 2025 |  | 2.8861 | 45 | 2025
4.8085 | 49 | 2401 |  | 2.8861 | 49 | 2401
4.8115 | 39 | 1521 |  | 2.8882 | 39 | 1521
4.8115 | 47 | 2209 |  | 2.8882 | 47 | 2209
4.8125 | 69 | 4761 |  | 2.8889 | 69 | 4761
4.8145 | 36 | 1296 |  | 2.8904 | 36 | 1296
4.8154 | 51 | 2601 |  | 2.8911 | 51 | 2601
4.8154 | 53 | 2809 |  | 2.8911 | 53 | 2809
4.8154 | 69 | 4761 |  | 2.8911 | 69 | 4761
4.8164 | 33 | 1089 |  | 2.8918 | 33 | 1089
4.8164 | 49 | 2401 |  | 2.8918 | 49 | 2401
4.8164 | 70 | 4900 |  | 2.8918 | 70 | 4900
4.8174 | 52 | 2704 |  | 2.8926 | 52 | 2704
4.8184 | 58 | 3364 |  | 2.8933 | 58 | 3364
4.8184 | 57 | 3249 |  | 2.8933 | 57 | 3249
4.8184 | 44 | 1936 |  | 2.8933 | 44 | 1936
4.8184 | 66 | 4356 |  | 2.8933 | 66 | 4356
4.8193 | 56 | 3136 |  | 2.894 | 56 | 3136
4.8193 | 47 | 2209 |  | 2.894 | 47 | 2209
4.8193 | 40 | 1600 |  | 2.894 | 40 | 1600
4.8203 | 54 | 2916 |  | 2.8948 | 54 | 2916
4.8203 | 50 | 2500 |  | 2.8948 | 50 | 2500
4.8213 | 33 | 1089 |  | 2.8955 | 33 | 1089
4.8223 | 55 | 3025 |  | 2.8963 | 55 | 3025
4.8223 | 57 | 3249 |  | 2.8963 | 57 | 3249
4.8232 | 47 | 2209 |  | 2.897 | 47 | 2209
4.8232 | 51 | 2601 |  | 2.897 | 51 | 2601
4.8232 | 69 | 4761 |  | 2.897 | 69 | 4761
4.8242 | 46 | 2116 |  | 2.8977 | 46 | 2116
4.8242 | 45 | 2025 |  | 2.8977 | 45 | 2025
4.8242 | 46 | 2116 |  | 2.8977 | 46 | 2116
4.8242 | 52 | 2704 |  | 2.8977 | 52 | 2704
4.8252 | 56 | 3136 |  | 2.8985 | 56 | 3136
4.8262 | 37 | 1369 |  | 2.8992 | 37 | 1369
4.8262 | 49 | 2401 |  | 2.8992 | 49 | 2401
4.8281 | 50 | 2500 |  | 2.9007 | 50 | 2500
4.8281 | 49 | 2401 |  | 2.9007 | 49 | 2401
4.8281 | 54 | 2916 |  | 2.9007 | 54 | 2916
4.8281 | 49 | 2401 |  | 2.9007 | 49 | 2401
4.8291 | 46 | 2116 |  | 2.9014 | 46 | 2116
4.8301 | 58 | 3364 |  | 2.9022 | 58 | 3364
4.8301 | 34 | 1156 |  | 2.9022 | 34 | 1156
4.8301 | 54 | 2916 |  | 2.9022 | 54 | 2916
4.8301 | 54 | 2916 |  | 2.9022 | 54 | 2916
4.8311 | 47 | 2209 |  | 2.9029 | 47 | 2209
4.832 | 32 | 1024 |  | 2.9036 | 32 | 1024
4.8331 | 45 | 2025 |  | 2.9044 | 45 | 2025
4.8331 | 38 | 1444 |  | 2.9044 | 38 | 1444
4.8331 | 51 | 2601 |  | 2.9044 | 51 | 2601
4.834 | 45 | 2025 |  | 2.9051 | 45 | 2025
4.834 | 58 | 3364 |  | 2.9051 | 58 | 3364
4.834 | 55 | 3025 |  | 2.9051 | 55 | 3025
4.834 | 55 | 3025 |  | 2.9051 | 55 | 3025
4.834 | 75 | 5625 |  | 2.9051 | 75 | 5625
4.835 | 51 | 2601 |  | 2.9059 | 51 | 2601
4.835 | 45 | 2025 |  | 2.9059 | 45 | 2025
4.8359 | 52 | 2704 |  | 2.9066 | 52 | 2704
4.8359 | 52 | 2704 |  | 2.9066 | 52 | 2704
4.837 | 45 | 2025 |  | 2.9074 | 45 | 2025
4.837 | 49 | 2401 |  | 2.9074 | 49 | 2401
4.8379 | 32 | 1024 |  | 2.9081 | 32 | 1024
4.8379 | 51 | 2601 |  | 2.9081 | 51 | 2601
4.8389 | 45 | 2025 |  | 2.9089 | 45 | 2025
4.8389 | 49 | 2401 |  | 2.9089 | 49 | 2401
4.8389 | 61 | 3721 |  | 2.9089 | 61 | 3721
4.8398 | 46 | 2116 |  | 2.9096 | 46 | 2116
4.8418 | 53 | 2809 |  | 2.9112 | 53 | 2809
4.8418 | 50 | 2500 |  | 2.9112 | 50 | 2500
4.8428 | 27 | 729 |  | 2.9119 | 27 | 729
4.8438 | 44 | 1936 |  | 2.9127 | 44 | 1936
4.8438 | 58 | 3364 |  | 2.9127 | 58 | 3364
4.8448 | 47 | 2209 |  | 2.9134 | 47 | 2209
4.8448 | 61 | 3721 |  | 2.9134 | 61 | 3721
4.8448 | 51 | 2601 |  | 2.9134 | 51 | 2601
4.8457 | 31 | 961 |  | 2.9142 | 31 | 961
4.8457 | 45 | 2025 |  | 2.9142 | 45 | 2025
4.8457 | 41 | 1681 |  | 2.9142 | 41 | 1681
4.8467 | 42 | 1764 |  | 2.9149 | 42 | 1764
4.8467 | 48 | 2304 |  | 2.9149 | 48 | 2304
4.8487 | 51 | 2601 |  | 2.9165 | 51 | 2601
4.8496 | 32 | 1024 |  | 2.9172 | 32 | 1024
4.8496 | 66 | 4356 |  | 2.9172 | 66 | 4356
4.8506 | 68 | 4624 |  | 2.918 | 68 | 4624
4.8516 | 34 | 1156 |  | 2.9188 | 34 | 1156
4.8516 | 51 | 2601 |  | 2.9188 | 51 | 2601
4.8526 | 54 | 2916 |  | 2.9196 | 54 | 2916
4.8526 | 49 | 2401 |  | 2.9196 | 49 | 2401
4.8526 | 65 | 4225 |  | 2.9196 | 65 | 4225
4.8535 | 41 | 1681 |  | 2.9203 | 41 | 1681
4.8535 | 48 | 2304 |  | 2.9203 | 48 | 2304
4.8545 | 48 | 2304 |  | 2.9211 | 48 | 2304
4.8555 | 29 | 841 |  | 2.9219 | 29 | 841
4.8555 | 54 | 2916 |  | 2.9219 | 54 | 2916
4.8565 | 47 | 2209 |  | 2.9226 | 47 | 2209
4.8565 | 53 | 2809 |  | 2.9226 | 53 | 2809
4.8565 | 65 | 4225 |  | 2.9226 | 65 | 4225
4.8574 | 49 | 2401 |  | 2.9234 | 49 | 2401
4.8584 | 53 | 2809 |  | 2.9242 | 53 | 2809
4.8584 | 53 | 2809 |  | 2.9242 | 53 | 2809
4.8584 | 49 | 2401 |  | 2.9242 | 49 | 2401
4.8584 | 34 | 1156 |  | 2.9242 | 34 | 1156
4.8594 | 50 | 2500 |  | 2.925 | 50 | 2500
4.8594 | 48 | 2304 |  | 2.925 | 48 | 2304
4.8604 | 36 | 1296 |  | 2.9257 | 36 | 1296
4.8604 | 42 | 1764 |  | 2.9257 | 42 | 1764
4.8604 | 56 | 3136 |  | 2.9257 | 56 | 3136
4.8604 | 50 | 2500 |  | 2.9257 | 50 | 2500
4.8604 | 63 | 3969 |  | 2.9257 | 63 | 3969
4.8613 | 48 | 2304 |  | 2.9265 | 48 | 2304
4.8613 | 48 | 2304 |  | 2.9265 | 48 | 2304
4.8623 | 50 | 2500 |  | 2.9273 | 50 | 2500
4.8623 | 51 | 2601 |  | 2.9273 | 51 | 2601
4.8643 | 46 | 2116 |  | 2.9288 | 46 | 2116
4.8643 | 51 | 2601 |  | 2.9288 | 51 | 2601
4.8643 | 51 | 2601 |  | 2.9288 | 51 | 2601
4.8652 | 43 | 1849 |  | 2.9296 | 43 | 1849
4.8652 | 45 | 2025 |  | 2.9296 | 45 | 2025
4.8652 | 43 | 1849 |  | 2.9296 | 43 | 1849
4.8652 | 44 | 1936 |  | 2.9296 | 44 | 1936
4.8652 | 63 | 3969 |  | 2.9296 | 63 | 3969
4.8662 | 44 | 1936 |  | 2.9304 | 44 | 1936
4.8672 | 56 | 3136 |  | 2.9312 | 56 | 3136
4.8672 | 51 | 2601 |  | 2.9312 | 51 | 2601
4.8672 | 50 | 2500 |  | 2.9312 | 50 | 2500
4.8672 | 65 | 4225 |  | 2.9312 | 65 | 4225
4.8682 | 53 | 2809 |  | 2.932 | 53 | 2809
4.8682 | 45 | 2025 |  | 2.932 | 45 | 2025
4.8691 | 75 | 5625 |  | 2.9328 | 75 | 5625
4.8701 | 45 | 2025 |  | 2.9336 | 45 | 2025
4.8701 | 27 | 729 |  | 2.9336 | 27 | 729
4.8701 | 32 | 1024 |  | 2.9336 | 32 | 1024
4.8701 | 63 | 3969 |  | 2.9336 | 63 | 3969
4.8711 | 52 | 2704 |  | 2.9344 | 52 | 2704
4.8721 | 50 | 2500 |  | 2.9351 | 50 | 2500
4.8721 | 49 | 2401 |  | 2.9351 | 49 | 2401
4.873 | 47 | 2209 |  | 2.9359 | 47 | 2209
4.873 | 43 | 1849 |  | 2.9359 | 43 | 1849
4.873 | 55 | 3025 |  | 2.9359 | 55 | 3025
4.874 | 48 | 2304 |  | 2.9367 | 48 | 2304
4.874 | 54 | 2916 |  | 2.9367 | 54 | 2916
4.8759 | 44 | 1936 |  | 2.9383 | 44 | 1936
4.8759 | 49 | 2401 |  | 2.9383 | 49 | 2401
4.8759 | 58 | 3364 |  | 2.9383 | 58 | 3364
4.8759 | 64 | 4096 |  | 2.9383 | 64 | 4096
4.8759 | 67 | 4489 |  | 2.9383 | 67 | 4489
4.8779 | 48 | 2304 |  | 2.9399 | 48 | 2304
4.8798 | 57 | 3249 |  | 2.9415 | 57 | 3249
4.8798 | 51 | 2601 |  | 2.9415 | 51 | 2601
4.8808 | 45 | 2025 |  | 2.9423 | 45 | 2025
4.8808 | 47 | 2209 |  | 2.9423 | 47 | 2209
4.8808 | 50 | 2500 |  | 2.9423 | 50 | 2500
4.8818 | 59 | 3481 |  | 2.9431 | 59 | 3481
4.8818 | 49 | 2401 |  | 2.9431 | 49 | 2401
4.8818 | 48 | 2304 |  | 2.9431 | 48 | 2304
4.8818 | 69 | 4761 |  | 2.9431 | 69 | 4761
4.8828 | 72 | 5184 |  | 2.9439 | 72 | 5184
4.8837 | 43 | 1849 |  | 2.9447 | 43 | 1849
4.8847 | 52 | 2704 |  | 2.9455 | 52 | 2704
4.8847 | 43 | 1849 |  | 2.9455 | 43 | 1849
4.8857 | 50 | 2500 |  | 2.9463 | 50 | 2500
4.8857 | 47 | 2209 |  | 2.9463 | 47 | 2209
4.8867 | 25 | 625 |  | 2.9471 | 25 | 625
4.8867 | 24 | 576 |  | 2.9471 | 24 | 576
4.8886 | 44 | 1936 |  | 2.9487 | 44 | 1936
4.8886 | 49 | 2401 |  | 2.9487 | 49 | 2401
4.8886 | 41 | 1681 |  | 2.9487 | 41 | 1681
4.8896 | 48 | 2304 |  | 2.9496 | 48 | 2304
4.8896 | 49 | 2401 |  | 2.9496 | 49 | 2401
4.8896 | 57 | 3249 |  | 2.9496 | 57 | 3249
4.8905 | 48 | 2304 |  | 2.9504 | 48 | 2304
4.8905 | 48 | 2304 |  | 2.9504 | 48 | 2304
4.8905 | 45 | 2025 |  | 2.9504 | 45 | 2025
4.8905 | 57 | 3249 |  | 2.9504 | 57 | 3249
4.8924 | 55 | 3025 |  | 2.952 | 55 | 3025
4.8924 | 54 | 2916 |  | 2.952 | 54 | 2916
4.8935 | 46 | 2116 |  | 2.9528 | 46 | 2116
4.8935 | 50 | 2500 |  | 2.9528 | 50 | 2500
4.8944 | 46 | 2116 |  | 2.9536 | 46 | 2116
4.8944 | 52 | 2704 |  | 2.9536 | 52 | 2704
4.8944 | 52 | 2704 |  | 2.9536 | 52 | 2704
4.8944 | 62 | 3844 |  | 2.9536 | 62 | 3844
4.8954 | 45 | 2025 |  | 2.9545 | 45 | 2025
4.8954 | 49 | 2401 |  | 2.9545 | 49 | 2401
4.8954 | 51 | 2601 |  | 2.9545 | 51 | 2601
4.8954 | 60 | 3600 |  | 2.9545 | 60 | 3600
4.8964 | 45 | 2025 |  | 2.9553 | 45 | 2025
4.8964 | 53 | 2809 |  | 2.9553 | 53 | 2809
4.8964 | 52 | 2704 |  | 2.9553 | 52 | 2704
4.8964 | 41 | 1681 |  | 2.9553 | 41 | 1681
4.8973 | 58 | 3364 |  | 2.9561 | 58 | 3364
4.8973 | 52 | 2704 |  | 2.9561 | 52 | 2704
4.8983 | 45 | 2025 |  | 2.9569 | 45 | 2025
4.8983 | 45 | 2025 |  | 2.9569 | 45 | 2025
4.8983 | 48 | 2304 |  | 2.9569 | 48 | 2304
4.8983 | 66 | 4356 |  | 2.9569 | 66 | 4356
4.8983 | 55 | 3025 |  | 2.9569 | 55 | 3025
4.8992 | 50 | 2500 |  | 2.9577 | 50 | 2500
4.8992 | 42 | 1764 |  | 2.9577 | 42 | 1764
4.8992 | 56 | 3136 |  | 2.9577 | 56 | 3136
4.8992 | 55 | 3025 |  | 2.9577 | 55 | 3025
4.8992 | 61 | 3721 |  | 2.9577 | 61 | 3721
4.9003 | 45 | 2025 |  | 2.9586 | 45 | 2025
4.9003 | 40 | 1600 |  | 2.9586 | 40 | 1600
4.9003 | 48 | 2304 |  | 2.9586 | 48 | 2304
4.9003 | 50 | 2500 |  | 2.9586 | 50 | 2500
4.9012 | 46 | 2116 |  | 2.9594 | 46 | 2116
4.9012 | 53 | 2809 |  | 2.9594 | 53 | 2809
4.9022 | 24 | 576 |  | 2.9602 | 24 | 576
4.9022 | 46 | 2116 |  | 2.9602 | 46 | 2116
4.9022 | 62 | 3844 |  | 2.9602 | 62 | 3844
4.9031 | 26 | 676 |  | 2.961 | 26 | 676
4.9031 | 40 | 1600 |  | 2.961 | 40 | 1600
4.9031 | 26 | 676 |  | 2.961 | 26 | 676
4.9031 | 55 | 3025 |  | 2.961 | 55 | 3025
4.9031 | 62 | 3844 |  | 2.961 | 62 | 3844
4.9051 | 48 | 2304 |  | 2.9627 | 48 | 2304
4.9051 | 50 | 2500 |  | 2.9627 | 50 | 2500
4.9051 | 47 | 2209 |  | 2.9627 | 47 | 2209
4.906 | 45 | 2025 |  | 2.9635 | 45 | 2025
4.906 | 48 | 2304 |  | 2.9635 | 48 | 2304
4.907 | 62 | 3844 |  | 2.9644 | 62 | 3844
4.907 | 54 | 2916 |  | 2.9644 | 54 | 2916
4.908 | 45 | 2025 |  | 2.9652 | 45 | 2025
4.908 | 49 | 2401 |  | 2.9652 | 49 | 2401
4.908 | 39 | 1521 |  | 2.9652 | 39 | 1521
4.908 | 50 | 2500 |  | 2.9652 | 50 | 2500
4.908 | 48 | 2304 |  | 2.9652 | 48 | 2304
4.908 | 49 | 2401 |  | 2.9652 | 49 | 2401
4.908 | 59 | 3481 |  | 2.9652 | 59 | 3481
4.909 | 66 | 4356 |  | 2.9661 | 66 | 4356
4.9099 | 45 | 2025 |  | 2.9669 | 45 | 2025
4.9099 | 45 | 2025 |  | 2.9669 | 45 | 2025
4.9109 | 53 | 2809 |  | 2.9677 | 53 | 2809
4.9109 | 52 | 2704 |  | 2.9677 | 52 | 2704
4.9109 | 48 | 2304 |  | 2.9677 | 48 | 2304
4.9109 | 62 | 3844 |  | 2.9677 | 62 | 3844
4.9109 | 56 | 3136 |  | 2.9677 | 56 | 3136
4.9119 | 52 | 2704 |  | 2.9686 | 52 | 2704
4.9128 | 24 | 576 |  | 2.9694 | 24 | 576
4.9128 | 25 | 625 |  | 2.9694 | 25 | 625
4.9128 | 48 | 2304 |  | 2.9694 | 48 | 2304
4.9138 | 50 | 2500 |  | 2.9702 | 50 | 2500
4.9138 | 50 | 2500 |  | 2.9702 | 50 | 2500
4.9147 | 47 | 2209 |  | 2.9711 | 47 | 2209
4.9147 | 49 | 2401 |  | 2.9711 | 49 | 2401
4.9158 | 46 | 2116 |  | 2.9719 | 46 | 2116
4.9158 | 59 | 3481 |  | 2.9719 | 59 | 3481
4.9167 | 55 | 3025 |  | 2.9728 | 55 | 3025
4.9167 | 49 | 2401 |  | 2.9728 | 49 | 2401
4.9177 | 44 | 1936 |  | 2.9736 | 44 | 1936
4.9177 | 60 | 3600 |  | 2.9736 | 60 | 3600
4.9177 | 55 | 3025 |  | 2.9736 | 55 | 3025
4.9186 | 49 | 2401 |  | 2.9744 | 49 | 2401
4.9186 | 51 | 2601 |  | 2.9744 | 51 | 2601
4.9186 | 56 | 3136 |  | 2.9744 | 56 | 3136
4.9196 | 47 | 2209 |  | 2.9753 | 47 | 2209
4.9196 | 61 | 3721 |  | 2.9753 | 61 | 3721
4.9196 | 59 | 3481 |  | 2.9753 | 59 | 3481
4.9206 | 41 | 1681 |  | 2.9762 | 41 | 1681
4.9206 | 47 | 2209 |  | 2.9762 | 47 | 2209
4.9206 | 42 | 1764 |  | 2.9762 | 42 | 1764
4.9206 | 58 | 3364 |  | 2.9762 | 58 | 3364
4.9215 | 48 | 2304 |  | 2.977 | 48 | 2304
4.9215 | 50 | 2500 |  | 2.977 | 50 | 2500
4.9225 | 27 | 729 |  | 2.9779 | 27 | 729
4.9225 | 51 | 2601 |  | 2.9779 | 51 | 2601
4.9235 | 58 | 3364 |  | 2.9787 | 58 | 3364
4.9235 | 57 | 3249 |  | 2.9787 | 57 | 3249
4.9244 | 42 | 1764 |  | 2.9796 | 42 | 1764
4.9244 | 28 | 784 |  | 2.9796 | 28 | 784
4.9254 | 32 | 1024 |  | 2.9804 | 32 | 1024
4.9254 | 47 | 2209 |  | 2.9804 | 47 | 2209
4.9264 | 46 | 2116 |  | 2.9813 | 46 | 2116
4.9264 | 47 | 2209 |  | 2.9813 | 47 | 2209
4.9283 | 24 | 576 |  | 2.983 | 24 | 576
4.9283 | 62 | 3844 |  | 2.983 | 62 | 3844
4.9283 | 63 | 3969 |  | 2.983 | 63 | 3969
4.9293 | 25 | 625 |  | 2.9839 | 25 | 625
4.9293 | 47 | 2209 |  | 2.9839 | 47 | 2209
4.9293 | 57 | 3249 |  | 2.9839 | 57 | 3249
4.9303 | 25 | 625 |  | 2.9848 | 25 | 625
4.9303 | 49 | 2401 |  | 2.9848 | 49 | 2401
4.9303 | 57 | 3249 |  | 2.9848 | 57 | 3249
4.9312 | 50 | 2500 |  | 2.9856 | 50 | 2500
4.9312 | 51 | 2601 |  | 2.9856 | 51 | 2601
4.9322 | 48 | 2304 |  | 2.9865 | 48 | 2304
4.9322 | 55 | 3025 |  | 2.9865 | 55 | 3025
4.9322 | 60 | 3600 |  | 2.9865 | 60 | 3600
4.9341 | 46 | 2116 |  | 2.9882 | 46 | 2116
4.9341 | 50 | 2500 |  | 2.9882 | 50 | 2500
4.9341 | 48 | 2304 |  | 2.9882 | 48 | 2304
4.9341 | 59 | 3481 |  | 2.9882 | 59 | 3481
4.9341 | 61 | 3721 |  | 2.9882 | 61 | 3721
4.9351 | 30 | 900 |  | 2.9891 | 30 | 900
4.9351 | 50 | 2500 |  | 2.9891 | 50 | 2500
4.9351 | 61 | 3721 |  | 2.9891 | 61 | 3721
4.9351 | 64 | 4096 |  | 2.9891 | 64 | 4096
4.9351 | 51 | 2601 |  | 2.9891 | 51 | 2601
4.936 | 48 | 2304 |  | 2.9899 | 48 | 2304
4.936 | 56 | 3136 |  | 2.9899 | 56 | 3136
4.937 | 47 | 2209 |  | 2.9908 | 47 | 2209
4.937 | 47 | 2209 |  | 2.9908 | 47 | 2209
4.937 | 46 | 2116 |  | 2.9908 | 46 | 2116
4.937 | 62 | 3844 |  | 2.9908 | 62 | 3844
4.938 | 47 | 2209 |  | 2.9917 | 47 | 2209
4.938 | 53 | 2809 |  | 2.9917 | 53 | 2809
4.9389 | 54 | 2916 |  | 2.9926 | 54 | 2916
4.9389 | 61 | 3721 |  | 2.9926 | 61 | 3721
4.9389 | 55 | 3025 |  | 2.9926 | 55 | 3025
4.9399 | 47 | 2209 |  | 2.9934 | 47 | 2209
4.9399 | 51 | 2601 |  | 2.9934 | 51 | 2601
4.9408 | 26 | 676 |  | 2.9943 | 26 | 676
4.9408 | 48 | 2304 |  | 2.9943 | 48 | 2304
4.9408 | 58 | 3364 |  | 2.9943 | 58 | 3364
4.9408 | 53 | 2809 |  | 2.9943 | 53 | 2809
4.9408 | 57 | 3249 |  | 2.9943 | 57 | 3249
4.9419 | 50 | 2500 |  | 2.9952 | 50 | 2500
4.9419 | 60 | 3600 |  | 2.9952 | 60 | 3600
4.9419 | 57 | 3249 |  | 2.9952 | 57 | 3249
4.9428 | 46 | 2116 |  | 2.9961 | 46 | 2116
4.9428 | 47 | 2209 |  | 2.9961 | 47 | 2209
4.9428 | 49 | 2401 |  | 2.9961 | 49 | 2401
4.9437 | 52 | 2704 |  | 2.9969 | 52 | 2704
4.9437 | 50 | 2500 |  | 2.9969 | 50 | 2500
4.9437 | 31 | 961 |  | 2.9969 | 31 | 961
4.9437 | 56 | 3136 |  | 2.9969 | 56 | 3136
4.9437 | 55 | 3025 |  | 2.9969 | 55 | 3025
4.9437 | 58 | 3364 |  | 2.9969 | 58 | 3364
4.9437 | 51 | 2601 |  | 2.9969 | 51 | 2601
4.9447 | 48 | 2304 |  | 2.9978 | 48 | 2304
4.9457 | 29 | 841 |  | 2.9987 | 29 | 841
4.9457 | 46 | 2116 |  | 2.9987 | 46 | 2116
4.9457 | 51 | 2601 |  | 2.9987 | 51 | 2601
4.9457 | 46 | 2116 |  | 2.9987 | 46 | 2116
4.9457 | 53 | 2809 |  | 2.9987 | 53 | 2809
4.9457 | 56 | 3136 |  | 2.9987 | 56 | 3136
4.9457 | 57 | 3249 |  | 2.9987 | 57 | 3249
4.9457 | 64 | 4096 |  | 2.9987 | 64 | 4096
4.9486 | 26 | 676 |  | 3.0014 | 26 | 676
4.9486 | 60 | 3600 |  | 3.0014 | 60 | 3600
4.9486 | 62 | 3844 |  | 3.0014 | 62 | 3844
4.9486 | 54 | 2916 |  | 3.0014 | 54 | 2916
4.9486 | 58 | 3364 |  | 3.0014 | 58 | 3364
4.9496 | 44 | 1936 |  | 3.0022 | 44 | 1936
4.9496 | 66 | 4356 |  | 3.0022 | 66 | 4356
4.9496 | 56 | 3136 |  | 3.0022 | 56 | 3136
4.9515 | 45 | 2025 |  | 3.004 | 45 | 2025
4.9515 | 53 | 2809 |  | 3.004 | 53 | 2809
4.9515 | 51 | 2601 |  | 3.004 | 51 | 2601
4.9515 | 56 | 3136 |  | 3.004 | 56 | 3136
4.9515 | 58 | 3364 |  | 3.004 | 58 | 3364
4.9525 | 25 | 625 |  | 3.0049 | 25 | 625
4.9525 | 53 | 2809 |  | 3.0049 | 53 | 2809
4.9525 | 54 | 2916 |  | 3.0049 | 54 | 2916
4.9534 | 47 | 2209 |  | 3.0058 | 47 | 2209
4.9534 | 55 | 3025 |  | 3.0058 | 55 | 3025
4.9544 | 49 | 2401 |  | 3.0067 | 49 | 2401
4.9553 | 54 | 2916 |  | 3.0076 | 54 | 2916
4.9553 | 55 | 3025 |  | 3.0076 | 55 | 3025
4.9553 | 57 | 3249 |  | 3.0076 | 57 | 3249
4.9563 | 59 | 3481 |  | 3.0085 | 59 | 3481
4.9563 | 46 | 2116 |  | 3.0085 | 46 | 2116
4.9563 | 50 | 2500 |  | 3.0085 | 50 | 2500
4.9573 | 34 | 1156 |  | 3.0094 | 34 | 1156
4.9573 | 65 | 4225 |  | 3.0094 | 65 | 4225
4.9573 | 57 | 3249 |  | 3.0094 | 57 | 3249
4.9582 | 35 | 1225 |  | 3.0103 | 35 | 1225
4.9592 | 56 | 3136 |  | 3.0112 | 56 | 3136
4.9592 | 53 | 2809 |  | 3.0112 | 53 | 2809
4.9592 | 60 | 3600 |  | 3.0112 | 60 | 3600
4.9602 | 52 | 2704 |  | 3.0121 | 52 | 2704
4.9602 | 50 | 2500 |  | 3.0121 | 50 | 2500
4.9611 | 45 | 2025 |  | 3.013 | 45 | 2025
4.9611 | 54 | 2916 |  | 3.013 | 54 | 2916
4.9611 | 58 | 3364 |  | 3.013 | 58 | 3364
4.9621 | 33 | 1089 |  | 3.0139 | 33 | 1089
4.9621 | 55 | 3025 |  | 3.0139 | 55 | 3025
4.963 | 45 | 2025 |  | 3.0148 | 45 | 2025
4.963 | 51 | 2601 |  | 3.0148 | 51 | 2601
4.963 | 46 | 2116 |  | 3.0148 | 46 | 2116
4.964 | 44 | 1936 |  | 3.0157 | 44 | 1936
4.964 | 57 | 3249 |  | 3.0157 | 57 | 3249
4.964 | 44 | 1936 |  | 3.0157 | 44 | 1936
4.964 | 59 | 3481 |  | 3.0157 | 59 | 3481
4.964 | 65 | 4225 |  | 3.0157 | 65 | 4225
4.965 | 53 | 2809 |  | 3.0166 | 53 | 2809
4.9659 | 34 | 1156 |  | 3.0175 | 34 | 1156
4.9668 | 51 | 2601 |  | 3.0184 | 51 | 2601
4.9668 | 55 | 3025 |  | 3.0184 | 55 | 3025
4.9668 | 62 | 3844 |  | 3.0184 | 62 | 3844
4.9679 | 41.7 | 1738.89 |  | 3.0193 | 41.7 | 1738.89
4.9679 | 57 | 3249 |  | 3.0193 | 57 | 3249
4.9679 | 54 | 2916 |  | 3.0193 | 54 | 2916
4.9679 | 52 | 2704 |  | 3.0193 | 52 | 2704
4.9679 | 51 | 2601 |  | 3.0193 | 51 | 2601
4.9688 | 46 | 2116 |  | 3.0202 | 46 | 2116
4.9688 | 52 | 2704 |  | 3.0202 | 52 | 2704
4.9697 | 32 | 1024 |  | 3.0211 | 32 | 1024
4.9697 | 59 | 3481 |  | 3.0211 | 59 | 3481
4.9707 | 41 | 1681 |  | 3.022 | 41 | 1681
4.9707 | 60 | 3600 |  | 3.022 | 60 | 3600
4.9717 | 55 | 3025 |  | 3.023 | 55 | 3025
4.9726 | 51 | 2601 |  | 3.0239 | 51 | 2601
4.9726 | 53 | 2809 |  | 3.0239 | 53 | 2809
4.9736 | 47 | 2209 |  | 3.0248 | 47 | 2209
4.9736 | 46 | 2116 |  | 3.0248 | 46 | 2116
4.9736 | 52 | 2704 |  | 3.0248 | 52 | 2704
4.9745 | 23 | 529 |  | 3.0257 | 23 | 529
4.9745 | 34 | 1156 |  | 3.0257 | 34 | 1156
4.9745 | 31 | 961 |  | 3.0257 | 31 | 961
4.9745 | 46 | 2116 |  | 3.0257 | 46 | 2116
4.9755 | 23 | 529 |  | 3.0267 | 23 | 529
4.9755 | 53 | 2809 |  | 3.0267 | 53 | 2809
4.9765 | 58 | 3364 |  | 3.0276 | 58 | 3364
4.9774 | 54 | 2916 |  | 3.0285 | 54 | 2916
4.9774 | 49 | 2401 |  | 3.0285 | 49 | 2401
4.9774 | 48 | 2304 |  | 3.0285 | 48 | 2304
4.9794 | 47 | 2209 |  | 3.0304 | 47 | 2209
4.9803 | 55 | 3025 |  | 3.0313 | 55 | 3025
4.9803 | 56 | 3136 |  | 3.0313 | 56 | 3136
4.9813 | 50 | 2500 |  | 3.0322 | 50 | 2500
4.9813 | 56 | 3136 |  | 3.0322 | 56 | 3136
4.9823 | 53 | 2809 |  | 3.0332 | 53 | 2809
4.9823 | 57 | 3249 |  | 3.0332 | 57 | 3249
4.9823 | 54 | 2916 |  | 3.0332 | 54 | 2916
4.9861 | 51 | 2601 |  | 3.0369 | 51 | 2601
4.987 | 47 | 2209 |  | 3.0378 | 47 | 2209
4.987 | 43 | 1849 |  | 3.0378 | 43 | 1849
4.987 | 59 | 3481 |  | 3.0378 | 59 | 3481
4.988 | 45 | 2025 |  | 3.0388 | 45 | 2025
4.988 | 54 | 2916 |  | 3.0388 | 54 | 2916
4.9889 | 47 | 2209 |  | 3.0397 | 47 | 2209
4.9889 | 46 | 2116 |  | 3.0397 | 46 | 2116
4.9899 | 32 | 1024 |  | 3.0407 | 32 | 1024
4.9899 | 46 | 2116 |  | 3.0407 | 46 | 2116
4.9899 | 45 | 2025 |  | 3.0407 | 45 | 2025
4.9899 | 58 | 3364 |  | 3.0407 | 58 | 3364
4.9899 | 49 | 2401 |  | 3.0407 | 49 | 2401
4.9918 | 44 | 1936 |  | 3.0425 | 44 | 1936
4.9918 | 45 | 2025 |  | 3.0425 | 45 | 2025
4.9928 | 44 | 1936 |  | 3.0435 | 44 | 1936
4.9928 | 52 | 2704 |  | 3.0435 | 52 | 2704
4.9928 | 49 | 2401 |  | 3.0435 | 49 | 2401
4.9938 | 50 | 2500 |  | 3.0444 | 50 | 2500
4.9947 | 49 | 2401 |  | 3.0454 | 49 | 2401
4.9947 | 51 | 2601 |  | 3.0454 | 51 | 2601
4.9947 | 51 | 2601 |  | 3.0454 | 51 | 2601
4.9947 | 55 | 3025 |  | 3.0454 | 55 | 3025
4.9947 | 64 | 4096 |  | 3.0454 | 64 | 4096
4.9956 | 53 | 2809 |  | 3.0463 | 53 | 2809
4.9976 | 54 | 2916 |  | 3.0482 | 54 | 2916
4.9976 | 62 | 3844 |  | 3.0482 | 62 | 3844
4.9985 | 46 | 2116 |  | 3.0492 | 46 | 2116
5.0004 | 45 | 2025 |  | 3.0511 | 45 | 2025
5.0004 | 52 | 2704 |  | 3.0511 | 52 | 2704
5.0004 | 52 | 2704 |  | 3.0511 | 52 | 2704
5.0004 | 55 | 3025 |  | 3.0511 | 55 | 3025
5.0014 | 50 | 2500 |  | 3.0521 | 50 | 2500
5.0024 | 59 | 3481 |  | 3.053 | 59 | 3481
5.0024 | 55 | 3025 |  | 3.053 | 55 | 3025
5.0033 | 51 | 2601 |  | 3.054 | 51 | 2601
5.0033 | 49 | 2401 |  | 3.054 | 49 | 2401
5.0033 | 47 | 2209 |  | 3.054 | 47 | 2209
5.0043 | 55 | 3025 |  | 3.055 | 55 | 3025
5.0062 | 56 | 3136 |  | 3.0569 | 56 | 3136
5.0062 | 46 | 2116 |  | 3.0569 | 46 | 2116
5.0062 | 47 | 2209 |  | 3.0569 | 47 | 2209
5.0071 | 47 | 2209 |  | 3.0578 | 47 | 2209
5.0071 | 51 | 2601 |  | 3.0578 | 51 | 2601
5.0071 | 50 | 2500 |  | 3.0578 | 50 | 2500
5.0081 | 30 | 900 |  | 3.0588 | 30 | 900
5.0081 | 59 | 3481 |  | 3.0588 | 59 | 3481
5.0081 | 46 | 2116 |  | 3.0588 | 46 | 2116
5.0091 | 58 | 3364 |  | 3.0598 | 58 | 3364
5.0091 | 52 | 2704 |  | 3.0598 | 52 | 2704
5.0091 | 52 | 2704 |  | 3.0598 | 52 | 2704
5.0091 | 50 | 2500 |  | 3.0598 | 50 | 2500
5.0091 | 49 | 2401 |  | 3.0598 | 49 | 2401
5.01 | 43 | 1849 |  | 3.0607 | 43 | 1849
5.0109 | 54 | 2916 |  | 3.0617 | 54 | 2916
5.0109 | 49 | 2401 |  | 3.0617 | 49 | 2401
5.0109 | 47 | 2209 |  | 3.0617 | 47 | 2209
5.0109 | 60 | 3600 |  | 3.0617 | 60 | 3600
5.012 | 57 | 3249 |  | 3.0627 | 57 | 3249
5.012 | 51 | 2601 |  | 3.0627 | 51 | 2601
5.012 | 50 | 2500 |  | 3.0627 | 50 | 2500
5.0129 | 47 | 2209 |  | 3.0637 | 47 | 2209
5.0129 | 55 | 3025 |  | 3.0637 | 55 | 3025
5.0138 | 23 | 529 |  | 3.0646 | 23 | 529
5.0138 | 28 | 784 |  | 3.0646 | 28 | 784
5.0138 | 44 | 1936 |  | 3.0646 | 44 | 1936
5.0148 | 56 | 3136 |  | 3.0656 | 56 | 3136
5.0148 | 53 | 2809 |  | 3.0656 | 53 | 2809
5.0158 | 47 | 2209 |  | 3.0666 | 47 | 2209
5.0158 | 43 | 1849 |  | 3.0666 | 43 | 1849
5.0158 | 51 | 2601 |  | 3.0666 | 51 | 2601
5.0158 | 46 | 2116 |  | 3.0666 | 46 | 2116
5.0158 | 60 | 3600 |  | 3.0666 | 60 | 3600
5.0158 | 58 | 3364 |  | 3.0666 | 58 | 3364
5.0167 | 50 | 2500 |  | 3.0676 | 50 | 2500
5.0167 | 51 | 2601 |  | 3.0676 | 51 | 2601
5.0176 | 50 | 2500 |  | 3.0685 | 50 | 2500
5.0176 | 52 | 2704 |  | 3.0685 | 52 | 2704
5.0176 | 63 | 3969 |  | 3.0685 | 63 | 3969
5.0186 | 46 | 2116 |  | 3.0695 | 46 | 2116
5.0196 | 50 | 2500 |  | 3.0705 | 50 | 2500
5.0196 | 59 | 3481 |  | 3.0705 | 59 | 3481
5.0196 | 50 | 2500 |  | 3.0705 | 50 | 2500
5.0205 | 51 | 2601 |  | 3.0715 | 51 | 2601
5.0205 | 51 | 2601 |  | 3.0715 | 51 | 2601
5.0205 | 53 | 2809 |  | 3.0715 | 53 | 2809
5.0205 | 58 | 3364 |  | 3.0715 | 58 | 3364
5.0205 | 54 | 2916 |  | 3.0715 | 54 | 2916
5.0215 | 23 | 529 |  | 3.0725 | 23 | 529
5.0215 | 46 | 2116 |  | 3.0725 | 46 | 2116
5.0215 | 51 | 2601 |  | 3.0725 | 51 | 2601
5.0224 | 23 | 529 |  | 3.0734 | 23 | 529
5.0224 | 57 | 3249 |  | 3.0734 | 57 | 3249
5.0224 | 60 | 3600 |  | 3.0734 | 60 | 3600
5.0234 | 52 | 2704 |  | 3.0745 | 52 | 2704
5.0234 | 49 | 2401 |  | 3.0745 | 49 | 2401
5.0243 | 32 | 1024 |  | 3.0754 | 32 | 1024
5.0253 | 50 | 2500 |  | 3.0764 | 50 | 2500
5.0253 | 48 | 2304 |  | 3.0764 | 48 | 2304
5.0262 | 55 | 3025 |  | 3.0774 | 55 | 3025
5.0272 | 51 | 2601 |  | 3.0784 | 51 | 2601
5.0282 | 32 | 1024 |  | 3.0794 | 32 | 1024
5.0282 | 53 | 2809 |  | 3.0794 | 53 | 2809
5.0282 | 48 | 2304 |  | 3.0794 | 48 | 2304
5.0291 | 46 | 2116 |  | 3.0804 | 46 | 2116
5.0291 | 50 | 2500 |  | 3.0804 | 50 | 2500
5.0291 | 50 | 2500 |  | 3.0804 | 50 | 2500
5.0291 | 45 | 2025 |  | 3.0804 | 45 | 2025
5.0301 | 50 | 2500 |  | 3.0814 | 50 | 2500
5.0301 | 49 | 2401 |  | 3.0814 | 49 | 2401
5.0301 | 49 | 2401 |  | 3.0814 | 49 | 2401
5.032 | 53 | 2809 |  | 3.0834 | 53 | 2809
5.0329 | 56 | 3136 |  | 3.0844 | 56 | 3136
5.0329 | 52 | 2704 |  | 3.0844 | 52 | 2704
5.0329 | 64 | 4096 |  | 3.0844 | 64 | 4096
5.0329 | 59 | 3481 |  | 3.0844 | 59 | 3481
5.0339 | 52 | 2704 |  | 3.0855 | 52 | 2704
5.0348 | 58 | 3364 |  | 3.0864 | 58 | 3364
5.0358 | 45 | 2025 |  | 3.0874 | 45 | 2025
5.0358 | 53 | 2809 |  | 3.0874 | 53 | 2809
5.0367 | 60 | 3600 |  | 3.0884 | 60 | 3600
5.0367 | 54 | 2916 |  | 3.0884 | 54 | 2916
5.0377 | 53 | 2809 |  | 3.0895 | 53 | 2809
5.0386 | 51 | 2601 |  | 3.0905 | 51 | 2601
5.0386 | 51 | 2601 |  | 3.0905 | 51 | 2601
5.0396 | 52 | 2704 |  | 3.0915 | 52 | 2704
5.0405 | 59 | 3481 |  | 3.0925 | 59 | 3481
5.0415 | 50 | 2500 |  | 3.0935 | 50 | 2500
5.0415 | 55 | 3025 |  | 3.0935 | 55 | 3025
5.0415 | 45 | 2025 |  | 3.0935 | 45 | 2025
5.0415 | 45 | 2025 |  | 3.0935 | 45 | 2025
5.0415 | 50 | 2500 |  | 3.0935 | 50 | 2500
5.0424 | 23 | 529 |  | 3.0945 | 23 | 529
5.0424 | 44 | 1936 |  | 3.0945 | 44 | 1936
5.0424 | 55 | 3025 |  | 3.0945 | 55 | 3025
5.0434 | 31 | 961 |  | 3.0955 | 31 | 961
5.0443 | 47 | 2209 |  | 3.0965 | 47 | 2209
5.0443 | 52 | 2704 |  | 3.0965 | 52 | 2704
5.0453 | 57 | 3249 |  | 3.0976 | 57 | 3249
5.0453 | 53 | 2809 |  | 3.0976 | 53 | 2809
5.0462 | 50 | 2500 |  | 3.0986 | 50 | 2500
5.0472 | 52 | 2704 |  | 3.0996 | 52 | 2704
5.0491 | 56 | 3136 |  | 3.1017 | 56 | 3136
5.05 | 50 | 2500 |  | 3.1027 | 50 | 2500
5.0519 | 52 | 2704 |  | 3.1047 | 52 | 2704
5.0519 | 67 | 4489 |  | 3.1047 | 67 | 4489
5.0538 | 37 | 1369 |  | 3.1068 | 37 | 1369
5.0538 | 51 | 2601 |  | 3.1068 | 51 | 2601
5.0548 | 52 | 2704 |  | 3.1079 | 52 | 2704
5.0558 | 60 | 3600 |  | 3.1089 | 60 | 3600
5.0586 | 42 | 1764 |  | 3.112 | 42 | 1764
5.0596 | 23 | 529 |  | 3.1131 | 23 | 529
5.0596 | 36 | 1296 |  | 3.1131 | 36 | 1296
5.0596 | 44 | 1936 |  | 3.1131 | 44 | 1936
5.0614 | 51 | 2601 |  | 3.1152 | 51 | 2601
5.0624 | 47 | 2209 |  | 3.1162 | 47 | 2209
5.0643 | 51 | 2601 |  | 3.1183 | 51 | 2601
5.0662 | 46 | 2116 |  | 3.1204 | 46 | 2116
5.0672 | 49 | 2401 |  | 3.1215 | 49 | 2401
5.0681 | 45 | 2025 |  | 3.1225 | 45 | 2025
5.0681 | 51 | 2601 |  | 3.1225 | 51 | 2601
5.0681 | 50 | 2500 |  | 3.1225 | 50 | 2500
5.0681 | 51 | 2601 |  | 3.1225 | 51 | 2601
5.0719 | 70 | 4900 |  | 3.1268 | 70 | 4900
5.0728 | 45 | 2025 |  | 3.1278 | 45 | 2025
5.0737 | 56 | 3136 |  | 3.1289 | 56 | 3136
5.0757 | 55 | 3025 |  | 3.131 | 55 | 3025
5.0766 | 44 | 1936 |  | 3.1321 | 44 | 1936
5.0766 | 50 | 2500 |  | 3.1321 | 50 | 2500
5.0785 | 26 | 676 |  | 3.1343 | 26 | 676
5.0785 | 52 | 2704 |  | 3.1343 | 52 | 2704
5.0785 | 49 | 2401 |  | 3.1343 | 49 | 2401
5.0794 | 28 | 784 |  | 3.1353 | 28 | 784
5.0794 | 42 | 1764 |  | 3.1353 | 42 | 1764
5.0794 | 42 | 1764 |  | 3.1353 | 42 | 1764
5.0842 | 46 | 2116 |  | 3.1407 | 46 | 2116
5.0861 | 50 | 2500 |  | 3.1429 | 50 | 2500
5.087 | 30 | 900 |  | 3.144 | 30 | 900
5.087 | 50 | 2500 |  | 3.144 | 50 | 2500
5.087 | 45 | 2025 |  | 3.144 | 45 | 2025
5.0879 | 34 | 1156 |  | 3.145 | 34 | 1156
5.0879 | 47 | 2209 |  | 3.145 | 47 | 2209
5.0908 | 43 | 1849 |  | 3.1483 | 43 | 1849
5.0908 | 52 | 2704 |  | 3.1483 | 52 | 2704
5.0917 | 36 | 1296 |  | 3.1494 | 36 | 1296
5.0917 | 51 | 2601 |  | 3.1494 | 51 | 2601
5.0917 | 54 | 2916 |  | 3.1494 | 54 | 2916
5.0936 | 55 | 3025 |  | 3.1516 | 55 | 3025
5.0946 | 45 | 2025 |  | 3.1527 | 45 | 2025
5.0946 | 58 | 3364 |  | 3.1527 | 58 | 3364
5.0955 | 47 | 2209 |  | 3.1538 | 47 | 2209
5.0955 | 52 | 2704 |  | 3.1538 | 52 | 2704
5.0965 | 42 | 1764 |  | 3.1549 | 42 | 1764
5.0965 | 51 | 2601 |  | 3.1549 | 51 | 2601
5.0974 | 45 | 2025 |  | 3.156 | 45 | 2025
5.0983 | 51 | 2601 |  | 3.1571 | 51 | 2601
5.0993 | 46 | 2116 |  | 3.1582 | 46 | 2116
5.0993 | 44 | 1936 |  | 3.1582 | 44 | 1936
5.103 | 58 | 3364 |  | 3.1626 | 58 | 3364
5.104 | 56 | 3136 |  | 3.1638 | 56 | 3136
5.1049 | 51 | 2601 |  | 3.1649 | 51 | 2601
5.1106 | 47 | 2209 |  | 3.1717 | 47 | 2209
5.1106 | 56 | 3136 |  | 3.1717 | 56 | 3136
5.1125 | 49 | 2401 |  | 3.1739 | 49 | 2401
5.1144 | 45 | 2025 |  | 3.1762 | 45 | 2025
5.1144 | 46 | 2116 |  | 3.1762 | 46 | 2116
5.1144 | 54 | 2916 |  | 3.1762 | 54 | 2916
5.1191 | 40 | 1600 |  | 3.1818 | 40 | 1600
5.1191 | 50 | 2500 |  | 3.1818 | 50 | 2500
5.1219 | 41 | 1681 |  | 3.1853 | 41 | 1681
5.1219 | 40 | 1600 |  | 3.1853 | 40 | 1600
5.1219 | 52 | 2704 |  | 3.1853 | 52 | 2704
5.1219 | 51 | 2601 |  | 3.1853 | 51 | 2601
5.1228 | 55 | 3025 |  | 3.1864 | 55 | 3025
5.1238 | 49 | 2401 |  | 3.1875 | 49 | 2401
5.1284 | 57 | 3249 |  | 3.1932 | 57 | 3249
5.1304 | 24 | 576 |  | 3.1956 | 24 | 576
5.1304 | 50 | 2500 |  | 3.1956 | 50 | 2500
5.1322 | 47 | 2209 |  | 3.1979 | 47 | 2209
5.135 | 42 | 1764 |  | 3.2014 | 42 | 1764
5.1388 | 48 | 2304 |  | 3.2061 | 48 | 2304
5.1388 | 49 | 2401 |  | 3.2061 | 49 | 2401
5.1453 | 45 | 2025 |  | 3.2143 | 45 | 2025
5.151 | 43 | 1849 |  | 3.2215 | 43 | 1849
5.1547 | 53 | 2809 |  | 3.2263 | 53 | 2809
5.1603 | 45 | 2025 |  | 3.2335 | 45 | 2025
5.1622 | 53 | 2809 |  | 3.2359 | 53 | 2809
5.1688 | 66 | 4356 |  | 3.2445 | 66 | 4356
5.1715 | 40 | 1600 |  | 3.2481 | 40 | 1600
5.1743 | 42 | 1764 |  | 3.2518 | 42 | 1764
5.1771 | 42 | 1764 |  | 3.2556 | 42 | 1764
5.1837 | 41 | 1681 |  | 3.2643 | 41 | 1681
5.1911 | 73 | 5329 |  | 3.2744 | 73 | 5329
5.1948 | 54 | 2916 |  | 3.2794 | 54 | 2916
5.2705 | 48 | 2304 |  | 3.3899 | 48 | 2304
5.3226 | 72 | 5184 |  | 3.4743 | 72 | 5184
5.4092 | 81 | 6561 |  | 3.6319 | 81 | 6561
5.6591 | 72 | 5184 |  | 4.0959 | 44 | 1936
5.7635 | 66 | 4356 |  | 4.0959 | 46 | 2116
6.0663 | 77 | 5929 |  | 4.0959 | 49 | 2401
6.1446 | 47 | 2209 |  | 4.0959 | 49 | 2401
6.2229 | 42 | 1764 |  | 4.0959 | 48 | 2304
6.2393 | 79 | 6241 |  | 4.0959 | 48 | 2304
6.4743 | 37 | 1369 |  | 4.0959 | 48 | 2304
6.4801 | 73 | 5329 |  | 4.0959 | 46 | 2116
6.544 | 46 | 2116 |  | 4.0959 | 45 | 2025
6.731 | 76 | 5776 |  | 4.0959 | 43 | 1849
6.7462 | 45 | 2025 |  | 4.0959 | 42 | 1764
6.8727 | 65 | 4225 |  | 4.0959 | 37 | 1369
6.9225 | 60 | 3600 |  | 4.0959 | 37 | 1369
7.1334 | 68 | 4624 |  | 4.0959 | 37 | 1369
7.1507 | 72 | 5184 |  | 4.0959 | 37 | 1369
7.1532 | 84 | 7056 |  | 4.0959 | 41 | 1681
7.1545 | 76 | 5776 |  | 4.0959 | 45 | 2025
7.1591 | 73 | 5329 |  | 4.0959 | 47 | 2209
7.1595 | 75 | 5625 |  | 4.0959 | 51 | 2601
7.1603 | 75 | 5625 |  | 4.0959 | 53 | 2809
7.169 | 72 | 5184 |  | 4.0959 | 54 | 2916
7.1777 | 77 | 5929 |  | 4.0959 | 52 | 2704
7.1818 | 73 | 5329 |  | 4.0959 | 50 | 2500
7.1915 | 80 | 6400 |  | 4.0959 | 48 | 2304
7.1956 | 74 | 5476 |  | 4.0959 | 47 | 2209
7.2317 | 75 | 5625 |  | 4.0959 | 40 | 1600
7.2438 | 52 | 2704 |  | 4.0959 | 40 | 1600
7.3086 | 38 | 1444 |  | 4.0959 | 42 | 1764
7.3269 | 59 | 3481 |  | 4.0959 | 46 | 2116
7.3804 | 46 | 2116 |  | 4.0959 | 49 | 2401
7.5048 | 75 | 5625 |  | 4.0959 | 50 | 2500
7.6049 | 65 | 4225 |  | 4.0959 | 52 | 2704
7.6958 | 54 | 2916 |  | 4.0959 | 55 | 3025
7.7841 | 76 | 5776 |  | 4.0959 | 56 | 3136
7.7985 | 54 | 2916 |  | 4.0959 | 55 | 3025
7.8452 | 43 | 1849 |  | 4.0959 | 54 | 2916
7.8506 | 73 | 5329 |  | 4.0959 | 53 | 2809
7.898 | 50 | 2500 |  | 4.0959 | 45 | 2025
7.9093 | 91 | 8281 |  | 4.0959 | 44 | 1936
8.0279 | 47 | 2209 |  | 4.0959 | 47 | 2209
8.0566 | 44 | 1936 |  | 4.0959 | 56 | 3136
8.1323 | 68 | 4624 |  | 4.0959 | 58 | 3364
8.3996 | 64 | 4096 |  | 4.0959 | 60 | 3600
8.4223 | 49 | 2401 |  | 4.0959 | 62 | 3844
8.4296 | 57 | 3249 |  | 4.0959 | 60 | 3600
8.5305 | 41 | 1681 |  | 4.0959 | 58 | 3364
8.5391 | 47 | 2209 |  | 4.0959 | 55 | 3025
8.6689 | 53 | 2809 |  | 4.0959 | 54 | 2916
8.8533 | 50 | 2500 |  | 4.0959 | 54 | 2916
8.8652 | 78 | 6084 |  | 4.0959 | 50 | 2500
8.8919 | 50 | 2500 |  | 4.0959 | 47 | 2209
8.8932 | 48 | 2304 |  | 4.0959 | 47 | 2209
8.9074 | 79 | 6241 |  | 4.0959 | 47 | 2209
8.9237 | 50 | 2500 |  | 4.0959 | 48 | 2304
8.929 | 48 | 2304 |  | 4.0959 | 51 | 2601
8.9303 | 47 | 2209 |  | 4.0959 | 52 | 2704
8.9556 | 47 | 2209 |  | 4.0959 | 52 | 2704
8.9711 | 50 | 2500 |  | 4.0959 | 53 | 2809
9.0564 | 47 | 2209 |  | 4.0959 | 54 | 2916
9.0628 | 56 | 3136 |  | 4.0959 | 55 | 3025
9.1642 | 61 | 3721 |  | 4.0959 | 54 | 2916
9.1665 | 48 | 2304 |  | 4.0959 | 52 | 2704
9.1712 | 44 | 1936 |  | 4.0959 | 51 | 2601
9.2086 | 40 | 1600 |  | 4.0959 | 51 | 2601
9.411 | 31 | 961 |  | 4.0959 | 51 | 2601
9.4172 | 58 | 3364 |  | 4.0959 | 51 | 2601
9.4978 | 87 | 7569 |  | 4.0959 | 55 | 3025
9.7511 | 40 | 1600 |  | 4.0959 | 60 | 3600
9.7974 | 38 | 1444 |  | 4.0959 | 62 | 3844
9.8675 | 46 | 2116 |  | 4.0959 | 61 | 3721
9.8718 | 63 | 3969 |  | 4.0959 | 59 | 3481
9.9006 | 54 | 2916 |  | 4.0959 | 57 | 3249
10.1685 | 77 | 5929 |  | 4.0959 | 56 | 3136
10.2971 | 44 | 1936 |  | 4.0959 | 52 | 2704
10.3876 | 74 | 5476 |  | 4.0959 | 45 | 2025
11.4901 | 40 | 1600 |  | 4.0959 | 45 | 2025
11.5232 | 62 | 3844 |  | 4.0959 | 45 | 2025
11.5343 | 45 | 2025 |  | 4.0959 | 46 | 2116
11.5958 | 64 | 4096 |  | 4.0959 | 48 | 2304
11.8351 | 49 | 2401 |  | 4.0959 | 51 | 2601
11.9457 | 51 | 2601 |  | 4.0959 | 53 | 2809
12.0351 | 44 | 1936 |  | 4.0959 | 55 | 3025
12.0351 | 46 | 2116 |  | 4.0959 | 58 | 3364
12.0351 | 49 | 2401 |  | 4.0959 | 60 | 3600
12.0351 | 49 | 2401 |  | 4.0959 | 62 | 3844
12.0351 | 48 | 2304 |  | 4.0959 | 62 | 3844
12.0351 | 48 | 2304 |  | 4.0959 | 63 | 3969
12.0351 | 48 | 2304 |  | 4.0959 | 49 | 2401
12.0351 | 46 | 2116 |  | 4.0959 | 47 | 2209
12.0351 | 45 | 2025 |  | 4.0959 | 46 | 2116
12.0351 | 43 | 1849 |  | 4.0959 | 47 | 2209
12.0351 | 37 | 1369 |  | 4.0959 | 48 | 2304
12.0351 | 37 | 1369 |  | 4.0959 | 50 | 2500
12.0351 | 37 | 1369 |  | 4.0959 | 52 | 2704
12.0351 | 41 | 1681 |  | 4.0959 | 54 | 2916
12.0351 | 45 | 2025 |  | 4.0959 | 56 | 3136
12.0351 | 47 | 2209 |  | 4.0959 | 59 | 3481
12.0351 | 51 | 2601 |  | 4.0959 | 58 | 3364
12.0351 | 53 | 2809 |  | 4.0959 | 57 | 3249
12.0351 | 54 | 2916 |  | 4.0959 | 40 | 1600
12.0351 | 52 | 2704 |  | 4.0959 | 40 | 1600
12.0351 | 50 | 2500 |  | 4.0959 | 40 | 1600
12.0351 | 48 | 2304 |  | 4.0959 | 42 | 1764
12.0351 | 47 | 2209 |  | 4.0959 | 43 | 1849
12.0351 | 40 | 1600 |  | 4.0959 | 43 | 1849
12.0351 | 40 | 1600 |  | 4.0959 | 43 | 1849
12.0351 | 42 | 1764 |  | 4.0959 | 45 | 2025
12.0351 | 46 | 2116 |  | 4.0959 | 45 | 2025
12.0351 | 49 | 2401 |  | 4.0959 | 43 | 1849
12.0351 | 50 | 2500 |  | 4.0959 | 42 | 1764
12.0351 | 52 | 2704 |  | 4.0959 | 41 | 1681
12.0351 | 55 | 3025 |  | 4.0959 | 44 | 1936
12.0351 | 56 | 3136 |  | 4.0959 | 44 | 1936
12.0351 | 55 | 3025 |  | 4.0959 | 45 | 2025
12.0351 | 54 | 2916 |  | 4.0959 | 45 | 2025
12.0351 | 53 | 2809 |  | 4.0959 | 46 | 2116
12.0351 | 44 | 1936 |  | 4.0959 | 47 | 2209
12.0351 | 47 | 2209 |  | 4.0959 | 46 | 2116
12.0351 | 56 | 3136 |  | 4.0959 | 45 | 2025
12.0351 | 58 | 3364 |  | 4.0959 | 45 | 2025
12.0351 | 60 | 3600 |  | 4.0959 | 45 | 2025
12.0351 | 62 | 3844 |  | 4.0959 | 46 | 2116
12.0351 | 60 | 3600 |  | 4.0959 | 46 | 2116
12.0351 | 58 | 3364 |  | 4.0959 | 47 | 2209
12.0351 | 55 | 3025 |  | 4.0959 | 49 | 2401
12.0351 | 54 | 2916 |  | 4.0959 | 49 | 2401
12.0351 | 50 | 2500 |  | 4.0959 | 49 | 2401
12.0351 | 47 | 2209 |  | 4.0959 | 51 | 2601
12.0351 | 47 | 2209 |  | 4.0959 | 55 | 3025
12.0351 | 47 | 2209 |  | 4.0959 | 55 | 3025
12.0351 | 48 | 2304 |  | 4.0959 | 54 | 2916
12.0351 | 51 | 2601 |  | 4.0959 | 57 | 3249
12.0351 | 52 | 2704 |  | 4.0959 | 56 | 3136
12.0351 | 52 | 2704 |  | 4.0959 | 23 | 529
12.0351 | 53 | 2809 |  | 4.0959 | 23 | 529
12.0351 | 54 | 2916 |  | 4.0959 | 25 | 625
12.0351 | 55 | 3025 |  | 4.0959 | 26 | 676
12.0351 | 52 | 2704 |  | 4.0959 | 28 | 784
12.0351 | 51 | 2601 |  | 4.0959 | 31 | 961
12.0351 | 51 | 2601 |  | 4.0959 | 32 | 1024
12.0351 | 51 | 2601 |  | 4.0959 | 32 | 1024
12.0351 | 51 | 2601 |  | 4.0959 | 33 | 1089
12.0351 | 55 | 3025 |  | 4.0959 | 32 | 1024
12.0351 | 60 | 3600 |  | 4.0959 | 32 | 1024
12.0351 | 62 | 3844 |  | 4.0959 | 31 | 961
12.0351 | 61 | 3721 |  | 4.0959 | 25 | 625
12.0351 | 59 | 3481 |  | 4.0959 | 25 | 625
12.0351 | 57 | 3249 |  | 4.0959 | 27 | 729
12.0351 | 56 | 3136 |  | 4.0959 | 29 | 841
12.0351 | 45 | 2025 |  | 4.0959 | 31 | 961
12.0351 | 45 | 2025 |  | 4.0959 | 34 | 1156
12.0351 | 46 | 2116 |  | 4.0959 | 36 | 1296
12.0351 | 48 | 2304 |  | 4.0959 | 36 | 1296
12.0351 | 51 | 2601 |  | 4.0959 | 37 | 1369
12.0351 | 53 | 2809 |  | 4.0959 | 35 | 1225
12.0351 | 55 | 3025 |  | 4.0959 | 37 | 1369
12.0351 | 58 | 3364 |  | 4.0959 | 38 | 1444
12.0351 | 60 | 3600 |  | 4.0959 | 38 | 1444
12.0351 | 62 | 3844 |  | 4.0959 | 29 | 841
12.0351 | 62 | 3844 |  | 4.0959 | 29 | 841
12.0351 | 63 | 3969 |  | 4.0959 | 32 | 1024
12.0351 | 49 | 2401 |  | 4.0959 | 35 | 1225
12.0351 | 47 | 2209 |  | 4.0959 | 37 | 1369
12.0351 | 46 | 2116 |  | 4.0959 | 39 | 1521
12.0351 | 47 | 2209 |  | 4.0959 | 40 | 1600
12.0351 | 48 | 2304 |  | 4.0959 | 40 | 1600
12.0351 | 50 | 2500 |  | 4.0959 | 42 | 1764
12.0351 | 52 | 2704 |  | 4.0959 | 41 | 1681
12.0351 | 54 | 2916 |  | 4.0959 | 42 | 1764
12.0351 | 56 | 3136 |  | 4.0959 | 41 | 1681
12.0351 | 59 | 3481 |  | 4.0959 | 41 | 1681
12.0351 | 58 | 3364 |  | 4.0959 | 40 | 1600
12.0351 | 40 | 1600 |  | 4.0959 | 41 | 1681
12.0351 | 40 | 1600 |  | 4.0959 | 47 | 2209
12.0351 | 42 | 1764 |  | 4.0959 | 47 | 2209
12.0351 | 43 | 1849 |  | 4.0959 | 48 | 2304
12.0351 | 43 | 1849 |  | 4.0959 | 52 | 2704
12.0351 | 43 | 1849 |  | 4.0959 | 56 | 3136
12.0351 | 45 | 2025 |  | 4.0959 | 54 | 2916
12.0351 | 45 | 2025 |  | 4.0959 | 55 | 3025
12.0351 | 43 | 1849 |  | 4.0959 | 54 | 2916
12.0351 | 42 | 1764 |  | 4.0959 | 55 | 3025
12.0351 | 41 | 1681 |  | 4.0959 | 54 | 2916
12.0351 | 44 | 1936 |  | 4.0959 | 54 | 2916
12.0351 | 45 | 2025 |  | 4.0959 | 53 | 2809
12.0351 | 45 | 2025 |  | 4.0959 | 39 | 1521
12.0351 | 46 | 2116 |  | 4.0959 | 40 | 1600
12.0351 | 47 | 2209 |  | 4.0959 | 43 | 1849
12.0351 | 46 | 2116 |  | 4.0959 | 45 | 2025
12.0351 | 45 | 2025 |  | 4.0959 | 47 | 2209
12.0351 | 45 | 2025 |  | 4.0959 | 50 | 2500
12.0351 | 45 | 2025 |  | 4.0959 | 51 | 2601
12.0351 | 46 | 2116 |  | 4.0959 | 52 | 2704
12.0351 | 49 | 2401 |  | 4.0959 | 53 | 2809
12.0351 | 49 | 2401 |  | 4.0959 | 54 | 2916
12.0351 | 49 | 2401 |  | 4.0959 | 54 | 2916
12.0351 | 51 | 2601 |  | 4.0959 | 43 | 1849
12.0351 | 55 | 3025 |  | 4.0959 | 42 | 1764
12.0351 | 55 | 3025 |  | 4.0959 | 45 | 2025
12.0351 | 54 | 2916 |  | 4.0959 | 46 | 2116
12.0351 | 57 | 3249 |  | 4.0959 | 50 | 2500
12.0351 | 23 | 529 |  | 4.0959 | 51 | 2601
12.0351 | 23 | 529 |  | 4.0959 | 52 | 2704
12.0351 | 25 | 625 |  | 4.0959 | 52 | 2704
12.0351 | 26 | 676 |  | 4.0959 | 51 | 2601
12.0351 | 28 | 784 |  | 4.0959 | 51 | 2601
12.0351 | 31 | 961 |  | 4.0959 | 51 | 2601
12.0351 | 32 | 1024 |  | 4.0959 | 49 | 2401
12.0351 | 32 | 1024 |  | 4.0959 | 50 | 2500
12.0351 | 33 | 1089 |  | 4.0959 | 48 | 2304
12.0351 | 32 | 1024 |  | 4.0959 | 48 | 2304
12.0351 | 32 | 1024 |  | 4.0959 | 47 | 2209
12.0351 | 25 | 625 |  | 4.0959 | 49 | 2401
12.0351 | 25 | 625 |  | 4.0959 | 50 | 2500
12.0351 | 27 | 729 |  | 4.0959 | 52 | 2704
12.0351 | 29 | 841 |  | 4.0959 | 51 | 2601
12.0351 | 31 | 961 |  | 4.0959 | 51 | 2601
12.0351 | 34 | 1156 |  | 4.0959 | 53 | 2809
12.0351 | 36 | 1296 |  | 4.0959 | 46 | 2116
12.0351 | 36 | 1296 |  | 4.0959 | 45 | 2025
12.0351 | 37 | 1369 |  | 4.0959 | 46 | 2116
12.0351 | 35 | 1225 |  | 4.0959 | 46 | 2116
12.0351 | 37 | 1369 |  | 4.0959 | 46 | 2116
12.0351 | 38 | 1444 |  | 4.0959 | 46 | 2116
12.0351 | 29 | 841 |  | 4.0959 | 47 | 2209
12.0351 | 29 | 841 |  | 4.0959 | 48 | 2304
12.0351 | 32 | 1024 |  | 4.0959 | 49 | 2401
12.0351 | 35 | 1225 |  | 4.0959 | 50 | 2500
12.0351 | 37 | 1369 |  | 4.0959 | 50 | 2500
12.0351 | 39 | 1521 |  | 4.0959 | 50 | 2500
12.0351 | 40 | 1600 |  | 4.0959 | 52 | 2704
12.0351 | 40 | 1600 |  | 4.0959 | 54 | 2916
12.0351 | 42 | 1764 |  | 4.0959 | 57 | 3249
12.0351 | 41 | 1681 |  | 4.0959 | 59 | 3481
12.0351 | 42 | 1764 |  | 4.0959 | 59 | 3481
12.0351 | 41 | 1681 |  | 4.0959 | 61 | 3721
12.0351 | 41 | 1681 |  | 4.0959 | 61 | 3721
12.0351 | 40 | 1600 |  | 4.0959 | 63 | 3969
12.0351 | 47 | 2209 |  | 4.0959 | 58 | 3364
12.0351 | 47 | 2209 |  | 4.0959 | 40 | 1600
12.0351 | 48 | 2304 |  | 4.0959 | 41 | 1681
12.0351 | 52 | 2704 |  | 4.0959 | 44 | 1936
12.0351 | 56 | 3136 |  | 4.0959 | 46 | 2116
12.0351 | 54 | 2916 |  | 4.0959 | 48 | 2304
12.0351 | 55 | 3025 |  | 4.0959 | 50 | 2500
12.0351 | 54 | 2916 |  | 4.0959 | 51 | 2601
12.0351 | 55 | 3025 |  | 4.0959 | 52 | 2704
12.0351 | 54 | 2916 |  | 4.0959 | 54 | 2916
12.0351 | 54 | 2916 |  | 4.0959 | 53 | 2809
12.0351 | 39 | 1521 |  | 4.0959 | 53 | 2809
12.0351 | 40 | 1600 |  | 4.0959 | 49 | 2401
12.0351 | 43 | 1849 |  | 4.0959 | 38 | 1444
12.0351 | 45 | 2025 |  | 4.0959 | 40 | 1600
12.0351 | 47 | 2209 |  | 4.0959 | 44 | 1936
12.0351 | 50 | 2500 |  | 4.0959 | 47 | 2209
12.0351 | 51 | 2601 |  | 4.0959 | 50 | 2500
12.0351 | 52 | 2704 |  | 4.0959 | 50 | 2500
12.0351 | 53 | 2809 |  | 4.0959 | 50 | 2500
12.0351 | 54 | 2916 |  | 4.0959 | 50 | 2500
12.0351 | 54 | 2916 |  | 4.0959 | 48 | 2304
12.0351 | 43 | 1849 |  | 4.0959 | 48 | 2304
12.0351 | 42 | 1764 |  | 4.0959 | 47 | 2209
12.0351 | 45 | 2025 |  | 4.0959 | 47 | 2209
12.0351 | 46 | 2116 |  | 4.0959 | 44 | 1936
12.0351 | 50 | 2500 |  | 4.0959 | 41 | 1681
12.0351 | 51 | 2601 |  | 4.0959 | 43 | 1849
12.0351 | 52 | 2704 |  | 4.0959 | 43 | 1849
12.0351 | 52 | 2704 |  | 4.0959 | 45 | 2025
12.0351 | 51 | 2601 |  | 4.0959 | 45 | 2025
12.0351 | 51 | 2601 |  | 4.0959 | 46 | 2116
12.0351 | 51 | 2601 |  | 4.0959 | 48 | 2304
12.0351 | 49 | 2401 |  | 4.0959 | 49 | 2401
12.0351 | 50 | 2500 |  | 4.0959 | 50 | 2500
12.0351 | 48 | 2304 |  | 4.0959 | 50 | 2500
12.0351 | 48 | 2304 |  | 4.0959 | 51 | 2601
12.0351 | 49 | 2401 |  | 4.0959 | 50 | 2500
12.0351 | 50 | 2500 |  | 4.0959 | 41 | 1681
12.0351 | 52 | 2704 |  | 4.0959 | 43 | 1849
12.0351 | 51 | 2601 |  | 4.0959 | 45 | 2025
12.0351 | 51 | 2601 |  | 4.0959 | 48 | 2304
12.0351 | 53 | 2809 |  | 4.0959 | 50 | 2500
12.0351 | 45 | 2025 |  | 4.0959 | 51 | 2601
12.0351 | 46 | 2116 |  | 4.0959 | 54 | 2916
12.0351 | 46 | 2116 |  | 4.0959 | 55 | 3025
12.0351 | 46 | 2116 |  | 4.0959 | 56 | 3136
12.0351 | 47 | 2209 |  | 4.0959 | 57 | 3249
12.0351 | 50 | 2500 |  | 4.0959 | 59 | 3481
12.0351 | 50 | 2500 |  | 4.0959 | 58 | 3364
12.0351 | 52 | 2704 |  | 4.0959 | 51 | 2601
12.0351 | 54 | 2916 |  | 4.0959 | 43 | 1849
12.0351 | 57 | 3249 |  | 4.0959 | 45 | 2025
12.0351 | 59 | 3481 |  | 4.0959 | 48 | 2304
12.0351 | 59 | 3481 |  | 4.0959 | 51 | 2601
12.0351 | 61 | 3721 |  | 4.0959 | 52 | 2704
12.0351 | 61 | 3721 |  | 4.0959 | 53 | 2809
12.0351 | 63 | 3969 |  | 4.0959 | 55 | 3025
12.0351 | 41 | 1681 |  | 4.0959 | 54 | 2916
12.0351 | 44 | 1936 |  | 4.0959 | 55 | 3025
12.0351 | 46 | 2116 |  | 4.0959 | 53 | 2809
12.0351 | 48 | 2304 |  | 4.0959 | 51 | 2601
12.0351 | 50 | 2500 |  | 4.0959 | 51 | 2601
12.0351 | 51 | 2601 |  | 4.0959 | 50 | 2500
12.0351 | 52 | 2704 |  | 4.0959 | 48 | 2304
12.0351 | 54 | 2916 |  | 4.0959 | 51 | 2601
12.0351 | 53 | 2809 |  | 4.0959 | 57 | 3249
12.0351 | 53 | 2809 |  | 4.0959 | 61 | 3721
12.0351 | 41 | 1681 |  | 4.0959 | 63 | 3969
12.0351 | 43 | 1849 |  | 4.0959 | 65 | 4225
12.0351 | 43 | 1849 |  | 4.0959 | 66 | 4356
12.0351 | 45 | 2025 |  | 4.0959 | 68 | 4624
12.0351 | 45 | 2025 |  | 4.0959 | 69 | 4761
12.0351 | 46 | 2116 |  | 4.0959 | 69 | 4761
12.0351 | 48 | 2304 |  | 4.0959 | 69 | 4761
12.0351 | 49 | 2401 |  | 4.0959 | 69 | 4761
12.0351 | 50 | 2500 |  | 4.0959 | 68 | 4624
12.0351 | 50 | 2500 |  | 4.0959 | 44 | 1936
12.0351 | 51 | 2601 |  | 4.0959 | 46 | 2116
12.0351 | 50 | 2500 |  | 4.0959 | 49 | 2401
12.0351 | 41 | 1681 |  | 4.0959 | 52 | 2704
12.0351 | 43 | 1849 |  | 4.0959 | 54 | 2916
12.0351 | 45 | 2025 |  | 4.0959 | 55 | 3025
12.0351 | 48 | 2304 |  | 4.0959 | 54 | 2916
12.0351 | 50 | 2500 |  | 4.0959 | 54 | 2916
12.0351 | 51 | 2601 |  | 4.0959 | 54 | 2916
12.0351 | 54 | 2916 |  | 4.0959 | 54 | 2916
12.0351 | 55 | 3025 |  | 4.0959 | 53 | 2809
12.0351 | 56 | 3136 |  | 4.0959 | 54 | 2916
12.0351 | 57 | 3249 |  | 4.0959 | 40 | 1600
12.0351 | 59 | 3481 |  | 4.0959 | 41 | 1681
12.0351 | 58 | 3364 |  | 4.0959 | 43 | 1849
12.0351 | 45 | 2025 |  | 4.0959 | 44 | 1936
12.0351 | 48 | 2304 |  | 4.0959 | 47 | 2209
12.0351 | 51 | 2601 |  | 4.0959 | 50 | 2500
12.0351 | 52 | 2704 |  | 4.0959 | 52 | 2704
12.0351 | 53 | 2809 |  | 4.0959 | 54 | 2916
12.0351 | 55 | 3025 |  | 4.0959 | 57 | 3249
12.0351 | 54 | 2916 |  | 4.0959 | 57 | 3249
12.0351 | 55 | 3025 |  | 4.0959 | 57 | 3249
12.0351 | 53 | 2809 |  | 4.0959 | 57 | 3249
12.0351 | 51 | 2601 |  | 4.0959 | 56 | 3136
12.0351 | 51 | 2601 |  | 4.0959 | 54 | 2916
12.0351 | 50 | 2500 |  | 4.0959 | 42 | 1764
12.0351 | 48 | 2304 |  | 4.0959 | 43 | 1849
12.0351 | 51 | 2601 |  | 4.0959 | 45 | 2025
12.0351 | 57 | 3249 |  | 4.0959 | 47 | 2209
12.0351 | 61 | 3721 |  | 4.0959 | 50 | 2500
12.0351 | 63 | 3969 |  | 4.0959 | 52 | 2704
12.0351 | 65 | 4225 |  | 4.0959 | 56 | 3136
12.0351 | 66 | 4356 |  | 4.0959 | 59 | 3481
12.0351 | 68 | 4624 |  | 4.0959 | 60 | 3600
12.0351 | 69 | 4761 |  | 4.0959 | 62 | 3844
12.0351 | 69 | 4761 |  | 4.0959 | 63 | 3969
12.0351 | 69 | 4761 |  | 4.0959 | 63 | 3969
12.0351 | 69 | 4761 |  | 4.0959 | 47 | 2209
12.0351 | 44 | 1936 |  | 4.0959 | 50 | 2500
12.0351 | 46 | 2116 |  | 4.0959 | 53 | 2809
12.0351 | 49 | 2401 |  | 4.0959 | 56 | 3136
12.0351 | 52 | 2704 |  | 4.0959 | 59 | 3481
12.0351 | 54 | 2916 |  | 4.0959 | 62 | 3844
12.0351 | 55 | 3025 |  | 4.0959 | 64 | 4096
12.0351 | 54 | 2916 |  | 4.0959 | 66 | 4356
12.0351 | 54 | 2916 |  | 4.0959 | 68 | 4624
12.0351 | 54 | 2916 |  | 4.0959 | 69 | 4761
12.0351 | 54 | 2916 |  | 4.0959 | 70 | 4900
12.0351 | 53 | 2809 |  | 4.0959 | 68 | 4624
12.0351 | 54 | 2916 |  | 4.0959 | 61 | 3721
12.0351 | 40 | 1600 |  | 4.0959 | 57 | 3249
12.0351 | 41 | 1681 |  | 4.0959 | 57 | 3249
12.0351 | 43 | 1849 |  | 4.0959 | 61 | 3721
12.0351 | 44 | 1936 |  | 4.0959 | 64 | 4096
12.0351 | 47 | 2209 |  | 4.0959 | 62 | 3844
12.0351 | 50 | 2500 |  | 4.0959 | 66 | 4356
12.0351 | 52 | 2704 |  | 4.0959 | 70 | 4900
12.0351 | 54 | 2916 |  | 4.0959 | 69 | 4761
12.0351 | 57 | 3249 |  | 4.0959 | 68 | 4624
12.0351 | 57 | 3249 |  | 4.0959 | 68 | 4624
12.0351 | 57 | 3249 |  | 4.0959 | 68 | 4624
12.0351 | 57 | 3249 |  | 4.0959 | 65 | 4225
12.0351 | 56 | 3136 |  | 4.0959 | 63 | 3969
12.0351 | 42 | 1764 |  | 4.0959 | 63 | 3969
12.0351 | 43 | 1849 |  | 4.0959 | 61 | 3721
12.0351 | 45 | 2025 |  | 4.0959 | 67 | 4489
12.0351 | 47 | 2209 |  | 4.0959 | 66 | 4356
12.0351 | 50 | 2500 |  | 4.0959 | 69 | 4761
12.0351 | 52 | 2704 |  | 4.0959 | 68 | 4624
12.0351 | 56 | 3136 |  | 4.0959 | 67 | 4489
12.0351 | 59 | 3481 |  | 4.0959 | 64 | 4096
12.0351 | 60 | 3600 |  | 4.0959 | 63 | 3969
12.0351 | 62 | 3844 |  | 4.0959 | 64 | 4096
12.0351 | 63 | 3969 |  | 4.0959 | 57 | 3249
12.0351 | 50 | 2500 |  | 4.0959 | 60 | 3600
12.0351 | 53 | 2809 |  | 4.0959 | 62 | 3844
12.0351 | 56 | 3136 |  | 4.0959 | 63 | 3969
12.0351 | 59 | 3481 |  | 4.0959 | 67 | 4489
12.0351 | 62 | 3844 |  | 4.0959 | 69 | 4761
12.0351 | 64 | 4096 |  | 4.0959 | 71 | 5041
12.0351 | 66 | 4356 |  | 4.0959 | 77 | 5929
12.0351 | 68 | 4624 |  | 4.0959 | 77 | 5929
12.0351 | 69 | 4761 |  | 4.0959 | 78 | 6084
12.0351 | 70 | 4900 |  | 4.0959 | 77 | 5929
12.0351 | 57 | 3249 |  | 4.0959 | 76 | 5776
12.0351 | 57 | 3249 |  | 4.0959 | 77 | 5929
12.0351 | 61 | 3721 |  | 4.0959 | 56 | 3136
12.0351 | 64 | 4096 |  | 4.0959 | 57 | 3249
12.0351 | 62 | 3844 |  | 4.0959 | 60 | 3600
12.0351 | 66 | 4356 |  | 4.0959 | 63 | 3969
12.0351 | 70 | 4900 |  | 4.0959 | 63 | 3969
12.0351 | 69 | 4761 |  | 4.0959 | 65 | 4225
12.0351 | 68 | 4624 |  | 4.0959 | 66 | 4356
12.0351 | 68 | 4624 |  | 4.0959 | 68 | 4624
12.0351 | 68 | 4624 |  | 4.0959 | 68 | 4624
12.0351 | 63 | 3969 |  | 4.0959 | 70 | 4900
12.0351 | 63 | 3969 |  | 4.0959 | 54 | 2916
12.0351 | 61 | 3721 |  | 4.0959 | 54 | 2916
12.0351 | 67 | 4489 |  | 4.0959 | 54 | 2916
12.0351 | 66 | 4356 |  | 4.0959 | 54 | 2916
12.0351 | 69 | 4761 |  | 4.0959 | 55 | 3025
12.0351 | 68 | 4624 |  | 4.0959 | 55 | 3025
12.0351 | 67 | 4489 |  | 4.0959 | 56 | 3136
12.0351 | 64 | 4096 |  | 4.0959 | 56 | 3136
12.0351 | 63 | 3969 |  | 4.0959 | 58 | 3364
12.0351 | 64 | 4096 |  | 4.0959 | 59 | 3481
12.0351 | 57 | 3249 |  | 4.0959 | 60 | 3600
12.0351 | 60 | 3600 |  | 4.0959 | 61 | 3721
12.0351 | 62 | 3844 |  | 4.0959 | 53 | 2809
12.0351 | 63 | 3969 |  | 4.0959 | 56 | 3136
12.0351 | 67 | 4489 |  | 4.0959 | 59 | 3481
12.0351 | 69 | 4761 |  | 4.0959 | 61 | 3721
12.0351 | 71 | 5041 |  | 4.0959 | 63 | 3969
12.0351 | 77 | 5929 |  | 4.0959 | 67 | 4489
12.0351 | 77 | 5929 |  | 4.0959 | 65 | 4225
12.0351 | 78 | 6084 |  | 4.0959 | 59 | 3481
12.0351 | 77 | 5929 |  | 4.0959 | 61 | 3721
12.0351 | 76 | 5776 |  | 4.0959 | 66 | 4356
12.0351 | 56 | 3136 |  | 4.0959 | 63 | 3969
12.0351 | 57 | 3249 |  | 4.0959 | 63 | 3969
12.0351 | 60 | 3600 |  | 4.0959 | 62 | 3844
12.0351 | 63 | 3969 |  | 4.0959 | 64 | 4096
12.0351 | 63 | 3969 |  | 4.0959 | 63 | 3969
12.0351 | 65 | 4225 |  | 4.0959 | 65 | 4225
12.0351 | 66 | 4356 |  | 4.0959 | 65 | 4225
12.0351 | 68 | 4624 |  | 4.0959 | 66 | 4356
12.0351 | 68 | 4624 |  | 4.0959 | 68 | 4624
12.0351 | 70 | 4900 |  | 4.0959 | 70 | 4900
12.0351 | 54 | 2916 |  | 4.0959 | 71 | 5041
12.0351 | 54 | 2916 |  | 4.0959 | 73 | 5329
12.0351 | 54 | 2916 |  | 4.0959 | 73 | 5329
12.0351 | 54 | 2916 |  | 4.0959 | 74 | 5476
12.0351 | 55 | 3025 |  | 4.0959 | 74 | 5476
12.0351 | 55 | 3025 |  | 4.0959 | 59 | 3481
12.0351 | 56 | 3136 |  | 4.0959 | 60 | 3600
12.0351 | 56 | 3136 |  | 4.0959 | 60 | 3600
12.0351 | 58 | 3364 |  | 4.0959 | 62 | 3844
12.0351 | 59 | 3481 |  | 4.0959 | 63 | 3969
12.0351 | 60 | 3600 |  | 4.0959 | 63 | 3969
12.0351 | 61 | 3721 |  | 4.0959 | 62 | 3844
12.0351 | 53 | 2809 |  | 4.0959 | 63 | 3969
12.0351 | 56 | 3136 |  | 4.0959 | 65 | 4225
12.0351 | 59 | 3481 |  | 4.0959 | 67 | 4489
12.0351 | 61 | 3721 |  | 4.0959 | 65 | 4225
12.0351 | 63 | 3969 |  | 4.0959 | 52 | 2704
12.0351 | 67 | 4489 |  | 4.0959 | 55 | 3025
12.0351 | 65 | 4225 |  | 4.0959 | 58 | 3364
12.0351 | 59 | 3481 |  | 4.0959 | 60 | 3600
12.0351 | 61 | 3721 |  | 4.0959 | 62 | 3844
12.0351 | 66 | 4356 |  | 4.0959 | 64 | 4096
12.0351 | 63 | 3969 |  | 4.0959 | 65 | 4225
12.0351 | 63 | 3969 |  | 4.0959 | 64 | 4096
12.0351 | 63 | 3969 |  | 4.0959 | 64 | 4096
12.0351 | 65 | 4225 |  | 4.0959 | 63 | 3969
12.0351 | 65 | 4225 |  | 4.0959 | 63 | 3969
12.0351 | 66 | 4356 |  | 4.0959 | 61 | 3721
12.0351 | 68 | 4624 |  | 4.0959 | 59 | 3481
12.0351 | 70 | 4900 |  | 4.0959 | 53 | 2809
12.0351 | 71 | 5041 |  | 4.0959 | 56 | 3136
12.0351 | 73 | 5329 |  | 4.0959 | 59 | 3481
12.0351 | 73 | 5329 |  | 4.0959 | 61 | 3721
12.0351 | 74 | 5476 |  | 4.0959 | 63 | 3969
12.0351 | 74 | 5476 |  | 4.0959 | 64 | 4096
12.0351 | 59 | 3481 |  | 4.0959 | 65 | 4225
12.0351 | 60 | 3600 |  | 4.0959 | 66 | 4356
12.0351 | 60 | 3600 |  | 4.0959 | 66 | 4356
12.0351 | 62 | 3844 |  | 4.0959 | 64 | 4096
12.0351 | 63 | 3969 |  | 4.0959 | 66 | 4356
12.0351 | 63 | 3969 |  | 4.0959 | 65 | 4225
12.0351 | 62 | 3844 |  | 4.0959 | 62 | 3844
12.0351 | 63 | 3969 |  | 4.0959 | 62 | 3844
12.0351 | 65 | 4225 |  | 4.0959 | 62 | 3844
12.0351 | 67 | 4489 |  | 4.0959 | 64 | 4096
12.0351 | 65 | 4225 |  | 4.0959 | 66 | 4356
12.0351 | 52 | 2704 |  | 4.0959 | 69 | 4761
12.0351 | 55 | 3025 |  | 4.0959 | 70 | 4900
12.0351 | 58 | 3364 |  | 4.0959 | 71 | 5041
12.0351 | 60 | 3600 |  | 4.0959 | 72 | 5184
12.0351 | 62 | 3844 |  | 4.0959 | 70 | 4900
12.0351 | 64 | 4096 |  | 4.0959 | 71 | 5041
12.0351 | 65 | 4225 |  | 4.0959 | 65 | 4225
12.0351 | 64 | 4096 |  | 4.0959 | 67 | 4489
12.0351 | 64 | 4096 |  | 4.0959 | 70 | 4900
12.0351 | 63 | 3969 |  | 4.0959 | 73 | 5329
12.0351 | 63 | 3969 |  | 4.0959 | 75 | 5625
12.0351 | 61 | 3721 |  | 4.0959 | 77 | 5929
12.0351 | 53 | 2809 |  | 4.0959 | 79 | 6241
12.0351 | 56 | 3136 |  | 4.0959 | 79 | 6241
12.0351 | 59 | 3481 |  | 4.0959 | 73 | 5329
12.0351 | 61 | 3721 |  | 4.0959 | 75 | 5625
12.0351 | 63 | 3969 |  | 4.0959 | 80 | 6400
12.0351 | 64 | 4096 |  | 4.0959 | 85 | 7225
12.0351 | 65 | 4225 |  | 4.0959 | 88 | 7744
12.0351 | 66 | 4356 |  | 4.0959 | 90 | 8100
12.0351 | 66 | 4356 |  | 4.0959 | 91 | 8281
12.0351 | 64 | 4096 |  | 4.0959 | 92 | 8464
12.0351 | 66 | 4356 |  | 4.0959 | 93 | 8649
12.0351 | 65 | 4225 |  | 4.0959 | 91 | 8281
12.0351 | 62 | 3844 |  | 4.0959 | 87 | 7569
12.0351 | 62 | 3844 |  | 4.0959 | 83 | 6889
12.0351 | 62 | 3844 |  | 4.0959 | 82 | 6724
12.0351 | 64 | 4096 |  | 4.0959 | 80 | 6400
12.0351 | 66 | 4356 |  | 4.0959 | 75 | 5625
12.0351 | 69 | 4761 |  | 4.0959 | 60 | 3600
12.0351 | 70 | 4900 |  | 4.0959 | 61 | 3721
12.0351 | 71 | 5041 |  | 4.0959 | 62 | 3844
12.0351 | 72 | 5184 |  | 4.0959 | 63 | 3969
12.0351 | 70 | 4900 |  | 4.0959 | 64 | 4096
12.0351 | 71 | 5041 |  | 4.0959 | 67 | 4489
12.0351 | 65 | 4225 |  | 4.0959 | 65 | 4225
12.0351 | 67 | 4489 |  | 4.0959 | 65 | 4225
12.0351 | 70 | 4900 |  | 4.0959 | 64 | 4096
12.0351 | 73 | 5329 |  | 4.0959 | 63 | 3969
12.0351 | 75 | 5625 |  | 4.0959 | 62 | 3844
12.0351 | 77 | 5929 |  | 4.0959 | 60 | 3600
12.0351 | 79 | 6241 |  | 4.0959 | 64 | 4096
12.0351 | 79 | 6241 |  | 4.0959 | 66 | 4356
12.0351 | 73 | 5329 |  | 4.0959 | 67 | 4489
12.0351 | 75 | 5625 |  | 4.0959 | 69 | 4761
12.0351 | 80 | 6400 |  | 4.0959 | 70 | 4900
12.0351 | 85 | 7225 |  | 4.0959 | 71 | 5041
12.0351 | 88 | 7744 |  | 4.0959 | 73 | 5329
12.0351 | 90 | 8100 |  | 4.0959 | 72 | 5184
12.0351 | 91 | 8281 |  | 4.0959 | 72 | 5184
12.0351 | 92 | 8464 |  | 4.0959 | 74 | 5476
12.0351 | 93 | 8649 |  | 4.0959 | 75 | 5625
12.0351 | 91 | 8281 |  | 4.0959 | 71 | 5041
12.0351 | 87 | 7569 |  | 4.0959 | 71 | 5041
12.0351 | 83 | 6889 |  | 4.0959 | 65 | 4225
12.0351 | 82 | 6724 |  | 4.0959 | 65 | 4225
12.0351 | 80 | 6400 |  | 4.0959 | 64 | 4096
12.0351 | 75 | 5625 |  | 4.0959 | 64 | 4096
12.0351 | 60 | 3600 |  | 4.0959 | 67 | 4489
12.0351 | 61 | 3721 |  | 4.0959 | 66 | 4356
12.0351 | 62 | 3844 |  | 4.0959 | 66 | 4356
12.0351 | 63 | 3969 |  | 4.0959 | 68 | 4624
12.0351 | 64 | 4096 |  | 4.0959 | 68 | 4624
12.0351 | 67 | 4489 |  | 4.0959 | 68 | 4624
12.0351 | 65 | 4225 |  | 4.0959 | 68 | 4624
12.0351 | 65 | 4225 |  | 4.0959 | 67 | 4489
12.0351 | 64 | 4096 |  | 4.0959 | 68 | 4624
12.0351 | 63 | 3969 |  | 4.0959 | 67 | 4489
12.0351 | 62 | 3844 |  | 4.0959 | 65 | 4225
12.0351 | 66 | 4356 |  | 4.0959 | 61 | 3721
12.0351 | 67 | 4489 |  | 4.0959 | 66 | 4356
12.0351 | 69 | 4761 |  | 4.0959 | 69 | 4761
12.0351 | 70 | 4900 |  | 4.0959 | 72 | 5184
12.0351 | 71 | 5041 |  | 4.0959 | 74 | 5476
12.0351 | 73 | 5329 |  | 4.0959 | 75 | 5625
12.0351 | 72 | 5184 |  | 4.0959 | 77 | 5929
12.0351 | 72 | 5184 |  | 4.0959 | 74 | 5476
12.0351 | 74 | 5476 |  | 4.0959 | 75 | 5625
12.0351 | 75 | 5625 |  | 4.0959 | 76 | 5776
12.0351 | 71 | 5041 |  | 4.0959 | 75 | 5625
12.0351 | 71 | 5041 |  | 4.0959 | 74 | 5476
12.0351 | 65 | 4225 |  | 4.0959 | 60 | 3600
12.0351 | 65 | 4225 |  | 4.0959 | 66 | 4356
12.0351 | 64 | 4096 |  | 4.0959 | 68 | 4624
12.0351 | 64 | 4096 |  | 4.0959 | 70 | 4900
12.0351 | 67 | 4489 |  | 4.0959 | 70 | 4900
12.0351 | 66 | 4356 |  | 4.0959 | 72 | 5184
12.0351 | 66 | 4356 |  | 4.0959 | 72 | 5184
12.0351 | 68 | 4624 |  | 4.0959 | 74 | 5476
12.0351 | 68 | 4624 |  | 4.0959 | 74 | 5476
12.0351 | 68 | 4624 |  | 4.0959 | 75 | 5625
12.0351 | 68 | 4624 |  | 4.0959 | 71 | 5041
12.0351 | 67 | 4489 |  | 4.0959 | 71 | 5041
12.0351 | 68 | 4624 |  | 4.0959 | 67 | 4489
12.0351 | 67 | 4489 |  | 4.0959 | 68 | 4624
12.0351 | 66 | 4356 |  | 4.0959 | 71 | 5041
12.0351 | 69 | 4761 |  | 4.0959 | 74 | 5476
12.0351 | 72 | 5184 |  | 4.0959 | 78 | 6084
12.0351 | 74 | 5476 |  | 4.0959 | 80 | 6400
12.0351 | 75 | 5625 |  | 4.0959 | 82 | 6724
12.0351 | 77 | 5929 |  | 4.0959 | 83 | 6889
12.0351 | 74 | 5476 |  | 4.0959 | 83 | 6889
12.0351 | 75 | 5625 |  | 4.0959 | 83 | 6889
12.0351 | 76 | 5776 |  | 4.0959 | 83 | 6889
12.0351 | 75 | 5625 |  | 4.0959 | 78 | 6084
12.0351 | 60 | 3600 |  | 4.0959 | 69 | 4761
12.0351 | 66 | 4356 |  | 4.0959 | 68 | 4624
12.0351 | 68 | 4624 |  | 4.0959 | 69 | 4761
12.0351 | 70 | 4900 |  | 4.0959 | 70 | 4900
12.0351 | 70 | 4900 |  | 4.0959 | 75 | 5625
12.0351 | 72 | 5184 |  | 4.0959 | 79 | 6241
12.0351 | 72 | 5184 |  | 4.0959 | 81 | 6561
12.0351 | 74 | 5476 |  | 4.0959 | 82 | 6724
12.0351 | 74 | 5476 |  | 4.0959 | 83 | 6889
12.0351 | 75 | 5625 |  | 4.0959 | 83 | 6889
12.0351 | 71 | 5041 |  | 4.0959 | 82 | 6724
12.0351 | 67 | 4489 |  | 4.0959 | 81 | 6561
12.0351 | 68 | 4624 |  | 4.0959 | 80 | 6400
12.0351 | 71 | 5041 |  | 4.0959 | 80 | 6400
12.0351 | 74 | 5476 |  | 4.0959 | 76 | 5776
12.0351 | 78 | 6084 |  | 4.0959 | 74 | 5476
12.0351 | 80 | 6400 |  | 4.0959 | 64 | 4096
12.0351 | 82 | 6724 |  | 4.0959 | 66 | 4356
12.0351 | 83 | 6889 |  | 4.0959 | 68 | 4624
12.0351 | 83 | 6889 |  | 4.0959 | 71 | 5041
12.0351 | 83 | 6889 |  | 4.0959 | 72 | 5184
12.0351 | 83 | 6889 |  | 4.0959 | 74 | 5476
12.0351 | 78 | 6084 |  | 4.0959 | 75 | 5625
12.0351 | 69 | 4761 |  | 4.0959 | 78 | 6084
12.0351 | 68 | 4624 |  | 4.0959 | 79 | 6241
12.0351 | 69 | 4761 |  | 4.0959 | 80 | 6400
12.0351 | 70 | 4900 |  | 4.0959 | 79 | 6241
12.0351 | 75 | 5625 |  | 4.0959 | 77 | 5929
12.0351 | 79 | 6241 |  | 4.0959 | 67 | 4489
12.0351 | 81 | 6561 |  | 4.0959 | 68 | 4624
12.0351 | 82 | 6724 |  | 4.0959 | 69 | 4761
12.0351 | 83 | 6889 |  | 4.0959 | 72 | 5184
12.0351 | 83 | 6889 |  | 4.0959 | 76 | 5776
12.0351 | 82 | 6724 |  | 4.0959 | 77 | 5929
12.0351 | 81 | 6561 |  | 4.0959 | 77 | 5929
12.0351 | 80 | 6400 |  | 4.0959 | 79 | 6241
12.0351 | 80 | 6400 |  | 4.0959 | 75 | 5625
12.0351 | 76 | 5776 |  | 4.0959 | 77 | 5929
12.0351 | 74 | 5476 |  | 4.0959 | 79 | 6241
12.0351 | 64 | 4096 |  | 4.0959 | 79 | 6241
12.0351 | 66 | 4356 |  | 4.0959 | 78 | 6084
12.0351 | 68 | 4624 |  | 4.0959 | 76 | 5776
12.0351 | 71 | 5041 |  | 4.0959 | 68 | 4624
12.0351 | 72 | 5184 |  | 4.0959 | 67 | 4489
12.0351 | 74 | 5476 |  | 4.0959 | 68 | 4624
12.0351 | 75 | 5625 |  | 4.0959 | 69 | 4761
12.0351 | 78 | 6084 |  | 4.0959 | 70 | 4900
12.0351 | 79 | 6241 |  | 4.0959 | 73 | 5329
12.0351 | 80 | 6400 |  | 4.0959 | 77 | 5929
12.0351 | 79 | 6241 |  | 4.0959 | 78 | 6084
12.0351 | 77 | 5929 |  | 4.0959 | 76 | 5776
12.0351 | 67 | 4489 |  | 4.0959 | 75 | 5625
12.0351 | 68 | 4624 |  | 4.0959 | 76 | 5776
12.0351 | 69 | 4761 |  | 4.0959 | 77 | 5929
12.0351 | 72 | 5184 |  | 4.0959 | 67 | 4489
12.0351 | 76 | 5776 |  | 4.0959 | 71 | 5041
12.0351 | 77 | 5929 |  | 4.0959 | 75 | 5625
12.0351 | 77 | 5929 |  | 4.0959 | 76 | 5776
12.0351 | 79 | 6241 |  | 4.0959 | 79 | 6241
12.0351 | 75 | 5625 |  | 4.0959 | 77 | 5929
12.0351 | 77 | 5929 |  | 4.0959 | 76 | 5776
12.0351 | 79 | 6241 |  | 4.0959 | 74 | 5476
12.0351 | 79 | 6241 |  | 4.0959 | 74 | 5476
12.0351 | 78 | 6084 |  | 4.0959 | 75 | 5625
12.0351 | 68 | 4624 |  | 4.0959 | 73 | 5329
12.0351 | 67 | 4489 |  | 4.0959 | 68 | 4624
12.0351 | 68 | 4624 |  | 4.0959 | 68 | 4624
12.0351 | 69 | 4761 |  | 4.0959 | 66 | 4356
12.0351 | 70 | 4900 |  | 4.0959 | 65 | 4225
12.0351 | 73 | 5329 |  | 4.0959 | 66 | 4356
12.0351 | 77 | 5929 |  | 4.0959 | 68 | 4624
12.0351 | 78 | 6084 |  | 4.0959 | 69 | 4761
12.0351 | 76 | 5776 |  | 4.0959 | 71 | 5041
12.0351 | 75 | 5625 |  | 4.0959 | 69 | 4761
12.0351 | 76 | 5776 |  | 4.0959 | 70 | 4900
12.0351 | 67 | 4489 |  | 4.0959 | 70 | 4900
12.0351 | 71 | 5041 |  | 4.0959 | 69 | 4761
12.0351 | 75 | 5625 |  | 4.0959 | 71 | 5041
12.0351 | 76 | 5776 |  | 4.0959 | 71 | 5041
12.0351 | 79 | 6241 |  | 4.0959 | 73 | 5329
12.0351 | 77 | 5929 |  | 4.0959 | 76 | 5776
12.0351 | 76 | 5776 |  | 4.0959 | 80 | 6400
12.0351 | 74 | 5476 |  | 4.0959 | 80 | 6400
12.0351 | 74 | 5476 |  | 4.0959 | 83 | 6889
12.0351 | 75 | 5625 |  | 4.0959 | 91 | 8281
12.0351 | 73 | 5329 |  | 4.0959 | 93 | 8649
12.0351 | 68 | 4624 |  | 4.0959 | 92 | 8464
12.0351 | 68 | 4624 |  | 4.0959 | 91 | 8281
12.0351 | 66 | 4356 |  | 4.0959 | 65 | 4225
12.0351 | 65 | 4225 |  | 4.0959 | 67 | 4489
12.0351 | 66 | 4356 |  | 4.0959 | 70 | 4900
12.0351 | 68 | 4624 |  | 4.0959 | 74 | 5476
12.0351 | 69 | 4761 |  | 4.0959 | 76 | 5776
12.0351 | 71 | 5041 |  | 4.0959 | 76 | 5776
12.0351 | 69 | 4761 |  | 4.0959 | 74 | 5476
12.0351 | 70 | 4900 |  | 4.0959 | 77 | 5929
12.0351 | 70 | 4900 |  | 4.0959 | 76 | 5776
12.0351 | 69 | 4761 |  | 4.0959 | 77 | 5929
12.0351 | 71 | 5041 |  | 4.0959 | 75 | 5625
12.0351 | 71 | 5041 |  | 4.0959 | 65 | 4225
12.0351 | 73 | 5329 |  | 4.0959 | 65 | 4225
12.0351 | 76 | 5776 |  | 4.0959 | 63 | 3969
12.0351 | 80 | 6400 |  | 4.0959 | 63 | 3969
12.0351 | 80 | 6400 |  | 4.0959 | 64 | 4096
12.0351 | 83 | 6889 |  | 4.0959 | 64 | 4096
12.0351 | 91 | 8281 |  | 4.0959 | 64 | 4096
12.0351 | 93 | 8649 |  | 4.0959 | 64 | 4096
12.0351 | 92 | 8464 |  | 4.0959 | 64 | 4096
12.0351 | 65 | 4225 |  | 4.0959 | 63 | 3969
12.0351 | 67 | 4489 |  | 4.0959 | 64 | 4096
12.0351 | 70 | 4900 |  | 4.0959 | 62 | 3844
12.0351 | 74 | 5476 |  | 4.0959 | 65 | 4225
12.0351 | 76 | 5776 |  | 4.0959 | 67 | 4489
12.0351 | 76 | 5776 |  | 4.0959 | 68 | 4624
12.0351 | 74 | 5476 |  | 4.0959 | 71 | 5041
12.0351 | 77 | 5929 |  | 4.0959 | 72 | 5184
12.0351 | 76 | 5776 |  | 4.0959 | 73 | 5329
12.0351 | 77 | 5929 |  | 4.0959 | 73 | 5329
12.0351 | 75 | 5625 |  | 4.0959 | 73 | 5329
12.0351 | 65 | 4225 |  | 4.0959 | 72 | 5184
12.0351 | 65 | 4225 |  | 4.0959 | 73 | 5329
12.0351 | 63 | 3969 |  | 4.0959 | 61 | 3721
12.0351 | 63 | 3969 |  | 4.0959 | 65 | 4225
12.0351 | 64 | 4096 |  | 4.0959 | 66 | 4356
12.0351 | 64 | 4096 |  | 4.0959 | 69 | 4761
12.0351 | 64 | 4096 |  | 4.0959 | 71 | 5041
12.0351 | 64 | 4096 |  | 4.0959 | 72 | 5184
12.0351 | 64 | 4096 |  | 4.0959 | 72 | 5184
12.0351 | 63 | 3969 |  | 4.0959 | 74 | 5476
12.0351 | 64 | 4096 |  | 4.0959 | 75 | 5625
12.0351 | 62 | 3844 |  | 4.0959 | 75 | 5625
12.0351 | 65 | 4225 |  | 4.0959 | 74 | 5476
12.0351 | 67 | 4489 |  | 4.0959 | 70 | 4900
12.0351 | 68 | 4624 |  | 4.0959 | 71 | 5041
12.0351 | 71 | 5041 |  | 4.0959 | 72 | 5184
12.0351 | 72 | 5184 |  | 4.0959 | 73 | 5329
12.0351 | 73 | 5329 |  | 4.0959 | 75 | 5625
12.0351 | 73 | 5329 |  | 4.0959 | 73 | 5329
12.0351 | 73 | 5329 |  | 4.0959 | 71 | 5041
12.0351 | 72 | 5184 |  | 4.0959 | 76 | 5776
12.0351 | 73 | 5329 |  | 4.0959 | 75 | 5625
12.0351 | 61 | 3721 |  | 4.0959 | 75 | 5625
12.0351 | 65 | 4225 |  | 4.0959 | 73 | 5329
12.0351 | 66 | 4356 |  | 4.0959 | 73 | 5329
12.0351 | 69 | 4761 |  | 4.0959 | 65 | 4225
12.0351 | 71 | 5041 |  | 4.0959 | 66 | 4356
12.0351 | 72 | 5184 |  | 4.0959 | 70 | 4900
12.0351 | 72 | 5184 |  | 4.0959 | 70 | 4900
12.0351 | 74 | 5476 |  | 4.0959 | 73 | 5329
12.0351 | 75 | 5625 |  | 4.0959 | 75 | 5625
12.0351 | 75 | 5625 |  | 4.0959 | 77 | 5929
12.0351 | 74 | 5476 |  | 4.0959 | 76 | 5776
12.0351 | 70 | 4900 |  | 4.0959 | 76 | 5776
12.0351 | 71 | 5041 |  | 4.0959 | 76 | 5776
12.0351 | 72 | 5184 |  | 4.0959 | 77 | 5929
12.0351 | 73 | 5329 |  | 4.0959 | 79 | 6241
12.0351 | 75 | 5625 |  | 4.0959 | 64 | 4096
12.0351 | 73 | 5329 |  | 4.0959 | 67 | 4489
12.0351 | 71 | 5041 |  | 4.0959 | 70 | 4900
12.0351 | 76 | 5776 |  | 4.0959 | 72 | 5184
12.0351 | 75 | 5625 |  | 4.0959 | 75 | 5625
12.0351 | 75 | 5625 |  | 4.0959 | 79 | 6241
12.0351 | 73 | 5329 |  | 4.0959 | 80 | 6400
12.0351 | 65 | 4225 |  | 4.0959 | 81 | 6561
12.0351 | 66 | 4356 |  | 4.0959 | 81 | 6561
12.0351 | 70 | 4900 |  | 4.0959 | 81 | 6561
12.0351 | 70 | 4900 |  | 4.0959 | 80 | 6400
12.0351 | 73 | 5329 |  | 4.0959 | 79 | 6241
12.0351 | 75 | 5625 |  | 4.0959 | 70 | 4900
12.0351 | 77 | 5929 |  | 4.0959 | 72 | 5184
12.0351 | 76 | 5776 |  | 4.0959 | 75 | 5625
12.0351 | 76 | 5776 |  | 4.0959 | 77 | 5929
12.0351 | 76 | 5776 |  | 4.0959 | 80 | 6400
12.0351 | 77 | 5929 |  | 4.0959 | 82 | 6724
12.0351 | 64 | 4096 |  | 4.0959 | 79 | 6241
12.0351 | 67 | 4489 |  | 4.0959 | 81 | 6561
12.0351 | 70 | 4900 |  | 4.0959 | 82 | 6724
12.0351 | 72 | 5184 |  | 4.0959 | 81 | 6561
12.0351 | 75 | 5625 |  | 4.0959 | 82 | 6724
12.0351 | 79 | 6241 |  | 4.0959 | 71 | 5041
12.0351 | 80 | 6400 |  | 4.0959 | 73 | 5329
12.0351 | 81 | 6561 |  | 4.0959 | 74 | 5476
12.0351 | 81 | 6561 |  | 4.0959 | 77 | 5929
12.0351 | 81 | 6561 |  | 4.0959 | 78 | 6084
12.0351 | 80 | 6400 |  | 4.0959 | 80 | 6400
12.0351 | 70 | 4900 |  | 4.0959 | 81 | 6561
12.0351 | 72 | 5184 |  | 4.0959 | 83 | 6889
12.0351 | 75 | 5625 |  | 4.0959 | 84 | 7056
12.0351 | 77 | 5929 |  | 4.0959 | 84 | 7056
12.0351 | 80 | 6400 |  | 4.0959 | 83 | 6889
12.0351 | 82 | 6724 |  | 4.0959 | 70 | 4900
12.0351 | 79 | 6241 |  | 4.0959 | 72 | 5184
12.0351 | 81 | 6561 |  | 4.0959 | 73 | 5329
12.0351 | 82 | 6724 |  | 4.0959 | 76 | 5776
12.0351 | 81 | 6561 |  | 4.0959 | 77 | 5929
12.0351 | 82 | 6724 |  | 4.0959 | 81 | 6561
12.0351 | 71 | 5041 |  | 4.0959 | 82 | 6724
12.0351 | 73 | 5329 |  | 4.0959 | 81 | 6561
12.0351 | 74 | 5476 |  | 4.0959 | 81 | 6561
12.0351 | 77 | 5929 |  | 4.0959 | 77 | 5929
12.0351 | 78 | 6084 |  | 4.0959 | 76 | 5776
12.0351 | 80 | 6400 |  | 4.0959 | 75 | 5625
12.0351 | 81 | 6561 |  | 4.0959 | 75 | 5625
12.0351 | 83 | 6889 |  | 4.0959 | 73 | 5329
12.0351 | 84 | 7056 |  | 4.0959 | 76 | 5776
12.0351 | 84 | 7056 |  | 4.0959 | 79 | 6241
12.0351 | 83 | 6889 |  | 4.0959 | 83 | 6889
12.0351 | 70 | 4900 |  | 4.0959 | 87 | 7569
12.0351 | 72 | 5184 |  | 4.0959 | 86 | 7396
12.0351 | 73 | 5329 |  | 4.0959 | 86 | 7396
12.0351 | 76 | 5776 |  | 4.0959 | 86 | 7396
12.0351 | 77 | 5929 |  | 4.0959 | 86 | 7396
12.0351 | 81 | 6561 |  | 4.0959 | 86 | 7396
12.0351 | 82 | 6724 |  | 4.0959 | 87 | 7569
12.0351 | 81 | 6561 |  | 4.0959 | 87 | 7569
12.0351 | 81 | 6561 |  | 4.0959 | 73 | 5329
12.0351 | 77 | 5929 |  | 4.0959 | 74 | 5476
12.0351 | 76 | 5776 |  | 4.0959 | 74 | 5476
12.0351 | 75 | 5625 |  | 4.0959 | 76 | 5776
12.0351 | 73 | 5329 |  | 4.0959 | 77 | 5929
12.0351 | 76 | 5776 |  | 4.0959 | 78 | 6084
12.0351 | 79 | 6241 |  | 4.0959 | 79 | 6241
12.0351 | 83 | 6889 |  | 4.0959 | 81 | 6561
12.0351 | 87 | 7569 |  | 4.0959 | 81 | 6561
12.0351 | 86 | 7396 |  | 4.0959 | 79 | 6241
12.0351 | 86 | 7396 |  | 4.0959 | 80 | 6400
12.0351 | 86 | 7396 |  | 4.0959 | 78 | 6084
12.0351 | 86 | 7396 |  | 4.0959 | 67 | 4489
12.0351 | 86 | 7396 |  | 4.0959 | 70 | 4900
12.0351 | 87 | 7569 |  | 4.0959 | 71 | 5041
12.0351 | 73 | 5329 |  | 4.0959 | 74 | 5476
12.0351 | 74 | 5476 |  | 4.0959 | 74 | 5476
12.0351 | 74 | 5476 |  | 4.0959 | 77 | 5929
12.0351 | 76 | 5776 |  | 4.0959 | 77 | 5929
12.0351 | 77 | 5929 |  | 4.0959 | 78 | 6084
12.0351 | 78 | 6084 |  | 4.0959 | 80 | 6400
12.0351 | 79 | 6241 |  | 4.0959 | 79 | 6241
12.0351 | 81 | 6561 |  | 4.0959 | 77 | 5929
12.0351 | 81 | 6561 |  | 4.0959 | 75 | 5625
12.0351 | 79 | 6241 |  | 4.0959 | 66 | 4356
12.0351 | 80 | 6400 |  | 4.0959 | 65 | 4225
12.0351 | 67 | 4489 |  | 4.0959 | 69 | 4761
12.0351 | 70 | 4900 |  | 4.0959 | 72 | 5184
12.0351 | 71 | 5041 |  | 4.0959 | 75 | 5625
12.0351 | 74 | 5476 |  | 4.0959 | 77 | 5929
12.0351 | 74 | 5476 |  | 4.0959 | 79 | 6241
12.0351 | 77 | 5929 |  | 4.0959 | 79 | 6241
12.0351 | 77 | 5929 |  | 4.0959 | 80 | 6400
12.0351 | 78 | 6084 |  | 4.0959 | 80 | 6400
12.0351 | 80 | 6400 |  | 4.0959 | 81 | 6561
12.0351 | 79 | 6241 |  | 4.0959 | 80 | 6400
12.0351 | 77 | 5929 |  | 4.0959 | 78 | 6084
12.0351 | 65 | 4225 |  | 4.0959 | 76 | 5776
12.0351 | 69 | 4761 |  | 4.0959 | 70 | 4900
12.0351 | 72 | 5184 |  | 4.0959 | 71 | 5041
12.0351 | 75 | 5625 |  | 4.0959 | 73 | 5329
12.0351 | 77 | 5929 |  | 4.0959 | 75 | 5625
12.0351 | 79 | 6241 |  | 4.0959 | 77 | 5929
12.0351 | 79 | 6241 |  | 4.0959 | 80 | 6400
12.0351 | 80 | 6400 |  | 4.0959 | 82 | 6724
12.0351 | 80 | 6400 |  | 4.0959 | 82 | 6724
12.0351 | 81 | 6561 |  | 4.0959 | 83 | 6889
12.0351 | 80 | 6400 |  | 4.0959 | 82 | 6724
12.0351 | 78 | 6084 |  | 4.0959 | 82 | 6724
12.0351 | 70 | 4900 |  | 4.0959 | 81 | 6561
12.0351 | 71 | 5041 |  | 4.0959 | 75 | 5625
12.0351 | 73 | 5329 |  | 4.0959 | 78 | 6084
12.0351 | 75 | 5625 |  | 4.0959 | 80 | 6400
12.0351 | 77 | 5929 |  | 4.0959 | 82 | 6724
12.0351 | 80 | 6400 |  | 4.0959 | 86 | 7396
12.0351 | 82 | 6724 |  | 4.0959 | 85 | 7225
12.0351 | 82 | 6724 |  | 4.0959 | 88 | 7744
12.0351 | 83 | 6889 |  | 4.0959 | 88 | 7744
12.0351 | 82 | 6724 |  | 4.0959 | 89 | 7921
12.0351 | 82 | 6724 |  | 4.0959 | 91 | 8281
12.0351 | 81 | 6561 |  | 4.0959 | 88 | 7744
12.0351 | 75 | 5625 |  | 4.0959 | 84 | 7056
12.0351 | 78 | 6084 |  | 4.0959 | 84 | 7056
12.0351 | 80 | 6400 |  | 4.0959 | 80 | 6400
12.0351 | 82 | 6724 |  | 4.0959 | 77 | 5929
12.0351 | 86 | 7396 |  | 4.0959 | 76 | 5776
12.0351 | 85 | 7225 |  | 4.0959 | 75 | 5625
12.0351 | 88 | 7744 |  | 4.0959 | 75 | 5625
12.0351 | 88 | 7744 |  | 4.0959 | 73 | 5329
12.0351 | 89 | 7921 |  | 4.0959 | 73 | 5329
12.0351 | 91 | 8281 |  | 4.0959 | 72 | 5184
12.0351 | 88 | 7744 |  | 4.0959 | 72 | 5184
12.0351 | 84 | 7056 |  | 4.0959 | 74 | 5476
12.0351 | 72 | 5184 |  | 4.0959 | 73 | 5329
12.0351 | 73 | 5329 |  | 4.0959 | 72 | 5184
12.0351 | 74 | 5476 |  | 4.0959 | 73 | 5329
12.19 | 61 | 3721 |  | 4.0959 | 74 | 5476
12.4137 | 71 | 5041 |  | 4.2434 | 72 | 5184

## Step 4. Schedule Calcs
Supply Fan Datetime | Hour of Day | Day of Week | Supply Fan On/Off | Return Fan Datetime | Hour of Day | Day of Week | Return Fan On/Off
2022-03-11 09:00 | 9 | 6 | 1 | 2022-03-11 09:00 | 9 | 6 | 1
2022-03-11 10:00 | 10 | 6 | 1 | 2022-03-11 10:00 | 10 | 6 | 1
2022-03-11 11:00 | 11 | 6 | 1 | 2022-03-11 11:00 | 11 | 6 | 1
2022-03-11 12:00 | 12 | 6 | 1 | 2022-03-11 12:00 | 12 | 6 | 1
2022-03-11 13:00 | 13 | 6 | 1 | 2022-03-11 13:00 | 13 | 6 | 1
2022-03-11 14:00 | 14 | 6 | 1 | 2022-03-11 14:00 | 14 | 6 | 1
2022-03-11 15:00 | 15 | 6 | 1 | 2022-03-11 15:00 | 15 | 6 | 1
2022-03-11 16:00 | 16 | 6 | 1 | 2022-03-11 16:00 | 16 | 6 | 1
2022-03-11 17:00 | 17 | 6 | 1 | 2022-03-11 17:00 | 17 | 6 | 1
2022-03-11 18:00 | 18 | 6 | 1 | 2022-03-11 18:00 | 18 | 6 | 1
2022-03-11 19:00 | 19 | 6 | 1 | 2022-03-11 19:00 | 19 | 6 | 1
2022-03-11 20:00 | 20 | 6 | 1 | 2022-03-11 20:00 | 20 | 6 | 1
2022-03-11 21:00 | 21 | 6 | 1 | 2022-03-11 21:00 | 21 | 6 | 1
2022-03-11 22:00 | 22 | 6 | 1 | 2022-03-11 22:00 | 22 | 6 | 1
2022-03-11 23:00 | 23 | 6 | 1 | 2022-03-11 23:00 | 23 | 6 | 1
2022-03-12 | 0 | 7 | 1 | 2022-03-12 | 0 | 7 | 1
2022-03-12 01:00 | 1 | 7 | 1 | 2022-03-12 01:00 | 1 | 7 | 1
2022-03-12 02:00 | 2 | 7 | 1 | 2022-03-12 02:00 | 2 | 7 | 1
2022-03-12 03:00 | 3 | 7 | 1 | 2022-03-12 03:00 | 3 | 7 | 1
2022-03-12 04:00 | 4 | 7 | 1 | 2022-03-12 04:00 | 4 | 7 | 1
2022-03-12 05:00 | 5 | 7 | 1 | 2022-03-12 05:00 | 5 | 7 | 1
2022-03-12 06:00 | 6 | 7 | 1 | 2022-03-12 06:00 | 6 | 7 | 1
2022-03-12 07:00 | 7 | 7 | 1 | 2022-03-12 07:00 | 7 | 7 | 1
2022-03-12 08:00 | 8 | 7 | 1 | 2022-03-12 08:00 | 8 | 7 | 1
2022-03-12 09:00 | 9 | 7 | 1 | 2022-03-12 09:00 | 9 | 7 | 1
2022-03-12 10:00 | 10 | 7 | 1 | 2022-03-12 10:00 | 10 | 7 | 1
2022-03-12 11:00 | 11 | 7 | 1 | 2022-03-12 11:00 | 11 | 7 | 1
2022-03-12 12:00 | 12 | 7 | 1 | 2022-03-12 12:00 | 12 | 7 | 1
2022-03-12 13:00 | 13 | 7 | 1 | 2022-03-12 13:00 | 13 | 7 | 1
2022-03-12 14:00 | 14 | 7 | 1 | 2022-03-12 14:00 | 14 | 7 | 1
2022-03-12 15:00 | 15 | 7 | 1 | 2022-03-12 15:00 | 15 | 7 | 1
2022-03-12 16:00 | 16 | 7 | 1 | 2022-03-12 16:00 | 16 | 7 | 1
2022-03-12 17:00 | 17 | 7 | 1 | 2022-03-12 17:00 | 17 | 7 | 1
2022-03-12 18:00 | 18 | 7 | 1 | 2022-03-12 18:00 | 18 | 7 | 1
2022-03-12 19:00 | 19 | 7 | 1 | 2022-03-12 19:00 | 19 | 7 | 1
2022-03-12 20:00 | 20 | 7 | 1 | 2022-03-12 20:00 | 20 | 7 | 1
2022-03-12 21:00 | 21 | 7 | 1 | 2022-03-12 21:00 | 21 | 7 | 1
2022-03-12 22:00 | 22 | 7 | 1 | 2022-03-12 22:00 | 22 | 7 | 1
2022-03-12 23:00 | 23 | 7 | 1 | 2022-03-12 23:00 | 23 | 7 | 1
2022-03-13 | 0 | 1 | 1 | 2022-03-13 | 0 | 1 | 1
2022-03-13 01:00 | 1 | 1 | 1 | 2022-03-13 01:00 | 1 | 1 | 1
2022-03-13 02:00 | 2 | 1 | 1 | 2022-03-13 02:00 | 2 | 1 | 1
2022-03-13 03:00 | 3 | 1 | 1 | 2022-03-13 03:00 | 3 | 1 | 1
2022-03-13 04:00 | 4 | 1 | 1 | 2022-03-13 04:00 | 4 | 1 | 1
2022-03-13 05:00 | 5 | 1 | 1 | 2022-03-13 05:00 | 5 | 1 | 1
2022-03-13 06:00 | 6 | 1 | 1 | 2022-03-13 06:00 | 6 | 1 | 1
2022-03-13 07:00 | 7 | 1 | 1 | 2022-03-13 07:00 | 7 | 1 | 1
2022-03-13 08:00 | 8 | 1 | 1 | 2022-03-13 08:00 | 8 | 1 | 1
2022-03-13 09:00 | 9 | 1 | 1 | 2022-03-13 09:00 | 9 | 1 | 1
2022-03-13 10:00 | 10 | 1 | 1 | 2022-03-13 10:00 | 10 | 1 | 1
2022-03-13 11:00 | 11 | 1 | 1 | 2022-03-13 11:00 | 11 | 1 | 1
2022-03-13 12:00 | 12 | 1 | 1 | 2022-03-13 12:00 | 12 | 1 | 1
2022-03-13 13:00 | 13 | 1 | 1 | 2022-03-13 13:00 | 13 | 1 | 1
2022-03-13 14:00 | 14 | 1 | 1 | 2022-03-13 14:00 | 14 | 1 | 1
2022-03-13 15:00 | 15 | 1 | 1 | 2022-03-13 15:00 | 15 | 1 | 1
2022-03-13 16:00 | 16 | 1 | 1 | 2022-03-13 16:00 | 16 | 1 | 1
2022-03-13 17:00 | 17 | 1 | 1 | 2022-03-13 17:00 | 17 | 1 | 1
2022-03-13 18:00 | 18 | 1 | 1 | 2022-03-13 18:00 | 18 | 1 | 1
2022-03-13 19:00 | 19 | 1 | 1 | 2022-03-13 19:00 | 19 | 1 | 1
2022-03-13 20:00 | 20 | 1 | 1 | 2022-03-13 20:00 | 20 | 1 | 1
2022-03-13 21:00 | 21 | 1 | 1 | 2022-03-13 21:00 | 21 | 1 | 1
2022-03-13 22:00 | 22 | 1 | 1 | 2022-03-13 22:00 | 22 | 1 | 1
2022-03-13 23:00 | 23 | 1 | 1 | 2022-03-13 23:00 | 23 | 1 | 1
2022-03-14 | 0 | 2 | 1 | 2022-03-14 | 0 | 2 | 1
2022-03-14 01:00 | 1 | 2 | 1 | 2022-03-14 01:00 | 1 | 2 | 1
2022-03-14 02:00 | 2 | 2 | 1 | 2022-03-14 02:00 | 2 | 2 | 1
2022-03-14 03:00 | 3 | 2 | 1 | 2022-03-14 03:00 | 3 | 2 | 1
2022-03-14 04:00 | 4 | 2 | 1 | 2022-03-14 04:00 | 4 | 2 | 1
2022-03-14 05:00 | 5 | 2 | 1 | 2022-03-14 05:00 | 5 | 2 | 1
2022-03-14 06:00 | 6 | 2 | 1 | 2022-03-14 06:00 | 6 | 2 | 1
2022-03-14 07:00 | 7 | 2 | 1 | 2022-03-14 07:00 | 7 | 2 | 1
2022-03-14 08:00 | 8 | 2 | 1 | 2022-03-14 08:00 | 8 | 2 | 1
2022-03-14 09:00 | 9 | 2 | 1 | 2022-03-14 09:00 | 9 | 2 | 1
2022-03-14 10:00 | 10 | 2 | 1 | 2022-03-14 10:00 | 10 | 2 | 1
2022-03-14 11:00 | 11 | 2 | 1 | 2022-03-14 11:00 | 11 | 2 | 1
2022-03-14 12:00 | 12 | 2 | 1 | 2022-03-14 12:00 | 12 | 2 | 1
2022-03-14 13:00 | 13 | 2 | 1 | 2022-03-14 13:00 | 13 | 2 | 1
2022-03-14 14:00 | 14 | 2 | 1 | 2022-03-14 14:00 | 14 | 2 | 1
2022-03-14 15:00 | 15 | 2 | 1 | 2022-03-14 15:00 | 15 | 2 | 1
2022-03-14 16:00 | 16 | 2 | 1 | 2022-03-14 16:00 | 16 | 2 | 1
2022-03-14 17:00 | 17 | 2 | 1 | 2022-03-14 17:00 | 17 | 2 | 1
2022-03-14 18:00 | 18 | 2 | 1 | 2022-03-14 18:00 | 18 | 2 | 1
2022-03-14 19:00 | 19 | 2 | 1 | 2022-03-14 19:00 | 19 | 2 | 1
2022-03-14 20:00 | 20 | 2 | 1 | 2022-03-14 20:00 | 20 | 2 | 1
2022-03-14 21:00 | 21 | 2 | 1 | 2022-03-14 21:00 | 21 | 2 | 1
2022-03-14 22:00 | 22 | 2 | 1 | 2022-03-14 22:00 | 22 | 2 | 1
2022-03-14 23:00 | 23 | 2 | 1 | 2022-03-14 23:00 | 23 | 2 | 1
2022-03-15 | 0 | 3 | 1 | 2022-03-15 | 0 | 3 | 1
2022-03-15 01:00 | 1 | 3 | 1 | 2022-03-15 01:00 | 1 | 3 | 1
2022-03-15 02:00 | 2 | 3 | 1 | 2022-03-15 02:00 | 2 | 3 | 1
2022-03-15 03:00 | 3 | 3 | 1 | 2022-03-15 03:00 | 3 | 3 | 1
2022-03-15 04:00 | 4 | 3 | 1 | 2022-03-15 04:00 | 4 | 3 | 1
2022-03-15 05:00 | 5 | 3 | 1 | 2022-03-15 05:00 | 5 | 3 | 1
2022-03-15 06:00 | 6 | 3 | 1 | 2022-03-15 06:00 | 6 | 3 | 1
2022-03-15 07:00 | 7 | 3 | 1 | 2022-03-15 07:00 | 7 | 3 | 1
2022-03-15 08:00 | 8 | 3 | 1 | 2022-03-15 08:00 | 8 | 3 | 1
2022-03-15 09:00 | 9 | 3 | 1 | 2022-03-15 09:00 | 9 | 3 | 1
2022-03-15 10:00 | 10 | 3 | 1 | 2022-03-15 10:00 | 10 | 3 | 1
2022-03-15 11:00 | 11 | 3 | 1 | 2022-03-15 11:00 | 11 | 3 | 1
2022-03-15 12:00 | 12 | 3 | 1 | 2022-03-15 12:00 | 12 | 3 | 1
2022-03-15 13:00 | 13 | 3 | 1 | 2022-03-15 13:00 | 13 | 3 | 1
2022-03-15 14:00 | 14 | 3 | 1 | 2022-03-15 14:00 | 14 | 3 | 1
2022-03-15 15:00 | 15 | 3 | 1 | 2022-03-15 15:00 | 15 | 3 | 1
2022-03-15 16:00 | 16 | 3 | 1 | 2022-03-15 16:00 | 16 | 3 | 1
2022-03-15 17:00 | 17 | 3 | 1 | 2022-03-15 17:00 | 17 | 3 | 1
2022-03-15 18:00 | 18 | 3 | 1 | 2022-03-15 18:00 | 18 | 3 | 1
2022-03-15 19:00 | 19 | 3 | 1 | 2022-03-15 19:00 | 19 | 3 | 1
2022-03-15 20:00 | 20 | 3 | 1 | 2022-03-15 20:00 | 20 | 3 | 1
2022-03-15 21:00 | 21 | 3 | 1 | 2022-03-15 21:00 | 21 | 3 | 1
2022-03-15 22:00 | 22 | 3 | 1 | 2022-03-15 22:00 | 22 | 3 | 1
2022-03-15 23:00 | 23 | 3 | 1 | 2022-03-15 23:00 | 23 | 3 | 1
2022-03-16 | 0 | 4 | 1 | 2022-03-16 | 0 | 4 | 1
2022-03-16 01:00 | 1 | 4 | 1 | 2022-03-16 01:00 | 1 | 4 | 1
2022-03-16 02:00 | 2 | 4 | 1 | 2022-03-16 02:00 | 2 | 4 | 1
2022-03-16 03:00 | 3 | 4 | 1 | 2022-03-16 03:00 | 3 | 4 | 1
2022-03-16 04:00 | 4 | 4 | 1 | 2022-03-16 04:00 | 4 | 4 | 1
2022-03-16 05:00 | 5 | 4 | 1 | 2022-03-16 05:00 | 5 | 4 | 1
2022-03-16 06:00 | 6 | 4 | 1 | 2022-03-16 06:00 | 6 | 4 | 1
2022-03-16 07:00 | 7 | 4 | 1 | 2022-03-16 07:00 | 7 | 4 | 1
2022-03-16 08:00 | 8 | 4 | 1 | 2022-03-16 08:00 | 8 | 4 | 1
2022-03-16 09:00 | 9 | 4 | 1 | 2022-03-16 09:00 | 9 | 4 | 1
2022-03-16 10:00 | 10 | 4 | 1 | 2022-03-16 10:00 | 10 | 4 | 1
2022-03-16 11:00 | 11 | 4 | 1 | 2022-03-16 11:00 | 11 | 4 | 1
2022-03-16 12:00 | 12 | 4 | 1 | 2022-03-16 12:00 | 12 | 4 | 1
2022-03-16 13:00 | 13 | 4 | 1 | 2022-03-16 13:00 | 13 | 4 | 1
2022-03-16 14:00 | 14 | 4 | 1 | 2022-03-16 14:00 | 14 | 4 | 1
2022-03-16 15:00 | 15 | 4 | 1 | 2022-03-16 15:00 | 15 | 4 | 1
2022-03-16 16:00 | 16 | 4 | 1 | 2022-03-16 16:00 | 16 | 4 | 1
2022-03-16 17:00 | 17 | 4 | 1 | 2022-03-16 17:00 | 17 | 4 | 1
2022-03-16 18:00 | 18 | 4 | 1 | 2022-03-16 18:00 | 18 | 4 | 1
2022-03-16 19:00 | 19 | 4 | 1 | 2022-03-16 19:00 | 19 | 4 | 1
2022-03-16 20:00 | 20 | 4 | 1 | 2022-03-16 20:00 | 20 | 4 | 1
2022-03-16 21:00 | 21 | 4 | 1 | 2022-03-16 21:00 | 21 | 4 | 1
2022-03-16 22:00 | 22 | 4 | 1 | 2022-03-16 22:00 | 22 | 4 | 1
2022-03-16 23:00 | 23 | 4 | 1 | 2022-03-16 23:00 | 23 | 4 | 1
2022-03-17 | 0 | 5 | 1 | 2022-03-17 | 0 | 5 | 1
2022-03-17 01:00 | 1 | 5 | 1 | 2022-03-17 01:00 | 1 | 5 | 1
2022-03-17 02:00 | 2 | 5 | 1 | 2022-03-17 02:00 | 2 | 5 | 1
2022-03-17 03:00 | 3 | 5 | 1 | 2022-03-17 03:00 | 3 | 5 | 1
2022-03-17 04:00 | 4 | 5 | 1 | 2022-03-17 04:00 | 4 | 5 | 1
2022-03-17 05:00 | 5 | 5 | 1 | 2022-03-17 05:00 | 5 | 5 | 1
2022-03-17 06:00 | 6 | 5 | 1 | 2022-03-17 06:00 | 6 | 5 | 1
2022-03-17 07:00 | 7 | 5 | 1 | 2022-03-17 07:00 | 7 | 5 | 1
2022-03-17 08:00 | 8 | 5 | 1 | 2022-03-17 08:00 | 8 | 5 | 1
2022-03-17 09:00 | 9 | 5 | 1 | 2022-03-17 09:00 | 9 | 5 | 1
2022-03-17 10:00 | 10 | 5 | 1 | 2022-03-17 10:00 | 10 | 5 | 1
2022-03-17 11:00 | 11 | 5 | 1 | 2022-03-17 11:00 | 11 | 5 | 1
2022-03-17 12:00 | 12 | 5 | 1 | 2022-03-17 12:00 | 12 | 5 | 1
2022-03-17 13:00 | 13 | 5 | 1 | 2022-03-17 13:00 | 13 | 5 | 1
2022-03-17 14:00 | 14 | 5 | 1 | 2022-03-17 14:00 | 14 | 5 | 1
2022-03-17 15:00 | 15 | 5 | 1 | 2022-03-17 15:00 | 15 | 5 | 1
2022-03-17 16:00 | 16 | 5 | 1 | 2022-03-17 16:00 | 16 | 5 | 1
2022-03-17 17:00 | 17 | 5 | 1 | 2022-03-17 17:00 | 17 | 5 | 1
2022-03-17 18:00 | 18 | 5 | 1 | 2022-03-17 18:00 | 18 | 5 | 1
2022-03-17 19:00 | 19 | 5 | 1 | 2022-03-17 19:00 | 19 | 5 | 1
2022-03-17 20:00 | 20 | 5 | 1 | 2022-03-17 20:00 | 20 | 5 | 1
2022-03-17 21:00 | 21 | 5 | 1 | 2022-03-17 21:00 | 21 | 5 | 1
2022-03-17 22:00 | 22 | 5 | 1 | 2022-03-17 22:00 | 22 | 5 | 1
2022-03-17 23:00 | 23 | 5 | 1 | 2022-03-17 23:00 | 23 | 5 | 1
2022-03-18 | 0 | 6 | 1 | 2022-03-18 | 0 | 6 | 1
2022-03-18 01:00 | 1 | 6 | 1 | 2022-03-18 01:00 | 1 | 6 | 1
2022-03-18 02:00 | 2 | 6 | 1 | 2022-03-18 02:00 | 2 | 6 | 1
2022-03-18 03:00 | 3 | 6 | 1 | 2022-03-18 03:00 | 3 | 6 | 1
2022-03-18 04:00 | 4 | 6 | 1 | 2022-03-18 04:00 | 4 | 6 | 1
2022-03-18 05:00 | 5 | 6 | 1 | 2022-03-18 05:00 | 5 | 6 | 1
2022-03-18 06:00 | 6 | 6 | 1 | 2022-03-18 06:00 | 6 | 6 | 1
2022-03-18 07:00 | 7 | 6 | 1 | 2022-03-18 07:00 | 7 | 6 | 1
2022-03-18 08:00 | 8 | 6 | 1 | 2022-03-18 08:00 | 8 | 6 | 1
2022-03-18 09:00 | 9 | 6 | 1 | 2022-03-18 09:00 | 9 | 6 | 1
2022-03-18 10:00 | 10 | 6 | 1 | 2022-03-18 10:00 | 10 | 6 | 1
2022-03-18 11:00 | 11 | 6 | 1 | 2022-03-18 11:00 | 11 | 6 | 1
2022-03-18 12:00 | 12 | 6 | 1 | 2022-03-18 12:00 | 12 | 6 | 1
2022-03-18 13:00 | 13 | 6 | 1 | 2022-03-18 13:00 | 13 | 6 | 1
2022-03-18 14:00 | 14 | 6 | 1 | 2022-03-18 14:00 | 14 | 6 | 1
2022-03-18 15:00 | 15 | 6 | 1 | 2022-03-18 15:00 | 15 | 6 | 1
2022-03-18 16:00 | 16 | 6 | 1 | 2022-03-18 16:00 | 16 | 6 | 1
2022-03-18 17:00 | 17 | 6 | 1 | 2022-03-18 17:00 | 17 | 6 | 1
2022-03-18 18:00 | 18 | 6 | 1 | 2022-03-18 18:00 | 18 | 6 | 1
2022-03-18 19:00 | 19 | 6 | 1 | 2022-03-18 19:00 | 19 | 6 | 1
2022-03-18 20:00 | 20 | 6 | 1 | 2022-03-18 20:00 | 20 | 6 | 1
2022-03-18 21:00 | 21 | 6 | 1 | 2022-03-18 21:00 | 21 | 6 | 1
2022-03-18 22:00 | 22 | 6 | 1 | 2022-03-18 22:00 | 22 | 6 | 1
2022-03-18 23:00 | 23 | 6 | 1 | 2022-03-18 23:00 | 23 | 6 | 1
2022-03-19 | 0 | 7 | 1 | 2022-03-19 | 0 | 7 | 1
2022-03-19 01:00 | 1 | 7 | 1 | 2022-03-19 01:00 | 1 | 7 | 1
2022-03-19 02:00 | 2 | 7 | 1 | 2022-03-19 02:00 | 2 | 7 | 1
2022-03-19 03:00 | 3 | 7 | 1 | 2022-03-19 03:00 | 3 | 7 | 1
2022-03-19 04:00 | 4 | 7 | 1 | 2022-03-19 04:00 | 4 | 7 | 1
2022-03-19 05:00 | 5 | 7 | 1 | 2022-03-19 05:00 | 5 | 7 | 1
2022-03-19 06:00 | 6 | 7 | 1 | 2022-03-19 06:00 | 6 | 7 | 1
2022-03-19 07:00 | 7 | 7 | 1 | 2022-03-19 07:00 | 7 | 7 | 1
2022-03-19 08:00 | 8 | 7 | 1 | 2022-03-19 08:00 | 8 | 7 | 1
2022-03-19 09:00 | 9 | 7 | 1 | 2022-03-19 09:00 | 9 | 7 | 1
2022-03-19 10:00 | 10 | 7 | 1 | 2022-03-19 10:00 | 10 | 7 | 1
2022-03-19 11:00 | 11 | 7 | 1 | 2022-03-19 11:00 | 11 | 7 | 1
2022-03-19 12:00 | 12 | 7 | 1 | 2022-03-19 12:00 | 12 | 7 | 1
2022-03-19 13:00 | 13 | 7 | 1 | 2022-03-19 13:00 | 13 | 7 | 1
2022-03-19 14:00 | 14 | 7 | 1 | 2022-03-19 14:00 | 14 | 7 | 1
2022-03-19 15:00 | 15 | 7 | 1 | 2022-03-19 15:00 | 15 | 7 | 1
2022-03-19 16:00 | 16 | 7 | 1 | 2022-03-19 16:00 | 16 | 7 | 1
2022-03-19 17:00 | 17 | 7 | 1 | 2022-03-19 17:00 | 17 | 7 | 1
2022-03-19 18:00 | 18 | 7 | 1 | 2022-03-19 18:00 | 18 | 7 | 1
2022-03-19 19:00 | 19 | 7 | 1 | 2022-03-19 19:00 | 19 | 7 | 1
2022-03-19 20:00 | 20 | 7 | 1 | 2022-03-19 20:00 | 20 | 7 | 1
2022-03-19 21:00 | 21 | 7 | 1 | 2022-03-19 21:00 | 21 | 7 | 1
2022-03-19 22:00 | 22 | 7 | 1 | 2022-03-19 22:00 | 22 | 7 | 1
2022-03-19 23:00 | 23 | 7 | 1 | 2022-03-19 23:00 | 23 | 7 | 1
2022-03-20 | 0 | 1 | 1 | 2022-03-20 | 0 | 1 | 1
2022-03-20 01:00 | 1 | 1 | 1 | 2022-03-20 01:00 | 1 | 1 | 1
2022-03-20 02:00 | 2 | 1 | 1 | 2022-03-20 02:00 | 2 | 1 | 1
2022-03-20 03:00 | 3 | 1 | 1 | 2022-03-20 03:00 | 3 | 1 | 1
2022-03-20 04:00 | 4 | 1 | 1 | 2022-03-20 04:00 | 4 | 1 | 1
2022-03-20 05:00 | 5 | 1 | 1 | 2022-03-20 05:00 | 5 | 1 | 1
2022-03-20 06:00 | 6 | 1 | 1 | 2022-03-20 06:00 | 6 | 1 | 1
2022-03-20 07:00 | 7 | 1 | 1 | 2022-03-20 07:00 | 7 | 1 | 1
2022-03-20 08:00 | 8 | 1 | 1 | 2022-03-20 08:00 | 8 | 1 | 1
2022-03-20 09:00 | 9 | 1 | 1 | 2022-03-20 09:00 | 9 | 1 | 1
2022-03-20 10:00 | 10 | 1 | 1 | 2022-03-20 10:00 | 10 | 1 | 1
2022-03-20 11:00 | 11 | 1 | 1 | 2022-03-20 11:00 | 11 | 1 | 1
2022-03-20 12:00 | 12 | 1 | 1 | 2022-03-20 12:00 | 12 | 1 | 1
2022-03-20 13:00 | 13 | 1 | 1 | 2022-03-20 13:00 | 13 | 1 | 1
2022-03-20 14:00 | 14 | 1 | 1 | 2022-03-20 14:00 | 14 | 1 | 1
2022-03-20 15:00 | 15 | 1 | 1 | 2022-03-20 15:00 | 15 | 1 | 1
2022-03-20 16:00 | 16 | 1 | 1 | 2022-03-20 16:00 | 16 | 1 | 1
2022-03-20 17:00 | 17 | 1 | 1 | 2022-03-20 17:00 | 17 | 1 | 1
2022-03-20 18:00 | 18 | 1 | 1 | 2022-03-20 18:00 | 18 | 1 | 1
2022-03-20 19:00 | 19 | 1 | 1 | 2022-03-20 19:00 | 19 | 1 | 1
2022-03-20 20:00 | 20 | 1 | 1 | 2022-03-20 20:00 | 20 | 1 | 1
2022-03-20 21:00 | 21 | 1 | 1 | 2022-03-20 21:00 | 21 | 1 | 1
2022-03-20 22:00 | 22 | 1 | 1 | 2022-03-20 22:00 | 22 | 1 | 1
2022-03-20 23:00 | 23 | 1 | 1 | 2022-03-20 23:00 | 23 | 1 | 1
2022-03-21 | 0 | 2 | 1 | 2022-03-21 | 0 | 2 | 1
2022-03-21 01:00 | 1 | 2 | 1 | 2022-03-21 01:00 | 1 | 2 | 1
2022-03-21 02:00 | 2 | 2 | 1 | 2022-03-21 02:00 | 2 | 2 | 1
2022-03-21 03:00 | 3 | 2 | 1 | 2022-03-21 03:00 | 3 | 2 | 1
2022-03-21 04:00 | 4 | 2 | 1 | 2022-03-21 04:00 | 4 | 2 | 1
2022-03-21 05:00 | 5 | 2 | 1 | 2022-03-21 05:00 | 5 | 2 | 1
2022-03-21 06:00 | 6 | 2 | 1 | 2022-03-21 06:00 | 6 | 2 | 1
2022-03-21 07:00 | 7 | 2 | 1 | 2022-03-21 07:00 | 7 | 2 | 1
2022-03-21 08:00 | 8 | 2 | 1 | 2022-03-21 08:00 | 8 | 2 | 1
2022-03-21 09:00 | 9 | 2 | 1 | 2022-03-21 09:00 | 9 | 2 | 1
2022-03-21 10:00 | 10 | 2 | 1 | 2022-03-21 10:00 | 10 | 2 | 1
2022-03-21 11:00 | 11 | 2 | 1 | 2022-03-21 11:00 | 11 | 2 | 1
2022-03-21 12:00 | 12 | 2 | 1 | 2022-03-21 12:00 | 12 | 2 | 1
2022-03-21 13:00 | 13 | 2 | 1 | 2022-03-21 13:00 | 13 | 2 | 1
2022-03-21 14:00 | 14 | 2 | 1 | 2022-03-21 14:00 | 14 | 2 | 1
2022-03-21 15:00 | 15 | 2 | 1 | 2022-03-21 15:00 | 15 | 2 | 1
2022-03-21 16:00 | 16 | 2 | 1 | 2022-03-21 16:00 | 16 | 2 | 1
2022-03-21 17:00 | 17 | 2 | 1 | 2022-03-21 17:00 | 17 | 2 | 1
2022-03-21 18:00 | 18 | 2 | 1 | 2022-03-21 18:00 | 18 | 2 | 1
2022-03-21 19:00 | 19 | 2 | 1 | 2022-03-21 19:00 | 19 | 2 | 1
2022-03-21 20:00 | 20 | 2 | 1 | 2022-03-21 20:00 | 20 | 2 | 1
2022-03-21 21:00 | 21 | 2 | 1 | 2022-03-21 21:00 | 21 | 2 | 1
2022-03-21 22:00 | 22 | 2 | 1 | 2022-03-21 22:00 | 22 | 2 | 1
2022-03-21 23:00 | 23 | 2 | 1 | 2022-03-21 23:00 | 23 | 2 | 1
2022-03-22 | 0 | 3 | 1 | 2022-03-22 | 0 | 3 | 1
2022-03-22 01:00 | 1 | 3 | 1 | 2022-03-22 01:00 | 1 | 3 | 1
2022-03-22 02:00 | 2 | 3 | 1 | 2022-03-22 02:00 | 2 | 3 | 1
2022-03-22 03:00 | 3 | 3 | 1 | 2022-03-22 03:00 | 3 | 3 | 1
2022-03-22 04:00 | 4 | 3 | 1 | 2022-03-22 04:00 | 4 | 3 | 1
2022-03-22 05:00 | 5 | 3 | 1 | 2022-03-22 05:00 | 5 | 3 | 1
2022-03-22 06:00 | 6 | 3 | 1 | 2022-03-22 06:00 | 6 | 3 | 1
2022-03-22 07:00 | 7 | 3 | 1 | 2022-03-22 07:00 | 7 | 3 | 1
2022-03-22 08:00 | 8 | 3 | 1 | 2022-03-22 08:00 | 8 | 3 | 1
2022-03-22 09:00 | 9 | 3 | 1 | 2022-03-22 09:00 | 9 | 3 | 1
2022-03-22 10:00 | 10 | 3 | 1 | 2022-03-22 10:00 | 10 | 3 | 1
2022-03-22 11:00 | 11 | 3 | 1 | 2022-03-22 11:00 | 11 | 3 | 1
2022-03-22 12:00 | 12 | 3 | 1 | 2022-03-22 12:00 | 12 | 3 | 1
2022-03-22 13:00 | 13 | 3 | 1 | 2022-03-22 13:00 | 13 | 3 | 1
2022-03-22 14:00 | 14 | 3 | 1 | 2022-03-22 14:00 | 14 | 3 | 1
2022-03-22 15:00 | 15 | 3 | 1 | 2022-03-22 15:00 | 15 | 3 | 1
2022-03-22 16:00 | 16 | 3 | 1 | 2022-03-22 16:00 | 16 | 3 | 1
2022-03-22 17:00 | 17 | 3 | 1 | 2022-03-22 17:00 | 17 | 3 | 1
2022-03-22 18:00 | 18 | 3 | 1 | 2022-03-22 18:00 | 18 | 3 | 1
2022-03-22 19:00 | 19 | 3 | 1 | 2022-03-22 19:00 | 19 | 3 | 1
2022-03-22 20:00 | 20 | 3 | 1 | 2022-03-22 20:00 | 20 | 3 | 1
2022-03-22 21:00 | 21 | 3 | 1 | 2022-03-22 21:00 | 21 | 3 | 1
2022-03-22 22:00 | 22 | 3 | 1 | 2022-03-22 22:00 | 22 | 3 | 1
2022-03-22 23:00 | 23 | 3 | 1 | 2022-03-22 23:00 | 23 | 3 | 1
2022-03-23 | 0 | 4 | 1 | 2022-03-23 | 0 | 4 | 1
2022-03-23 01:00 | 1 | 4 | 1 | 2022-03-23 01:00 | 1 | 4 | 1
2022-03-23 02:00 | 2 | 4 | 1 | 2022-03-23 02:00 | 2 | 4 | 1
2022-03-23 03:00 | 3 | 4 | 1 | 2022-03-23 03:00 | 3 | 4 | 1
2022-03-23 04:00 | 4 | 4 | 1 | 2022-03-23 04:00 | 4 | 4 | 1
2022-03-23 05:00 | 5 | 4 | 1 | 2022-03-23 05:00 | 5 | 4 | 1
2022-03-23 06:00 | 6 | 4 | 1 | 2022-03-23 06:00 | 6 | 4 | 1
2022-03-23 07:00 | 7 | 4 | 1 | 2022-03-23 07:00 | 7 | 4 | 1
2022-03-23 08:00 | 8 | 4 | 1 | 2022-03-23 08:00 | 8 | 4 | 1
2022-03-23 09:00 | 9 | 4 | 1 | 2022-03-23 09:00 | 9 | 4 | 1
2022-03-23 10:00 | 10 | 4 | 1 | 2022-03-23 10:00 | 10 | 4 | 1
2022-03-23 11:00 | 11 | 4 | 1 | 2022-03-23 11:00 | 11 | 4 | 1
2022-03-23 12:00 | 12 | 4 | 1 | 2022-03-23 12:00 | 12 | 4 | 1
2022-03-23 13:00 | 13 | 4 | 1 | 2022-03-23 13:00 | 13 | 4 | 1
2022-03-23 14:00 | 14 | 4 | 1 | 2022-03-23 14:00 | 14 | 4 | 1
2022-03-23 15:00 | 15 | 4 | 1 | 2022-03-23 15:00 | 15 | 4 | 1
2022-03-23 16:00 | 16 | 4 | 1 | 2022-03-23 16:00 | 16 | 4 | 1
2022-03-23 17:00 | 17 | 4 | 1 | 2022-03-23 17:00 | 17 | 4 | 1
2022-03-23 18:00 | 18 | 4 | 1 | 2022-03-23 18:00 | 18 | 4 | 1
2022-03-23 19:00 | 19 | 4 | 1 | 2022-03-23 19:00 | 19 | 4 | 1
2022-03-23 20:00 | 20 | 4 | 1 | 2022-03-23 20:00 | 20 | 4 | 1
2022-03-23 21:00 | 21 | 4 | 1 | 2022-03-23 21:00 | 21 | 4 | 1
2022-03-23 22:00 | 22 | 4 | 1 | 2022-03-23 22:00 | 22 | 4 | 1
2022-03-23 23:00 | 23 | 4 | 1 | 2022-03-23 23:00 | 23 | 4 | 1
2022-03-24 | 0 | 5 | 1 | 2022-03-24 | 0 | 5 | 1
2022-03-24 01:00 | 1 | 5 | 1 | 2022-03-24 01:00 | 1 | 5 | 1
2022-03-24 02:00 | 2 | 5 | 1 | 2022-03-24 02:00 | 2 | 5 | 1
2022-03-24 03:00 | 3 | 5 | 1 | 2022-03-24 03:00 | 3 | 5 | 1
2022-03-24 04:00 | 4 | 5 | 1 | 2022-03-24 04:00 | 4 | 5 | 1
2022-03-24 05:00 | 5 | 5 | 1 | 2022-03-24 05:00 | 5 | 5 | 1
2022-03-24 06:00 | 6 | 5 | 1 | 2022-03-24 06:00 | 6 | 5 | 1
2022-03-24 07:00 | 7 | 5 | 1 | 2022-03-24 07:00 | 7 | 5 | 1
2022-03-24 08:00 | 8 | 5 | 1 | 2022-03-24 08:00 | 8 | 5 | 1
2022-03-24 09:00 | 9 | 5 | 1 | 2022-03-24 09:00 | 9 | 5 | 1
2022-03-24 10:00 | 10 | 5 | 1 | 2022-03-24 10:00 | 10 | 5 | 1
2022-03-24 11:00 | 11 | 5 | 1 | 2022-03-24 11:00 | 11 | 5 | 1
2022-03-24 12:00 | 12 | 5 | 1 | 2022-03-24 12:00 | 12 | 5 | 1
2022-03-24 13:00 | 13 | 5 | 1 | 2022-03-24 13:00 | 13 | 5 | 1
2022-03-24 14:00 | 14 | 5 | 1 | 2022-03-24 14:00 | 14 | 5 | 1
2022-03-24 15:00 | 15 | 5 | 1 | 2022-03-24 15:00 | 15 | 5 | 1
2022-03-24 16:00 | 16 | 5 | 1 | 2022-03-24 16:00 | 16 | 5 | 1
2022-03-24 17:00 | 17 | 5 | 1 | 2022-03-24 17:00 | 17 | 5 | 1
2022-03-24 18:00 | 18 | 5 | 1 | 2022-03-24 18:00 | 18 | 5 | 1
2022-03-24 19:00 | 19 | 5 | 1 | 2022-03-24 19:00 | 19 | 5 | 1
2022-03-24 20:00 | 20 | 5 | 1 | 2022-03-24 20:00 | 20 | 5 | 1
2022-03-24 21:00 | 21 | 5 | 1 | 2022-03-24 21:00 | 21 | 5 | 1
2022-03-24 22:00 | 22 | 5 | 1 | 2022-03-24 22:00 | 22 | 5 | 1
2022-03-24 23:00 | 23 | 5 | 1 | 2022-03-24 23:00 | 23 | 5 | 1
2022-03-25 | 0 | 6 | 1 | 2022-03-25 | 0 | 6 | 1
2022-03-25 01:00 | 1 | 6 | 1 | 2022-03-25 01:00 | 1 | 6 | 1
2022-03-25 02:00 | 2 | 6 | 1 | 2022-03-25 02:00 | 2 | 6 | 1
2022-03-25 03:00 | 3 | 6 | 1 | 2022-03-25 03:00 | 3 | 6 | 1
2022-03-25 04:00 | 4 | 6 | 1 | 2022-03-25 04:00 | 4 | 6 | 1
2022-03-25 05:00 | 5 | 6 | 1 | 2022-03-25 05:00 | 5 | 6 | 1
2022-03-25 06:00 | 6 | 6 | 1 | 2022-03-25 06:00 | 6 | 6 | 1
2022-03-25 07:00 | 7 | 6 | 1 | 2022-03-25 07:00 | 7 | 6 | 1
2022-03-25 08:00 | 8 | 6 | 1 | 2022-03-25 08:00 | 8 | 6 | 1
2022-03-25 09:00 | 9 | 6 | 1 | 2022-03-25 09:00 | 9 | 6 | 1
2022-03-25 10:00 | 10 | 6 | 1 | 2022-03-25 10:00 | 10 | 6 | 1
2022-03-25 11:00 | 11 | 6 | 1 | 2022-03-25 11:00 | 11 | 6 | 1
2022-03-25 12:00 | 12 | 6 | 1 | 2022-03-25 12:00 | 12 | 6 | 1
2022-03-25 13:00 | 13 | 6 | 1 | 2022-03-25 13:00 | 13 | 6 | 1
2022-03-25 14:00 | 14 | 6 | 1 | 2022-03-25 14:00 | 14 | 6 | 1
2022-03-25 15:00 | 15 | 6 | 1 | 2022-03-25 15:00 | 15 | 6 | 1
2022-03-25 16:00 | 16 | 6 | 1 | 2022-03-25 16:00 | 16 | 6 | 1
2022-03-25 17:00 | 17 | 6 | 1 | 2022-03-25 17:00 | 17 | 6 | 1
2022-03-25 18:00 | 18 | 6 | 1 | 2022-03-25 18:00 | 18 | 6 | 1
2022-03-25 19:00 | 19 | 6 | 1 | 2022-03-25 19:00 | 19 | 6 | 1
2022-03-25 20:00 | 20 | 6 | 1 | 2022-03-25 20:00 | 20 | 6 | 1
2022-03-25 21:00 | 21 | 6 | 1 | 2022-03-25 21:00 | 21 | 6 | 1
2022-03-25 22:00 | 22 | 6 | 1 | 2022-03-25 22:00 | 22 | 6 | 1
2022-03-25 23:00 | 23 | 6 | 1 | 2022-03-25 23:00 | 23 | 6 | 1
2022-03-26 | 0 | 7 | 1 | 2022-03-26 | 0 | 7 | 1
2022-03-26 01:00 | 1 | 7 | 1 | 2022-03-26 01:00 | 1 | 7 | 1
2022-03-26 02:00 | 2 | 7 | 1 | 2022-03-26 02:00 | 2 | 7 | 1
2022-03-26 03:00 | 3 | 7 | 1 | 2022-03-26 03:00 | 3 | 7 | 1
2022-03-26 04:00 | 4 | 7 | 1 | 2022-03-26 04:00 | 4 | 7 | 1
2022-03-26 05:00 | 5 | 7 | 1 | 2022-03-26 05:00 | 5 | 7 | 1
2022-03-26 06:00 | 6 | 7 | 1 | 2022-03-26 06:00 | 6 | 7 | 1
2022-03-26 07:00 | 7 | 7 | 1 | 2022-03-26 07:00 | 7 | 7 | 1
2022-03-26 08:00 | 8 | 7 | 1 | 2022-03-26 08:00 | 8 | 7 | 1
2022-03-26 09:00 | 9 | 7 | 1 | 2022-03-26 09:00 | 9 | 7 | 1
2022-03-26 10:00 | 10 | 7 | 1 | 2022-03-26 10:00 | 10 | 7 | 1
2022-03-26 11:00 | 11 | 7 | 1 | 2022-03-26 11:00 | 11 | 7 | 1
2022-03-26 12:00 | 12 | 7 | 1 | 2022-03-26 12:00 | 12 | 7 | 1
2022-03-26 13:00 | 13 | 7 | 1 | 2022-03-26 13:00 | 13 | 7 | 1
2022-03-26 14:00 | 14 | 7 | 1 | 2022-03-26 14:00 | 14 | 7 | 1
2022-03-26 15:00 | 15 | 7 | 1 | 2022-03-26 15:00 | 15 | 7 | 1
2022-03-26 16:00 | 16 | 7 | 1 | 2022-03-26 16:00 | 16 | 7 | 1
2022-03-26 17:00 | 17 | 7 | 1 | 2022-03-26 17:00 | 17 | 7 | 1
2022-03-26 18:00 | 18 | 7 | 1 | 2022-03-26 18:00 | 18 | 7 | 1
2022-03-26 19:00 | 19 | 7 | 1 | 2022-03-26 19:00 | 19 | 7 | 1
2022-03-26 20:00 | 20 | 7 | 1 | 2022-03-26 20:00 | 20 | 7 | 1
2022-03-26 21:00 | 21 | 7 | 1 | 2022-03-26 21:00 | 21 | 7 | 1
2022-03-26 22:00 | 22 | 7 | 1 | 2022-03-26 22:00 | 22 | 7 | 1
2022-03-26 23:00 | 23 | 7 | 1 | 2022-03-26 23:00 | 23 | 7 | 1
2022-03-27 | 0 | 1 | 1 | 2022-03-27 | 0 | 1 | 1
2022-03-27 01:00 | 1 | 1 | 1 | 2022-03-27 01:00 | 1 | 1 | 1
2022-03-27 02:00 | 2 | 1 | 1 | 2022-03-27 02:00 | 2 | 1 | 1
2022-03-27 03:00 | 3 | 1 | 1 | 2022-03-27 03:00 | 3 | 1 | 1
2022-03-27 04:00 | 4 | 1 | 1 | 2022-03-27 04:00 | 4 | 1 | 1
2022-03-27 05:00 | 5 | 1 | 1 | 2022-03-27 05:00 | 5 | 1 | 1
2022-03-27 06:00 | 6 | 1 | 1 | 2022-03-27 06:00 | 6 | 1 | 1
2022-03-27 07:00 | 7 | 1 | 1 | 2022-03-27 07:00 | 7 | 1 | 1
2022-03-27 08:00 | 8 | 1 | 1 | 2022-03-27 08:00 | 8 | 1 | 1
2022-03-27 09:00 | 9 | 1 | 1 | 2022-03-27 09:00 | 9 | 1 | 1
2022-03-27 10:00 | 10 | 1 | 1 | 2022-03-27 10:00 | 10 | 1 | 1
2022-03-27 11:00 | 11 | 1 | 1 | 2022-03-27 11:00 | 11 | 1 | 1
2022-03-27 12:00 | 12 | 1 | 1 | 2022-03-27 12:00 | 12 | 1 | 1
2022-03-27 13:00 | 13 | 1 | 1 | 2022-03-27 13:00 | 13 | 1 | 1
2022-03-27 14:00 | 14 | 1 | 1 | 2022-03-27 14:00 | 14 | 1 | 1
2022-03-27 15:00 | 15 | 1 | 1 | 2022-03-27 15:00 | 15 | 1 | 1
2022-03-27 16:00 | 16 | 1 | 1 | 2022-03-27 16:00 | 16 | 1 | 1
2022-03-27 17:00 | 17 | 1 | 1 | 2022-03-27 17:00 | 17 | 1 | 1
2022-03-27 18:00 | 18 | 1 | 1 | 2022-03-27 18:00 | 18 | 1 | 1
2022-03-27 19:00 | 19 | 1 | 1 | 2022-03-27 19:00 | 19 | 1 | 1
2022-03-27 20:00 | 20 | 1 | 1 | 2022-03-27 20:00 | 20 | 1 | 1
2022-03-27 21:00 | 21 | 1 | 1 | 2022-03-27 21:00 | 21 | 1 | 1
2022-03-27 22:00 | 22 | 1 | 1 | 2022-03-27 22:00 | 22 | 1 | 1
2022-03-27 23:00 | 23 | 1 | 1 | 2022-03-27 23:00 | 23 | 1 | 1
2022-03-28 | 0 | 2 | 1 | 2022-03-28 | 0 | 2 | 1
2022-03-28 01:00 | 1 | 2 | 1 | 2022-03-28 01:00 | 1 | 2 | 1
2022-03-28 02:00 | 2 | 2 | 1 | 2022-03-28 02:00 | 2 | 2 | 1
2022-03-28 03:00 | 3 | 2 | 1 | 2022-03-28 03:00 | 3 | 2 | 1
2022-03-28 04:00 | 4 | 2 | 1 | 2022-03-28 04:00 | 4 | 2 | 1
2022-03-28 05:00 | 5 | 2 | 1 | 2022-03-28 05:00 | 5 | 2 | 1
2022-03-28 06:00 | 6 | 2 | 1 | 2022-03-28 06:00 | 6 | 2 | 1
2022-03-28 07:00 | 7 | 2 | 1 | 2022-03-28 07:00 | 7 | 2 | 1
2022-03-28 08:00 | 8 | 2 | 1 | 2022-03-28 08:00 | 8 | 2 | 1
2022-03-28 09:00 | 9 | 2 | 1 | 2022-03-28 09:00 | 9 | 2 | 1
2022-03-28 10:00 | 10 | 2 | 1 | 2022-03-28 10:00 | 10 | 2 | 1
2022-03-28 11:00 | 11 | 2 | 1 | 2022-03-28 11:00 | 11 | 2 | 1
2022-03-28 12:00 | 12 | 2 | 1 | 2022-03-28 12:00 | 12 | 2 | 1
2022-03-28 13:00 | 13 | 2 | 1 | 2022-03-28 13:00 | 13 | 2 | 1
2022-03-28 14:00 | 14 | 2 | 1 | 2022-03-28 14:00 | 14 | 2 | 1
2022-03-28 15:00 | 15 | 2 | 1 | 2022-03-28 15:00 | 15 | 2 | 1
2022-03-28 16:00 | 16 | 2 | 1 | 2022-03-28 16:00 | 16 | 2 | 1
2022-03-28 17:00 | 17 | 2 | 1 | 2022-03-28 17:00 | 17 | 2 | 1
2022-03-28 18:00 | 18 | 2 | 1 | 2022-03-28 18:00 | 18 | 2 | 1
2022-03-28 19:00 | 19 | 2 | 1 | 2022-03-28 19:00 | 19 | 2 | 1
2022-03-28 20:00 | 20 | 2 | 1 | 2022-03-28 20:00 | 20 | 2 | 1
2022-03-28 21:00 | 21 | 2 | 1 | 2022-03-28 21:00 | 21 | 2 | 1
2022-03-28 22:00 | 22 | 2 | 1 | 2022-03-28 22:00 | 22 | 2 | 1
2022-03-28 23:00 | 23 | 2 | 1 | 2022-03-28 23:00 | 23 | 2 | 1
2022-03-29 | 0 | 3 | 1 | 2022-03-29 | 0 | 3 | 1
2022-03-29 01:00 | 1 | 3 | 1 | 2022-03-29 01:00 | 1 | 3 | 1
2022-03-29 02:00 | 2 | 3 | 1 | 2022-03-29 02:00 | 2 | 3 | 1
2022-03-29 03:00 | 3 | 3 | 1 | 2022-03-29 03:00 | 3 | 3 | 1
2022-03-29 04:00 | 4 | 3 | 1 | 2022-03-29 04:00 | 4 | 3 | 1
2022-03-29 05:00 | 5 | 3 | 1 | 2022-03-29 05:00 | 5 | 3 | 1
2022-03-29 06:00 | 6 | 3 | 1 | 2022-03-29 06:00 | 6 | 3 | 1
2022-03-29 07:00 | 7 | 3 | 1 | 2022-03-29 07:00 | 7 | 3 | 1
2022-03-29 08:00 | 8 | 3 | 1 | 2022-03-29 08:00 | 8 | 3 | 1
2022-03-29 09:00 | 9 | 3 | 1 | 2022-03-29 09:00 | 9 | 3 | 1
2022-03-29 10:00 | 10 | 3 | 1 | 2022-03-29 10:00 | 10 | 3 | 1
2022-03-29 11:00 | 11 | 3 | 1 | 2022-03-29 11:00 | 11 | 3 | 1
2022-03-29 12:00 | 12 | 3 | 1 | 2022-03-29 12:00 | 12 | 3 | 1
2022-03-29 13:00 | 13 | 3 | 1 | 2022-03-29 13:00 | 13 | 3 | 1
2022-03-29 14:00 | 14 | 3 | 1 | 2022-03-29 14:00 | 14 | 3 | 1
2022-03-29 15:00 | 15 | 3 | 1 | 2022-03-29 15:00 | 15 | 3 | 1
2022-03-29 16:00 | 16 | 3 | 1 | 2022-03-29 16:00 | 16 | 3 | 1
2022-03-29 17:00 | 17 | 3 | 1 | 2022-03-29 17:00 | 17 | 3 | 1
2022-03-29 18:00 | 18 | 3 | 1 | 2022-03-29 18:00 | 18 | 3 | 1
2022-03-29 19:00 | 19 | 3 | 1 | 2022-03-29 19:00 | 19 | 3 | 1
2022-03-29 20:00 | 20 | 3 | 1 | 2022-03-29 20:00 | 20 | 3 | 1
2022-03-29 21:00 | 21 | 3 | 1 | 2022-03-29 21:00 | 21 | 3 | 1
2022-03-29 22:00 | 22 | 3 | 1 | 2022-03-29 22:00 | 22 | 3 | 1
2022-03-29 23:00 | 23 | 3 | 1 | 2022-03-29 23:00 | 23 | 3 | 1
2022-03-30 | 0 | 4 | 1 | 2022-03-30 | 0 | 4 | 1
2022-03-30 01:00 | 1 | 4 | 1 | 2022-03-30 01:00 | 1 | 4 | 1
2022-03-30 02:00 | 2 | 4 | 1 | 2022-03-30 02:00 | 2 | 4 | 1
2022-03-30 03:00 | 3 | 4 | 1 | 2022-03-30 03:00 | 3 | 4 | 1
2022-03-30 04:00 | 4 | 4 | 1 | 2022-03-30 04:00 | 4 | 4 | 1
2022-03-30 05:00 | 5 | 4 | 1 | 2022-03-30 05:00 | 5 | 4 | 1
2022-03-30 06:00 | 6 | 4 | 1 | 2022-03-30 06:00 | 6 | 4 | 1
2022-03-30 07:00 | 7 | 4 | 1 | 2022-03-30 07:00 | 7 | 4 | 1
2022-03-30 08:00 | 8 | 4 | 1 | 2022-03-30 08:00 | 8 | 4 | 1
2022-03-30 09:00 | 9 | 4 | 1 | 2022-03-30 09:00 | 9 | 4 | 1
2022-03-30 10:00 | 10 | 4 | 1 | 2022-03-30 10:00 | 10 | 4 | 1
2022-03-30 11:00 | 11 | 4 | 1 | 2022-03-30 11:00 | 11 | 4 | 1
2022-03-30 12:00 | 12 | 4 | 1 | 2022-03-30 12:00 | 12 | 4 | 1
2022-03-30 13:00 | 13 | 4 | 1 | 2022-03-30 13:00 | 13 | 4 | 1
2022-03-30 14:00 | 14 | 4 | 1 | 2022-03-30 14:00 | 14 | 4 | 1
2022-03-30 15:00 | 15 | 4 | 1 | 2022-03-30 15:00 | 15 | 4 | 1
2022-03-30 16:00 | 16 | 4 | 1 | 2022-03-30 16:00 | 16 | 4 | 1
2022-03-30 17:00 | 17 | 4 | 1 | 2022-03-30 17:00 | 17 | 4 | 1
2022-03-30 18:00 | 18 | 4 | 1 | 2022-03-30 18:00 | 18 | 4 | 1
2022-03-30 19:00 | 19 | 4 | 1 | 2022-03-30 19:00 | 19 | 4 | 1
2022-03-30 20:00 | 20 | 4 | 1 | 2022-03-30 20:00 | 20 | 4 | 1
2022-03-30 21:00 | 21 | 4 | 1 | 2022-03-30 21:00 | 21 | 4 | 1
2022-03-30 22:00 | 22 | 4 | 1 | 2022-03-30 22:00 | 22 | 4 | 1
2022-03-30 23:00 | 23 | 4 | 1 | 2022-03-30 23:00 | 23 | 4 | 1
2022-03-31 | 0 | 5 | 1 | 2022-03-31 | 0 | 5 | 1
2022-03-31 01:00 | 1 | 5 | 1 | 2022-03-31 01:00 | 1 | 5 | 1
2022-03-31 02:00 | 2 | 5 | 1 | 2022-03-31 02:00 | 2 | 5 | 1
2022-03-31 03:00 | 3 | 5 | 1 | 2022-03-31 03:00 | 3 | 5 | 1
2022-03-31 04:00 | 4 | 5 | 1 | 2022-03-31 04:00 | 4 | 5 | 1
2022-03-31 05:00 | 5 | 5 | 1 | 2022-03-31 05:00 | 5 | 5 | 1
2022-03-31 06:00 | 6 | 5 | 1 | 2022-03-31 06:00 | 6 | 5 | 1
2022-03-31 07:00 | 7 | 5 | 1 | 2022-03-31 07:00 | 7 | 5 | 1
2022-03-31 08:00 | 8 | 5 | 1 | 2022-03-31 08:00 | 8 | 5 | 1
2022-03-31 09:00 | 9 | 5 | 1 | 2022-03-31 09:00 | 9 | 5 | 1
2022-03-31 10:00 | 10 | 5 | 1 | 2022-03-31 10:00 | 10 | 5 | 1
2022-03-31 11:00 | 11 | 5 | 1 | 2022-03-31 11:00 | 11 | 5 | 1
2022-03-31 12:00 | 12 | 5 | 1 | 2022-03-31 12:00 | 12 | 5 | 1
2022-03-31 13:00 | 13 | 5 | 1 | 2022-03-31 13:00 | 13 | 5 | 1
2022-03-31 14:00 | 14 | 5 | 1 | 2022-03-31 14:00 | 14 | 5 | 1
2022-03-31 15:00 | 15 | 5 | 1 | 2022-03-31 15:00 | 15 | 5 | 1
2022-03-31 16:00 | 16 | 5 | 1 | 2022-03-31 16:00 | 16 | 5 | 1
2022-03-31 17:00 | 17 | 5 | 1 | 2022-03-31 17:00 | 17 | 5 | 1
2022-03-31 18:00 | 18 | 5 | 1 | 2022-03-31 18:00 | 18 | 5 | 1
2022-03-31 19:00 | 19 | 5 | 1 | 2022-03-31 19:00 | 19 | 5 | 1
2022-03-31 20:00 | 20 | 5 | 1 | 2022-03-31 20:00 | 20 | 5 | 1
2022-03-31 21:00 | 21 | 5 | 1 | 2022-03-31 21:00 | 21 | 5 | 1
2022-03-31 22:00 | 22 | 5 | 1 | 2022-03-31 22:00 | 22 | 5 | 1
2022-03-31 23:00 | 23 | 5 | 1 | 2022-03-31 23:00 | 23 | 5 | 1
2022-04-01 | 0 | 6 | 1 | 2022-04-01 | 0 | 6 | 1
2022-04-01 01:00 | 1 | 6 | 1 | 2022-04-01 01:00 | 1 | 6 | 1
2022-04-01 02:00 | 2 | 6 | 1 | 2022-04-01 02:00 | 2 | 6 | 1
2022-04-01 03:00 | 3 | 6 | 1 | 2022-04-01 03:00 | 3 | 6 | 1
2022-04-01 04:00 | 4 | 6 | 1 | 2022-04-01 04:00 | 4 | 6 | 1
2022-04-01 05:00 | 5 | 6 | 1 | 2022-04-01 05:00 | 5 | 6 | 1
2022-04-01 06:00 | 6 | 6 | 1 | 2022-04-01 06:00 | 6 | 6 | 1
2022-04-01 07:00 | 7 | 6 | 1 | 2022-04-01 07:00 | 7 | 6 | 1
2022-04-01 08:00 | 8 | 6 | 1 | 2022-04-01 08:00 | 8 | 6 | 1
2022-04-01 09:00 | 9 | 6 | 1 | 2022-04-01 09:00 | 9 | 6 | 1
2022-04-01 10:00 | 10 | 6 | 1 | 2022-04-01 10:00 | 10 | 6 | 1
2022-04-01 11:00 | 11 | 6 | 1 | 2022-04-01 11:00 | 11 | 6 | 1
2022-04-01 12:00 | 12 | 6 | 1 | 2022-04-01 12:00 | 12 | 6 | 1
2022-04-01 13:00 | 13 | 6 | 1 | 2022-04-01 13:00 | 13 | 6 | 1
2022-04-01 14:00 | 14 | 6 | 1 | 2022-04-01 14:00 | 14 | 6 | 1
2022-04-01 15:00 | 15 | 6 | 1 | 2022-04-01 15:00 | 15 | 6 | 1
2022-04-01 16:00 | 16 | 6 | 1 | 2022-04-01 16:00 | 16 | 6 | 1
2022-04-01 17:00 | 17 | 6 | 1 | 2022-04-01 17:00 | 17 | 6 | 1
2022-04-01 18:00 | 18 | 6 | 1 | 2022-04-01 18:00 | 18 | 6 | 1
2022-04-01 19:00 | 19 | 6 | 1 | 2022-04-01 19:00 | 19 | 6 | 1
2022-04-01 20:00 | 20 | 6 | 1 | 2022-04-01 20:00 | 20 | 6 | 1
2022-04-01 21:00 | 21 | 6 | 1 | 2022-04-01 21:00 | 21 | 6 | 1
2022-04-01 22:00 | 22 | 6 | 1 | 2022-04-01 22:00 | 22 | 6 | 1
2022-04-01 23:00 | 23 | 6 | 1 | 2022-04-01 23:00 | 23 | 6 | 1
2022-04-02 | 0 | 7 | 1 | 2022-04-02 | 0 | 7 | 1
2022-04-02 01:00 | 1 | 7 | 1 | 2022-04-02 01:00 | 1 | 7 | 1
2022-04-02 02:00 | 2 | 7 | 1 | 2022-04-02 02:00 | 2 | 7 | 1
2022-04-02 03:00 | 3 | 7 | 1 | 2022-04-02 03:00 | 3 | 7 | 1
2022-04-02 04:00 | 4 | 7 | 1 | 2022-04-02 04:00 | 4 | 7 | 1
2022-04-02 05:00 | 5 | 7 | 1 | 2022-04-02 05:00 | 5 | 7 | 1
2022-04-02 06:00 | 6 | 7 | 1 | 2022-04-02 06:00 | 6 | 7 | 1
2022-04-02 07:00 | 7 | 7 | 1 | 2022-04-02 07:00 | 7 | 7 | 1
2022-04-02 08:00 | 8 | 7 | 1 | 2022-04-02 08:00 | 8 | 7 | 1
2022-04-02 09:00 | 9 | 7 | 1 | 2022-04-02 09:00 | 9 | 7 | 1
2022-04-02 10:00 | 10 | 7 | 1 | 2022-04-02 10:00 | 10 | 7 | 1
2022-04-02 11:00 | 11 | 7 | 1 | 2022-04-02 11:00 | 11 | 7 | 1
2022-04-02 12:00 | 12 | 7 | 1 | 2022-04-02 12:00 | 12 | 7 | 1
2022-04-02 13:00 | 13 | 7 | 1 | 2022-04-02 13:00 | 13 | 7 | 1
2022-04-02 14:00 | 14 | 7 | 1 | 2022-04-02 14:00 | 14 | 7 | 1
2022-04-02 15:00 | 15 | 7 | 1 | 2022-04-02 15:00 | 15 | 7 | 1
2022-04-02 16:00 | 16 | 7 | 1 | 2022-04-02 16:00 | 16 | 7 | 1
2022-04-02 17:00 | 17 | 7 | 1 | 2022-04-02 17:00 | 17 | 7 | 1
2022-04-02 18:00 | 18 | 7 | 1 | 2022-04-02 18:00 | 18 | 7 | 1
2022-04-02 19:00 | 19 | 7 | 1 | 2022-04-02 19:00 | 19 | 7 | 1
2022-04-02 20:00 | 20 | 7 | 1 | 2022-04-02 20:00 | 20 | 7 | 1
2022-04-02 21:00 | 21 | 7 | 1 | 2022-04-02 21:00 | 21 | 7 | 1
2022-04-02 22:00 | 22 | 7 | 1 | 2022-04-02 22:00 | 22 | 7 | 1
2022-04-02 23:00 | 23 | 7 | 1 | 2022-04-02 23:00 | 23 | 7 | 1
2022-04-03 | 0 | 1 | 1 | 2022-04-03 | 0 | 1 | 1
2022-04-03 01:00 | 1 | 1 | 1 | 2022-04-03 01:00 | 1 | 1 | 1
2022-04-03 02:00 | 2 | 1 | 1 | 2022-04-03 02:00 | 2 | 1 | 1
2022-04-03 03:00 | 3 | 1 | 1 | 2022-04-03 03:00 | 3 | 1 | 1
2022-04-03 04:00 | 4 | 1 | 1 | 2022-04-03 04:00 | 4 | 1 | 1
2022-04-03 05:00 | 5 | 1 | 1 | 2022-04-03 05:00 | 5 | 1 | 1
2022-04-03 06:00 | 6 | 1 | 1 | 2022-04-03 06:00 | 6 | 1 | 1
2022-04-03 07:00 | 7 | 1 | 1 | 2022-04-03 07:00 | 7 | 1 | 1
2022-04-03 08:00 | 8 | 1 | 1 | 2022-04-03 08:00 | 8 | 1 | 1
2022-04-03 09:00 | 9 | 1 | 1 | 2022-04-03 09:00 | 9 | 1 | 1
2022-04-03 10:00 | 10 | 1 | 1 | 2022-04-03 10:00 | 10 | 1 | 1
2022-04-03 11:00 | 11 | 1 | 1 | 2022-04-03 11:00 | 11 | 1 | 1
2022-04-03 12:00 | 12 | 1 | 1 | 2022-04-03 12:00 | 12 | 1 | 1
2022-04-03 13:00 | 13 | 1 | 1 | 2022-04-03 13:00 | 13 | 1 | 1
2022-04-03 14:00 | 14 | 1 | 1 | 2022-04-03 14:00 | 14 | 1 | 1
2022-04-03 15:00 | 15 | 1 | 1 | 2022-04-03 15:00 | 15 | 1 | 1
2022-04-03 16:00 | 16 | 1 | 1 | 2022-04-03 16:00 | 16 | 1 | 1
2022-04-03 17:00 | 17 | 1 | 1 | 2022-04-03 17:00 | 17 | 1 | 1
2022-04-03 18:00 | 18 | 1 | 1 | 2022-04-03 18:00 | 18 | 1 | 1
2022-04-03 19:00 | 19 | 1 | 1 | 2022-04-03 19:00 | 19 | 1 | 1
2022-04-03 20:00 | 20 | 1 | 1 | 2022-04-03 20:00 | 20 | 1 | 1
2022-04-03 21:00 | 21 | 1 | 1 | 2022-04-03 21:00 | 21 | 1 | 1
2022-04-03 22:00 | 22 | 1 | 1 | 2022-04-03 22:00 | 22 | 1 | 1
2022-04-03 23:00 | 23 | 1 | 1 | 2022-04-03 23:00 | 23 | 1 | 1
2022-04-04 | 0 | 2 | 1 | 2022-04-04 | 0 | 2 | 1
2022-04-04 01:00 | 1 | 2 | 1 | 2022-04-04 01:00 | 1 | 2 | 1
2022-04-04 02:00 | 2 | 2 | 1 | 2022-04-04 02:00 | 2 | 2 | 1
2022-04-04 03:00 | 3 | 2 | 1 | 2022-04-04 03:00 | 3 | 2 | 1
2022-04-04 04:00 | 4 | 2 | 1 | 2022-04-04 04:00 | 4 | 2 | 1
2022-04-04 05:00 | 5 | 2 | 1 | 2022-04-04 05:00 | 5 | 2 | 1
2022-04-04 06:00 | 6 | 2 | 1 | 2022-04-04 06:00 | 6 | 2 | 1
2022-04-04 07:00 | 7 | 2 | 1 | 2022-04-04 07:00 | 7 | 2 | 1
2022-04-04 08:00 | 8 | 2 | 1 | 2022-04-04 08:00 | 8 | 2 | 1
2022-04-04 09:00 | 9 | 2 | 1 | 2022-04-04 09:00 | 9 | 2 | 1
2022-04-04 10:00 | 10 | 2 | 1 | 2022-04-04 10:00 | 10 | 2 | 1
2022-04-04 11:00 | 11 | 2 | 1 | 2022-04-04 11:00 | 11 | 2 | 1
2022-04-04 12:00 | 12 | 2 | 1 | 2022-04-04 12:00 | 12 | 2 | 1
2022-04-04 13:00 | 13 | 2 | 1 | 2022-04-04 13:00 | 13 | 2 | 1
2022-04-04 14:00 | 14 | 2 | 1 | 2022-04-04 14:00 | 14 | 2 | 1
2022-04-04 15:00 | 15 | 2 | 1 | 2022-04-04 15:00 | 15 | 2 | 1
2022-04-04 16:00 | 16 | 2 | 1 | 2022-04-04 16:00 | 16 | 2 | 1
2022-04-04 17:00 | 17 | 2 | 1 | 2022-04-04 17:00 | 17 | 2 | 1
2022-04-04 18:00 | 18 | 2 | 1 | 2022-04-04 18:00 | 18 | 2 | 1
2022-04-04 19:00 | 19 | 2 | 1 | 2022-04-04 19:00 | 19 | 2 | 1
2022-04-04 20:00 | 20 | 2 | 1 | 2022-04-04 20:00 | 20 | 2 | 1
2022-04-04 21:00 | 21 | 2 | 1 | 2022-04-04 21:00 | 21 | 2 | 1
2022-04-04 22:00 | 22 | 2 | 1 | 2022-04-04 22:00 | 22 | 2 | 1
2022-04-04 23:00 | 23 | 2 | 1 | 2022-04-04 23:00 | 23 | 2 | 1
2022-04-05 | 0 | 3 | 1 | 2022-04-05 | 0 | 3 | 1
2022-04-05 01:00 | 1 | 3 | 1 | 2022-04-05 01:00 | 1 | 3 | 1
2022-04-05 02:00 | 2 | 3 | 1 | 2022-04-05 02:00 | 2 | 3 | 1
2022-04-05 03:00 | 3 | 3 | 1 | 2022-04-05 03:00 | 3 | 3 | 1
2022-04-05 04:00 | 4 | 3 | 1 | 2022-04-05 04:00 | 4 | 3 | 1
2022-04-05 05:00 | 5 | 3 | 1 | 2022-04-05 05:00 | 5 | 3 | 1
2022-04-05 06:00 | 6 | 3 | 1 | 2022-04-05 06:00 | 6 | 3 | 1
2022-04-05 07:00 | 7 | 3 | 1 | 2022-04-05 07:00 | 7 | 3 | 1
2022-04-05 08:00 | 8 | 3 | 1 | 2022-04-05 08:00 | 8 | 3 | 1
2022-04-05 09:00 | 9 | 3 | 1 | 2022-04-05 09:00 | 9 | 3 | 1
2022-04-05 10:00 | 10 | 3 | 1 | 2022-04-05 10:00 | 10 | 3 | 1
2022-04-05 11:00 | 11 | 3 | 1 | 2022-04-05 11:00 | 11 | 3 | 1
2022-04-05 12:00 | 12 | 3 | 1 | 2022-04-05 12:00 | 12 | 3 | 1
2022-04-05 13:00 | 13 | 3 | 1 | 2022-04-05 13:00 | 13 | 3 | 1
2022-04-05 14:00 | 14 | 3 | 1 | 2022-04-05 14:00 | 14 | 3 | 1
2022-04-05 15:00 | 15 | 3 | 1 | 2022-04-05 15:00 | 15 | 3 | 1
2022-04-05 16:00 | 16 | 3 | 1 | 2022-04-05 16:00 | 16 | 3 | 1
2022-04-05 17:00 | 17 | 3 | 1 | 2022-04-05 17:00 | 17 | 3 | 1
2022-04-05 18:00 | 18 | 3 | 1 | 2022-04-05 18:00 | 18 | 3 | 1
2022-04-05 19:00 | 19 | 3 | 1 | 2022-04-05 19:00 | 19 | 3 | 1
2022-04-05 20:00 | 20 | 3 | 1 | 2022-04-05 20:00 | 20 | 3 | 1
2022-04-05 21:00 | 21 | 3 | 1 | 2022-04-05 21:00 | 21 | 3 | 1
2022-04-05 22:00 | 22 | 3 | 1 | 2022-04-05 22:00 | 22 | 3 | 1
2022-04-05 23:00 | 23 | 3 | 1 | 2022-04-05 23:00 | 23 | 3 | 1
2022-04-06 | 0 | 4 | 1 | 2022-04-06 | 0 | 4 | 1
2022-04-06 01:00 | 1 | 4 | 1 | 2022-04-06 01:00 | 1 | 4 | 1
2022-04-06 02:00 | 2 | 4 | 1 | 2022-04-06 02:00 | 2 | 4 | 1
2022-04-06 03:00 | 3 | 4 | 1 | 2022-04-06 03:00 | 3 | 4 | 1
2022-04-06 04:00 | 4 | 4 | 1 | 2022-04-06 04:00 | 4 | 4 | 1
2022-04-06 05:00 | 5 | 4 | 1 | 2022-04-06 05:00 | 5 | 4 | 1
2022-04-06 06:00 | 6 | 4 | 1 | 2022-04-06 06:00 | 6 | 4 | 1
2022-04-06 07:00 | 7 | 4 | 1 | 2022-04-06 07:00 | 7 | 4 | 1
2022-04-06 08:00 | 8 | 4 | 1 | 2022-04-06 08:00 | 8 | 4 | 1
2022-04-06 09:00 | 9 | 4 | 1 | 2022-04-06 09:00 | 9 | 4 | 1
2022-04-06 10:00 | 10 | 4 | 1 | 2022-04-06 10:00 | 10 | 4 | 1
2022-04-06 11:00 | 11 | 4 | 1 | 2022-04-06 11:00 | 11 | 4 | 1
2022-04-06 12:00 | 12 | 4 | 1 | 2022-04-06 12:00 | 12 | 4 | 1
2022-04-06 13:00 | 13 | 4 | 1 | 2022-04-06 13:00 | 13 | 4 | 1
2022-04-06 14:00 | 14 | 4 | 1 | 2022-04-06 14:00 | 14 | 4 | 1
2022-04-06 15:00 | 15 | 4 | 1 | 2022-04-06 15:00 | 15 | 4 | 1
2022-04-06 16:00 | 16 | 4 | 1 | 2022-04-06 16:00 | 16 | 4 | 1
2022-04-06 17:00 | 17 | 4 | 1 | 2022-04-06 17:00 | 17 | 4 | 1
2022-04-06 18:00 | 18 | 4 | 1 | 2022-04-06 18:00 | 18 | 4 | 1
2022-04-06 19:00 | 19 | 4 | 1 | 2022-04-06 19:00 | 19 | 4 | 1
2022-04-06 20:00 | 20 | 4 | 1 | 2022-04-06 20:00 | 20 | 4 | 1
2022-04-06 21:00 | 21 | 4 | 1 | 2022-04-06 21:00 | 21 | 4 | 1
2022-04-06 22:00 | 22 | 4 | 1 | 2022-04-06 22:00 | 22 | 4 | 1
2022-04-06 23:00 | 23 | 4 | 1 | 2022-04-06 23:00 | 23 | 4 | 1
2022-04-07 | 0 | 5 | 1 | 2022-04-07 | 0 | 5 | 1
2022-04-07 01:00 | 1 | 5 | 1 | 2022-04-07 01:00 | 1 | 5 | 1
2022-04-07 02:00 | 2 | 5 | 1 | 2022-04-07 02:00 | 2 | 5 | 1
2022-04-07 03:00 | 3 | 5 | 1 | 2022-04-07 03:00 | 3 | 5 | 1
2022-04-07 04:00 | 4 | 5 | 1 | 2022-04-07 04:00 | 4 | 5 | 1
2022-04-07 05:00 | 5 | 5 | 1 | 2022-04-07 05:00 | 5 | 5 | 1
2022-04-07 06:00 | 6 | 5 | 1 | 2022-04-07 06:00 | 6 | 5 | 1
2022-04-07 07:00 | 7 | 5 | 1 | 2022-04-07 07:00 | 7 | 5 | 1
2022-04-07 08:00 | 8 | 5 | 1 | 2022-04-07 08:00 | 8 | 5 | 1
2022-04-07 09:00 | 9 | 5 | 1 | 2022-04-07 09:00 | 9 | 5 | 1
2022-04-07 10:00 | 10 | 5 | 1 | 2022-04-07 10:00 | 10 | 5 | 1
2022-04-07 11:00 | 11 | 5 | 1 | 2022-04-07 11:00 | 11 | 5 | 1
2022-04-07 12:00 | 12 | 5 | 1 | 2022-04-07 12:00 | 12 | 5 | 1
2022-04-07 13:00 | 13 | 5 | 1 | 2022-04-07 13:00 | 13 | 5 | 1
2022-04-07 14:00 | 14 | 5 | 1 | 2022-04-07 14:00 | 14 | 5 | 1
2022-04-07 15:00 | 15 | 5 | 1 | 2022-04-07 15:00 | 15 | 5 | 1
2022-04-07 16:00 | 16 | 5 | 1 | 2022-04-07 16:00 | 16 | 5 | 1
2022-04-07 17:00 | 17 | 5 | 1 | 2022-04-07 17:00 | 17 | 5 | 1
2022-04-07 18:00 | 18 | 5 | 1 | 2022-04-07 18:00 | 18 | 5 | 1
2022-04-07 19:00 | 19 | 5 | 1 | 2022-04-07 19:00 | 19 | 5 | 1
2022-04-07 20:00 | 20 | 5 | 1 | 2022-04-07 20:00 | 20 | 5 | 1
2022-04-07 21:00 | 21 | 5 | 1 | 2022-04-07 21:00 | 21 | 5 | 1
2022-04-07 22:00 | 22 | 5 | 1 | 2022-04-07 22:00 | 22 | 5 | 1
2022-04-07 23:00 | 23 | 5 | 1 | 2022-04-07 23:00 | 23 | 5 | 1
2022-04-08 | 0 | 6 | 1 | 2022-04-08 | 0 | 6 | 1
2022-04-08 01:00 | 1 | 6 | 1 | 2022-04-08 01:00 | 1 | 6 | 1
2022-04-08 02:00 | 2 | 6 | 1 | 2022-04-08 02:00 | 2 | 6 | 1
2022-04-08 03:00 | 3 | 6 | 1 | 2022-04-08 03:00 | 3 | 6 | 1
2022-04-08 04:00 | 4 | 6 | 1 | 2022-04-08 04:00 | 4 | 6 | 1
2022-04-08 05:00 | 5 | 6 | 1 | 2022-04-08 05:00 | 5 | 6 | 1
2022-04-08 06:00 | 6 | 6 | 1 | 2022-04-08 06:00 | 6 | 6 | 1
2022-04-08 07:00 | 7 | 6 | 1 | 2022-04-08 07:00 | 7 | 6 | 1
2022-04-08 08:00 | 8 | 6 | 1 | 2022-04-08 08:00 | 8 | 6 | 1
2022-04-08 09:00 | 9 | 6 | 1 | 2022-04-08 09:00 | 9 | 6 | 1
2022-04-08 10:00 | 10 | 6 | 1 | 2022-04-08 10:00 | 10 | 6 | 1
2022-04-08 11:00 | 11 | 6 | 1 | 2022-04-08 11:00 | 11 | 6 | 1
2022-04-08 12:00 | 12 | 6 | 1 | 2022-04-08 12:00 | 12 | 6 | 1
2022-04-08 13:00 | 13 | 6 | 1 | 2022-04-08 13:00 | 13 | 6 | 1
2022-04-08 14:00 | 14 | 6 | 1 | 2022-04-08 14:00 | 14 | 6 | 1
2022-04-08 15:00 | 15 | 6 | 1 | 2022-04-08 15:00 | 15 | 6 | 1
2022-04-08 16:00 | 16 | 6 | 1 | 2022-04-08 16:00 | 16 | 6 | 1
2022-04-08 17:00 | 17 | 6 | 1 | 2022-04-08 17:00 | 17 | 6 | 1
2022-04-08 18:00 | 18 | 6 | 1 | 2022-04-08 18:00 | 18 | 6 | 1
2022-04-08 19:00 | 19 | 6 | 1 | 2022-04-08 19:00 | 19 | 6 | 1
2022-04-08 20:00 | 20 | 6 | 1 | 2022-04-08 20:00 | 20 | 6 | 1
2022-04-08 21:00 | 21 | 6 | 1 | 2022-04-08 21:00 | 21 | 6 | 1
2022-04-08 22:00 | 22 | 6 | 1 | 2022-04-08 22:00 | 22 | 6 | 1
2022-04-08 23:00 | 23 | 6 | 1 | 2022-04-08 23:00 | 23 | 6 | 1
2022-04-09 | 0 | 7 | 1 | 2022-04-09 | 0 | 7 | 1
2022-04-09 01:00 | 1 | 7 | 1 | 2022-04-09 01:00 | 1 | 7 | 1
2022-04-09 02:00 | 2 | 7 | 1 | 2022-04-09 02:00 | 2 | 7 | 1
2022-04-09 03:00 | 3 | 7 | 1 | 2022-04-09 03:00 | 3 | 7 | 1
2022-04-09 04:00 | 4 | 7 | 1 | 2022-04-09 04:00 | 4 | 7 | 1
2022-04-09 05:00 | 5 | 7 | 1 | 2022-04-09 05:00 | 5 | 7 | 1
2022-04-09 06:00 | 6 | 7 | 1 | 2022-04-09 06:00 | 6 | 7 | 1
2022-04-09 07:00 | 7 | 7 | 1 | 2022-04-09 07:00 | 7 | 7 | 1
2022-04-09 08:00 | 8 | 7 | 1 | 2022-04-09 08:00 | 8 | 7 | 1
2022-04-09 09:00 | 9 | 7 | 1 | 2022-04-09 09:00 | 9 | 7 | 1
2022-04-09 10:00 | 10 | 7 | 1 | 2022-04-09 10:00 | 10 | 7 | 1
2022-04-09 11:00 | 11 | 7 | 1 | 2022-04-09 11:00 | 11 | 7 | 1
2022-04-09 12:00 | 12 | 7 | 1 | 2022-04-09 12:00 | 12 | 7 | 1
2022-04-09 13:00 | 13 | 7 | 1 | 2022-04-09 13:00 | 13 | 7 | 1
2022-04-09 14:00 | 14 | 7 | 1 | 2022-04-09 14:00 | 14 | 7 | 1
2022-04-09 15:00 | 15 | 7 | 1 | 2022-04-09 15:00 | 15 | 7 | 1
2022-04-09 16:00 | 16 | 7 | 1 | 2022-04-09 16:00 | 16 | 7 | 1
2022-04-09 17:00 | 17 | 7 | 1 | 2022-04-09 17:00 | 17 | 7 | 1
2022-04-09 18:00 | 18 | 7 | 1 | 2022-04-09 18:00 | 18 | 7 | 1
2022-04-09 19:00 | 19 | 7 | 1 | 2022-04-09 19:00 | 19 | 7 | 1
2022-04-09 20:00 | 20 | 7 | 1 | 2022-04-09 20:00 | 20 | 7 | 1
2022-04-09 21:00 | 21 | 7 | 1 | 2022-04-09 21:00 | 21 | 7 | 1
2022-04-09 22:00 | 22 | 7 | 1 | 2022-04-09 22:00 | 22 | 7 | 1
2022-04-09 23:00 | 23 | 7 | 1 | 2022-04-09 23:00 | 23 | 7 | 1
2022-04-10 | 0 | 1 | 1 | 2022-04-10 | 0 | 1 | 1
2022-04-10 01:00 | 1 | 1 | 1 | 2022-04-10 01:00 | 1 | 1 | 1
2022-04-10 02:00 | 2 | 1 | 1 | 2022-04-10 02:00 | 2 | 1 | 1
2022-04-10 03:00 | 3 | 1 | 1 | 2022-04-10 03:00 | 3 | 1 | 1
2022-04-10 04:00 | 4 | 1 | 1 | 2022-04-10 04:00 | 4 | 1 | 1
2022-04-10 05:00 | 5 | 1 | 1 | 2022-04-10 05:00 | 5 | 1 | 1
2022-04-10 06:00 | 6 | 1 | 1 | 2022-04-10 06:00 | 6 | 1 | 1
2022-04-10 07:00 | 7 | 1 | 1 | 2022-04-10 07:00 | 7 | 1 | 1
2022-04-10 08:00 | 8 | 1 | 1 | 2022-04-10 08:00 | 8 | 1 | 1
2022-04-10 09:00 | 9 | 1 | 1 | 2022-04-10 09:00 | 9 | 1 | 1
2022-04-10 10:00 | 10 | 1 | 1 | 2022-04-10 10:00 | 10 | 1 | 1
2022-04-10 11:00 | 11 | 1 | 1 | 2022-04-10 11:00 | 11 | 1 | 1
2022-04-10 12:00 | 12 | 1 | 1 | 2022-04-10 12:00 | 12 | 1 | 1
2022-04-10 13:00 | 13 | 1 | 1 | 2022-04-10 13:00 | 13 | 1 | 1
2022-04-10 14:00 | 14 | 1 | 1 | 2022-04-10 14:00 | 14 | 1 | 1
2022-04-10 15:00 | 15 | 1 | 1 | 2022-04-10 15:00 | 15 | 1 | 1
2022-04-10 16:00 | 16 | 1 | 1 | 2022-04-10 16:00 | 16 | 1 | 1
2022-04-10 17:00 | 17 | 1 | 1 | 2022-04-10 17:00 | 17 | 1 | 1
2022-04-10 18:00 | 18 | 1 | 1 | 2022-04-10 18:00 | 18 | 1 | 1
2022-04-10 19:00 | 19 | 1 | 1 | 2022-04-10 19:00 | 19 | 1 | 1
2022-04-10 20:00 | 20 | 1 | 1 | 2022-04-10 20:00 | 20 | 1 | 1
2022-04-10 21:00 | 21 | 1 | 1 | 2022-04-10 21:00 | 21 | 1 | 1
2022-04-10 22:00 | 22 | 1 | 1 | 2022-04-10 22:00 | 22 | 1 | 1
2022-04-10 23:00 | 23 | 1 | 1 | 2022-04-10 23:00 | 23 | 1 | 1
2022-04-11 | 0 | 2 | 1 | 2022-04-11 | 0 | 2 | 1
2022-04-11 01:00 | 1 | 2 | 1 | 2022-04-11 01:00 | 1 | 2 | 1
2022-04-11 02:00 | 2 | 2 | 1 | 2022-04-11 02:00 | 2 | 2 | 1
2022-04-11 03:00 | 3 | 2 | 1 | 2022-04-11 03:00 | 3 | 2 | 1
2022-04-11 04:00 | 4 | 2 | 1 | 2022-04-11 04:00 | 4 | 2 | 1
2022-04-11 05:00 | 5 | 2 | 1 | 2022-04-11 05:00 | 5 | 2 | 1
2022-04-11 06:00 | 6 | 2 | 1 | 2022-04-11 06:00 | 6 | 2 | 1
2022-04-11 07:00 | 7 | 2 | 1 | 2022-04-11 07:00 | 7 | 2 | 1
2022-04-11 08:00 | 8 | 2 | 1 | 2022-04-11 08:00 | 8 | 2 | 1
2022-04-11 09:00 | 9 | 2 | 1 | 2022-04-11 09:00 | 9 | 2 | 1
2022-04-11 10:00 | 10 | 2 | 1 | 2022-04-11 10:00 | 10 | 2 | 1
2022-04-11 11:00 | 11 | 2 | 1 | 2022-04-11 11:00 | 11 | 2 | 1
2022-04-11 12:00 | 12 | 2 | 1 | 2022-04-11 12:00 | 12 | 2 | 1
2022-04-11 13:00 | 13 | 2 | 1 | 2022-04-11 13:00 | 13 | 2 | 1
2022-04-11 14:00 | 14 | 2 | 1 | 2022-04-11 14:00 | 14 | 2 | 1
2022-04-11 15:00 | 15 | 2 | 1 | 2022-04-11 15:00 | 15 | 2 | 1
2022-04-11 16:00 | 16 | 2 | 1 | 2022-04-11 16:00 | 16 | 2 | 1
2022-04-11 17:00 | 17 | 2 | 1 | 2022-04-11 17:00 | 17 | 2 | 1
2022-04-11 18:00 | 18 | 2 | 1 | 2022-04-11 18:00 | 18 | 2 | 1
2022-04-11 19:00 | 19 | 2 | 1 | 2022-04-11 19:00 | 19 | 2 | 1
2022-04-11 20:00 | 20 | 2 | 1 | 2022-04-11 20:00 | 20 | 2 | 1
2022-04-11 21:00 | 21 | 2 | 1 | 2022-04-11 21:00 | 21 | 2 | 1
2022-04-11 22:00 | 22 | 2 | 1 | 2022-04-11 22:00 | 22 | 2 | 1
2022-04-11 23:00 | 23 | 2 | 1 | 2022-04-11 23:00 | 23 | 2 | 1
2022-04-12 | 0 | 3 | 1 | 2022-04-12 | 0 | 3 | 1
2022-04-12 01:00 | 1 | 3 | 1 | 2022-04-12 01:00 | 1 | 3 | 1
2022-04-12 02:00 | 2 | 3 | 1 | 2022-04-12 02:00 | 2 | 3 | 1
2022-04-12 03:00 | 3 | 3 | 1 | 2022-04-12 03:00 | 3 | 3 | 1
2022-04-12 04:00 | 4 | 3 | 1 | 2022-04-12 04:00 | 4 | 3 | 1
2022-04-12 05:00 | 5 | 3 | 1 | 2022-04-12 05:00 | 5 | 3 | 1
2022-04-12 06:00 | 6 | 3 | 1 | 2022-04-12 06:00 | 6 | 3 | 1
2022-04-12 07:00 | 7 | 3 | 1 | 2022-04-12 07:00 | 7 | 3 | 1
2022-04-12 08:00 | 8 | 3 | 1 | 2022-04-12 08:00 | 8 | 3 | 1
2022-04-12 09:00 | 9 | 3 | 1 | 2022-04-12 09:00 | 9 | 3 | 1
2022-04-12 10:00 | 10 | 3 | 1 | 2022-04-12 10:00 | 10 | 3 | 1
2022-04-12 11:00 | 11 | 3 | 1 | 2022-04-12 11:00 | 11 | 3 | 1
2022-04-12 12:00 | 12 | 3 | 1 | 2022-04-12 12:00 | 12 | 3 | 1
2022-04-12 13:00 | 13 | 3 | 1 | 2022-04-12 13:00 | 13 | 3 | 1
2022-04-12 14:00 | 14 | 3 | 1 | 2022-04-12 14:00 | 14 | 3 | 1
2022-04-12 15:00 | 15 | 3 | 1 | 2022-04-12 15:00 | 15 | 3 | 1
2022-04-12 16:00 | 16 | 3 | 1 | 2022-04-12 16:00 | 16 | 3 | 1
2022-04-12 17:00 | 17 | 3 | 1 | 2022-04-12 17:00 | 17 | 3 | 1
2022-04-12 18:00 | 18 | 3 | 1 | 2022-04-12 18:00 | 18 | 3 | 1
2022-04-12 19:00 | 19 | 3 | 1 | 2022-04-12 19:00 | 19 | 3 | 1
2022-04-12 20:00 | 20 | 3 | 1 | 2022-04-12 20:00 | 20 | 3 | 1
2022-04-12 21:00 | 21 | 3 | 1 | 2022-04-12 21:00 | 21 | 3 | 1
2022-04-12 22:00 | 22 | 3 | 1 | 2022-04-12 22:00 | 22 | 3 | 1
2022-04-12 23:00 | 23 | 3 | 1 | 2022-04-12 23:00 | 23 | 3 | 1
2022-04-13 | 0 | 4 | 1 | 2022-04-13 | 0 | 4 | 1
2022-04-13 01:00 | 1 | 4 | 1 | 2022-04-13 01:00 | 1 | 4 | 1
2022-04-13 02:00 | 2 | 4 | 1 | 2022-04-13 02:00 | 2 | 4 | 1
2022-04-13 03:00 | 3 | 4 | 1 | 2022-04-13 03:00 | 3 | 4 | 1
2022-04-13 04:00 | 4 | 4 | 1 | 2022-04-13 04:00 | 4 | 4 | 1
2022-04-13 05:00 | 5 | 4 | 1 | 2022-04-13 05:00 | 5 | 4 | 1
2022-04-13 06:00 | 6 | 4 | 1 | 2022-04-13 06:00 | 6 | 4 | 1
2022-04-13 07:00 | 7 | 4 | 1 | 2022-04-13 07:00 | 7 | 4 | 1
2022-04-13 08:00 | 8 | 4 | 1 | 2022-04-13 08:00 | 8 | 4 | 1
2022-04-13 09:00 | 9 | 4 | 1 | 2022-04-13 09:00 | 9 | 4 | 1
2022-04-13 10:00 | 10 | 4 | 1 | 2022-04-13 10:00 | 10 | 4 | 1
2022-04-13 11:00 | 11 | 4 | 1 | 2022-04-13 11:00 | 11 | 4 | 1
2022-04-13 12:00 | 12 | 4 | 1 | 2022-04-13 12:00 | 12 | 4 | 1
2022-04-13 13:00 | 13 | 4 | 1 | 2022-04-13 13:00 | 13 | 4 | 1
2022-04-13 14:00 | 14 | 4 | 1 | 2022-04-13 14:00 | 14 | 4 | 1
2022-04-13 15:00 | 15 | 4 | 1 | 2022-04-13 15:00 | 15 | 4 | 1
2022-04-13 16:00 | 16 | 4 | 1 | 2022-04-13 16:00 | 16 | 4 | 1
2022-04-13 17:00 | 17 | 4 | 1 | 2022-04-13 17:00 | 17 | 4 | 1
2022-04-13 18:00 | 18 | 4 | 1 | 2022-04-13 18:00 | 18 | 4 | 1
2022-04-13 19:00 | 19 | 4 | 1 | 2022-04-13 19:00 | 19 | 4 | 1
2022-04-13 20:00 | 20 | 4 | 1 | 2022-04-13 20:00 | 20 | 4 | 1
2022-04-13 21:00 | 21 | 4 | 1 | 2022-04-13 21:00 | 21 | 4 | 1
2022-04-13 22:00 | 22 | 4 | 1 | 2022-04-13 22:00 | 22 | 4 | 1
2022-04-13 23:00 | 23 | 4 | 1 | 2022-04-13 23:00 | 23 | 4 | 1
2022-04-14 | 0 | 5 | 1 | 2022-04-14 | 0 | 5 | 1
2022-04-14 01:00 | 1 | 5 | 1 | 2022-04-14 01:00 | 1 | 5 | 1
2022-04-14 02:00 | 2 | 5 | 1 | 2022-04-14 02:00 | 2 | 5 | 1
2022-04-14 03:00 | 3 | 5 | 1 | 2022-04-14 03:00 | 3 | 5 | 1
2022-04-14 04:00 | 4 | 5 | 1 | 2022-04-14 04:00 | 4 | 5 | 1
2022-04-14 05:00 | 5 | 5 | 1 | 2022-04-14 05:00 | 5 | 5 | 1
2022-04-14 06:00 | 6 | 5 | 1 | 2022-04-14 06:00 | 6 | 5 | 1
2022-04-14 07:00 | 7 | 5 | 1 | 2022-04-14 07:00 | 7 | 5 | 1
2022-04-14 08:00 | 8 | 5 | 1 | 2022-04-14 08:00 | 8 | 5 | 1
2022-04-14 09:00 | 9 | 5 | 1 | 2022-04-14 09:00 | 9 | 5 | 1
2022-04-14 10:00 | 10 | 5 | 1 | 2022-04-14 10:00 | 10 | 5 | 1
2022-04-14 11:00 | 11 | 5 | 1 | 2022-04-14 11:00 | 11 | 5 | 1
2022-04-14 12:00 | 12 | 5 | 1 | 2022-04-14 12:00 | 12 | 5 | 1
2022-04-14 13:00 | 13 | 5 | 1 | 2022-04-14 13:00 | 13 | 5 | 1
2022-04-14 14:00 | 14 | 5 | 1 | 2022-04-14 14:00 | 14 | 5 | 1
2022-04-14 15:00 | 15 | 5 | 1 | 2022-04-14 15:00 | 15 | 5 | 1
2022-04-14 16:00 | 16 | 5 | 1 | 2022-04-14 16:00 | 16 | 5 | 1
2022-04-14 17:00 | 17 | 5 | 1 | 2022-04-14 17:00 | 17 | 5 | 1
2022-04-14 18:00 | 18 | 5 | 1 | 2022-04-14 18:00 | 18 | 5 | 1
2022-04-14 19:00 | 19 | 5 | 1 | 2022-04-14 19:00 | 19 | 5 | 1
2022-04-14 20:00 | 20 | 5 | 1 | 2022-04-14 20:00 | 20 | 5 | 1
2022-04-14 21:00 | 21 | 5 | 1 | 2022-04-14 21:00 | 21 | 5 | 1
2022-04-14 22:00 | 22 | 5 | 1 | 2022-04-14 22:00 | 22 | 5 | 1
2022-04-14 23:00 | 23 | 5 | 1 | 2022-04-14 23:00 | 23 | 5 | 1
2022-04-15 | 0 | 6 | 1 | 2022-04-15 | 0 | 6 | 1
2022-04-15 01:00 | 1 | 6 | 1 | 2022-04-15 01:00 | 1 | 6 | 1
2022-04-15 02:00 | 2 | 6 | 1 | 2022-04-15 02:00 | 2 | 6 | 1
2022-04-15 03:00 | 3 | 6 | 1 | 2022-04-15 03:00 | 3 | 6 | 1
2022-04-15 04:00 | 4 | 6 | 1 | 2022-04-15 04:00 | 4 | 6 | 1
2022-04-15 05:00 | 5 | 6 | 1 | 2022-04-15 05:00 | 5 | 6 | 1
2022-04-15 06:00 | 6 | 6 | 1 | 2022-04-15 06:00 | 6 | 6 | 1
2022-04-15 07:00 | 7 | 6 | 1 | 2022-04-15 07:00 | 7 | 6 | 1
2022-04-15 08:00 | 8 | 6 | 1 | 2022-04-15 08:00 | 8 | 6 | 1
2022-04-15 09:00 | 9 | 6 | 1 | 2022-04-15 09:00 | 9 | 6 | 1
2022-04-15 10:00 | 10 | 6 | 1 | 2022-04-15 10:00 | 10 | 6 | 1
2022-04-15 11:00 | 11 | 6 | 1 | 2022-04-15 11:00 | 11 | 6 | 1
2022-04-15 12:00 | 12 | 6 | 1 | 2022-04-15 12:00 | 12 | 6 | 1
2022-04-15 13:00 | 13 | 6 | 1 | 2022-04-15 13:00 | 13 | 6 | 1
2022-04-15 14:00 | 14 | 6 | 1 | 2022-04-15 14:00 | 14 | 6 | 1
2022-04-15 15:00 | 15 | 6 | 1 | 2022-04-15 15:00 | 15 | 6 | 1
2022-04-15 16:00 | 16 | 6 | 1 | 2022-04-15 16:00 | 16 | 6 | 1
2022-04-15 17:00 | 17 | 6 | 1 | 2022-04-15 17:00 | 17 | 6 | 1
2022-04-15 18:00 | 18 | 6 | 1 | 2022-04-15 18:00 | 18 | 6 | 1
2022-04-15 19:00 | 19 | 6 | 1 | 2022-04-15 19:00 | 19 | 6 | 1
2022-04-15 20:00 | 20 | 6 | 1 | 2022-04-15 20:00 | 20 | 6 | 1
2022-04-15 21:00 | 21 | 6 | 1 | 2022-04-15 21:00 | 21 | 6 | 1
2022-04-15 22:00 | 22 | 6 | 1 | 2022-04-15 22:00 | 22 | 6 | 1
2022-04-15 23:00 | 23 | 6 | 1 | 2022-04-15 23:00 | 23 | 6 | 1
2022-04-16 | 0 | 7 | 1 | 2022-04-16 | 0 | 7 | 1
2022-04-16 01:00 | 1 | 7 | 1 | 2022-04-16 01:00 | 1 | 7 | 1
2022-04-16 02:00 | 2 | 7 | 1 | 2022-04-16 02:00 | 2 | 7 | 1
2022-04-16 03:00 | 3 | 7 | 1 | 2022-04-16 03:00 | 3 | 7 | 1
2022-04-16 04:00 | 4 | 7 | 1 | 2022-04-16 04:00 | 4 | 7 | 1
2022-04-16 05:00 | 5 | 7 | 1 | 2022-04-16 05:00 | 5 | 7 | 1
2022-04-16 06:00 | 6 | 7 | 1 | 2022-04-16 06:00 | 6 | 7 | 1
2022-04-16 07:00 | 7 | 7 | 1 | 2022-04-16 07:00 | 7 | 7 | 1
2022-04-16 08:00 | 8 | 7 | 1 | 2022-04-16 08:00 | 8 | 7 | 1
2022-04-16 09:00 | 9 | 7 | 1 | 2022-04-16 09:00 | 9 | 7 | 1
2022-04-16 10:00 | 10 | 7 | 1 | 2022-04-16 10:00 | 10 | 7 | 1
2022-04-16 11:00 | 11 | 7 | 1 | 2022-04-16 11:00 | 11 | 7 | 1
2022-04-16 12:00 | 12 | 7 | 1 | 2022-04-16 12:00 | 12 | 7 | 1
2022-04-16 13:00 | 13 | 7 | 1 | 2022-04-16 13:00 | 13 | 7 | 1
2022-04-16 14:00 | 14 | 7 | 1 | 2022-04-16 14:00 | 14 | 7 | 1
2022-04-16 15:00 | 15 | 7 | 1 | 2022-04-16 15:00 | 15 | 7 | 1
2022-04-16 16:00 | 16 | 7 | 1 | 2022-04-16 16:00 | 16 | 7 | 1
2022-04-16 17:00 | 17 | 7 | 1 | 2022-04-16 17:00 | 17 | 7 | 1
2022-04-16 18:00 | 18 | 7 | 1 | 2022-04-16 18:00 | 18 | 7 | 1
2022-04-16 19:00 | 19 | 7 | 1 | 2022-04-16 19:00 | 19 | 7 | 1
2022-04-16 20:00 | 20 | 7 | 1 | 2022-04-16 20:00 | 20 | 7 | 1
2022-04-16 21:00 | 21 | 7 | 1 | 2022-04-16 21:00 | 21 | 7 | 1
2022-04-16 22:00 | 22 | 7 | 1 | 2022-04-16 22:00 | 22 | 7 | 1
2022-04-16 23:00 | 23 | 7 | 1 | 2022-04-16 23:00 | 23 | 7 | 1
2022-04-17 | 0 | 1 | 1 | 2022-04-17 | 0 | 1 | 1
2022-04-17 01:00 | 1 | 1 | 1 | 2022-04-17 01:00 | 1 | 1 | 1
2022-04-17 02:00 | 2 | 1 | 1 | 2022-04-17 02:00 | 2 | 1 | 1
2022-04-17 03:00 | 3 | 1 | 1 | 2022-04-17 03:00 | 3 | 1 | 1
2022-04-17 04:00 | 4 | 1 | 1 | 2022-04-17 04:00 | 4 | 1 | 1
2022-04-17 05:00 | 5 | 1 | 1 | 2022-04-17 05:00 | 5 | 1 | 1
2022-04-17 06:00 | 6 | 1 | 1 | 2022-04-17 06:00 | 6 | 1 | 1
2022-04-17 07:00 | 7 | 1 | 1 | 2022-04-17 07:00 | 7 | 1 | 1
2022-04-17 08:00 | 8 | 1 | 1 | 2022-04-17 08:00 | 8 | 1 | 1
2022-04-17 09:00 | 9 | 1 | 1 | 2022-04-17 09:00 | 9 | 1 | 1
2022-04-17 10:00 | 10 | 1 | 1 | 2022-04-17 10:00 | 10 | 1 | 1
2022-04-17 11:00 | 11 | 1 | 1 | 2022-04-17 11:00 | 11 | 1 | 1
2022-04-17 12:00 | 12 | 1 | 1 | 2022-04-17 12:00 | 12 | 1 | 1
2022-04-17 13:00 | 13 | 1 | 1 | 2022-04-17 13:00 | 13 | 1 | 1
2022-04-17 14:00 | 14 | 1 | 1 | 2022-04-17 14:00 | 14 | 1 | 1
2022-04-17 15:00 | 15 | 1 | 1 | 2022-04-17 15:00 | 15 | 1 | 1
2022-04-17 16:00 | 16 | 1 | 1 | 2022-04-17 16:00 | 16 | 1 | 1
2022-04-17 17:00 | 17 | 1 | 1 | 2022-04-17 17:00 | 17 | 1 | 1
2022-04-17 18:00 | 18 | 1 | 1 | 2022-04-17 18:00 | 18 | 1 | 1
2022-04-17 19:00 | 19 | 1 | 1 | 2022-04-17 19:00 | 19 | 1 | 1
2022-04-17 20:00 | 20 | 1 | 1 | 2022-04-17 20:00 | 20 | 1 | 1
2022-04-17 21:00 | 21 | 1 | 1 | 2022-04-17 21:00 | 21 | 1 | 1
2022-04-17 22:00 | 22 | 1 | 1 | 2022-04-17 22:00 | 22 | 1 | 1
2022-04-17 23:00 | 23 | 1 | 1 | 2022-04-17 23:00 | 23 | 1 | 1
2022-04-18 | 0 | 2 | 1 | 2022-04-18 | 0 | 2 | 1
2022-04-18 01:00 | 1 | 2 | 1 | 2022-04-18 01:00 | 1 | 2 | 1
2022-04-18 02:00 | 2 | 2 | 1 | 2022-04-18 02:00 | 2 | 2 | 1
2022-04-18 03:00 | 3 | 2 | 1 | 2022-04-18 03:00 | 3 | 2 | 1
2022-04-18 04:00 | 4 | 2 | 1 | 2022-04-18 04:00 | 4 | 2 | 1
2022-04-18 05:00 | 5 | 2 | 1 | 2022-04-18 05:00 | 5 | 2 | 1
2022-04-18 06:00 | 6 | 2 | 1 | 2022-04-18 06:00 | 6 | 2 | 1
2022-04-18 07:00 | 7 | 2 | 1 | 2022-04-18 07:00 | 7 | 2 | 1
2022-04-18 08:00 | 8 | 2 | 1 | 2022-04-18 08:00 | 8 | 2 | 1
2022-04-18 09:00 | 9 | 2 | 1 | 2022-04-18 09:00 | 9 | 2 | 1
2022-04-18 10:00 | 10 | 2 | 1 | 2022-04-18 10:00 | 10 | 2 | 1
2022-04-18 11:00 | 11 | 2 | 1 | 2022-04-18 11:00 | 11 | 2 | 1
2022-04-18 12:00 | 12 | 2 | 1 | 2022-04-18 12:00 | 12 | 2 | 1
2022-04-18 13:00 | 13 | 2 | 1 | 2022-04-18 13:00 | 13 | 2 | 1
2022-04-18 14:00 | 14 | 2 | 1 | 2022-04-18 14:00 | 14 | 2 | 1
2022-04-18 15:00 | 15 | 2 | 1 | 2022-04-18 15:00 | 15 | 2 | 1
2022-04-18 16:00 | 16 | 2 | 1 | 2022-04-18 16:00 | 16 | 2 | 1
2022-04-18 17:00 | 17 | 2 | 1 | 2022-04-18 17:00 | 17 | 2 | 1
2022-04-18 18:00 | 18 | 2 | 1 | 2022-04-18 18:00 | 18 | 2 | 1
2022-04-18 19:00 | 19 | 2 | 1 | 2022-04-18 19:00 | 19 | 2 | 1
2022-04-18 20:00 | 20 | 2 | 1 | 2022-04-18 20:00 | 20 | 2 | 1
2022-04-18 21:00 | 21 | 2 | 1 | 2022-04-18 21:00 | 21 | 2 | 1
2022-04-18 22:00 | 22 | 2 | 1 | 2022-04-18 22:00 | 22 | 2 | 1
2022-04-18 23:00 | 23 | 2 | 1 | 2022-04-18 23:00 | 23 | 2 | 1
2022-04-19 | 0 | 3 | 1 | 2022-04-19 | 0 | 3 | 1
2022-04-19 01:00 | 1 | 3 | 1 | 2022-04-19 01:00 | 1 | 3 | 1
2022-04-19 02:00 | 2 | 3 | 1 | 2022-04-19 02:00 | 2 | 3 | 1
2022-04-19 03:00 | 3 | 3 | 1 | 2022-04-19 03:00 | 3 | 3 | 1
2022-04-19 04:00 | 4 | 3 | 1 | 2022-04-19 04:00 | 4 | 3 | 1
2022-04-19 05:00 | 5 | 3 | 1 | 2022-04-19 05:00 | 5 | 3 | 1
2022-04-19 06:00 | 6 | 3 | 1 | 2022-04-19 06:00 | 6 | 3 | 1
2022-04-19 07:00 | 7 | 3 | 1 | 2022-04-19 07:00 | 7 | 3 | 1
2022-04-19 08:00 | 8 | 3 | 1 | 2022-04-19 08:00 | 8 | 3 | 1
2022-04-19 09:00 | 9 | 3 | 1 | 2022-04-19 09:00 | 9 | 3 | 1
2022-04-19 10:00 | 10 | 3 | 1 | 2022-04-19 10:00 | 10 | 3 | 1
2022-04-19 11:00 | 11 | 3 | 1 | 2022-04-19 11:00 | 11 | 3 | 1
2022-04-19 12:00 | 12 | 3 | 1 | 2022-04-19 12:00 | 12 | 3 | 1
2022-04-19 13:00 | 13 | 3 | 1 | 2022-04-19 13:00 | 13 | 3 | 1
2022-04-19 14:00 | 14 | 3 | 1 | 2022-04-19 14:00 | 14 | 3 | 1
2022-04-19 15:00 | 15 | 3 | 1 | 2022-04-19 15:00 | 15 | 3 | 1
2022-04-19 16:00 | 16 | 3 | 1 | 2022-04-19 16:00 | 16 | 3 | 1
2022-04-19 17:00 | 17 | 3 | 1 | 2022-04-19 17:00 | 17 | 3 | 1
2022-04-19 18:00 | 18 | 3 | 1 | 2022-04-19 18:00 | 18 | 3 | 1
2022-04-19 19:00 | 19 | 3 | 1 | 2022-04-19 19:00 | 19 | 3 | 1
2022-04-19 20:00 | 20 | 3 | 1 | 2022-04-19 20:00 | 20 | 3 | 1
2022-04-19 21:00 | 21 | 3 | 1 | 2022-04-19 21:00 | 21 | 3 | 1
2022-04-19 22:00 | 22 | 3 | 1 | 2022-04-19 22:00 | 22 | 3 | 1
2022-04-19 23:00 | 23 | 3 | 1 | 2022-04-19 23:00 | 23 | 3 | 1
2022-04-20 | 0 | 4 | 1 | 2022-04-20 | 0 | 4 | 1
2022-04-20 01:00 | 1 | 4 | 1 | 2022-04-20 01:00 | 1 | 4 | 1
2022-04-20 02:00 | 2 | 4 | 1 | 2022-04-20 02:00 | 2 | 4 | 1
2022-04-20 03:00 | 3 | 4 | 1 | 2022-04-20 03:00 | 3 | 4 | 1
2022-04-20 04:00 | 4 | 4 | 1 | 2022-04-20 04:00 | 4 | 4 | 1
2022-04-20 05:00 | 5 | 4 | 1 | 2022-04-20 05:00 | 5 | 4 | 1
2022-04-20 06:00 | 6 | 4 | 1 | 2022-04-20 06:00 | 6 | 4 | 1
2022-04-20 07:00 | 7 | 4 | 1 | 2022-04-20 07:00 | 7 | 4 | 1
2022-04-20 08:00 | 8 | 4 | 1 | 2022-04-20 08:00 | 8 | 4 | 1
2022-04-20 09:00 | 9 | 4 | 1 | 2022-04-20 09:00 | 9 | 4 | 1
2022-04-20 10:00 | 10 | 4 | 1 | 2022-04-20 10:00 | 10 | 4 | 1
2022-04-20 11:00 | 11 | 4 | 1 | 2022-04-20 11:00 | 11 | 4 | 1
2022-04-20 12:00 | 12 | 4 | 1 | 2022-04-20 12:00 | 12 | 4 | 1
2022-04-20 13:00 | 13 | 4 | 1 | 2022-04-20 13:00 | 13 | 4 | 1
2022-04-20 14:00 | 14 | 4 | 1 | 2022-04-20 14:00 | 14 | 4 | 1
2022-04-20 15:00 | 15 | 4 | 1 | 2022-04-20 15:00 | 15 | 4 | 1
2022-04-20 16:00 | 16 | 4 | 1 | 2022-04-20 16:00 | 16 | 4 | 1
2022-04-20 17:00 | 17 | 4 | 1 | 2022-04-20 17:00 | 17 | 4 | 1
2022-04-20 18:00 | 18 | 4 | 1 | 2022-04-20 18:00 | 18 | 4 | 1
2022-04-20 19:00 | 19 | 4 | 1 | 2022-04-20 19:00 | 19 | 4 | 1
2022-04-20 20:00 | 20 | 4 | 1 | 2022-04-20 20:00 | 20 | 4 | 1
2022-04-20 21:00 | 21 | 4 | 1 | 2022-04-20 21:00 | 21 | 4 | 1
2022-04-20 22:00 | 22 | 4 | 1 | 2022-04-20 22:00 | 22 | 4 | 1
2022-04-20 23:00 | 23 | 4 | 1 | 2022-04-20 23:00 | 23 | 4 | 1
2022-04-21 | 0 | 5 | 1 | 2022-04-21 | 0 | 5 | 1
2022-04-21 01:00 | 1 | 5 | 1 | 2022-04-21 01:00 | 1 | 5 | 1
2022-04-21 02:00 | 2 | 5 | 1 | 2022-04-21 02:00 | 2 | 5 | 1
2022-04-21 03:00 | 3 | 5 | 1 | 2022-04-21 03:00 | 3 | 5 | 1
2022-04-21 04:00 | 4 | 5 | 1 | 2022-04-21 04:00 | 4 | 5 | 1
2022-04-21 05:00 | 5 | 5 | 1 | 2022-04-21 05:00 | 5 | 5 | 1
2022-04-21 06:00 | 6 | 5 | 1 | 2022-04-21 06:00 | 6 | 5 | 1
2022-04-21 07:00 | 7 | 5 | 1 | 2022-04-21 07:00 | 7 | 5 | 1
2022-04-21 08:00 | 8 | 5 | 1 | 2022-04-21 08:00 | 8 | 5 | 1
2022-04-21 09:00 | 9 | 5 | 1 | 2022-04-21 09:00 | 9 | 5 | 1
2022-04-21 10:00 | 10 | 5 | 1 | 2022-04-21 10:00 | 10 | 5 | 1
2022-04-21 11:00 | 11 | 5 | 1 | 2022-04-21 11:00 | 11 | 5 | 1
2022-04-21 12:00 | 12 | 5 | 1 | 2022-04-21 12:00 | 12 | 5 | 1
2022-04-21 13:00 | 13 | 5 | 1 | 2022-04-21 13:00 | 13 | 5 | 1
2022-04-21 14:00 | 14 | 5 | 1 | 2022-04-21 14:00 | 14 | 5 | 1
2022-04-21 15:00 | 15 | 5 | 1 | 2022-04-21 15:00 | 15 | 5 | 1
2022-04-21 16:00 | 16 | 5 | 1 | 2022-04-21 16:00 | 16 | 5 | 1
2022-04-21 17:00 | 17 | 5 | 1 | 2022-04-21 17:00 | 17 | 5 | 1
2022-04-21 18:00 | 18 | 5 | 1 | 2022-04-21 18:00 | 18 | 5 | 1
2022-04-21 19:00 | 19 | 5 | 1 | 2022-04-21 19:00 | 19 | 5 | 1
2022-04-21 20:00 | 20 | 5 | 1 | 2022-04-21 20:00 | 20 | 5 | 1
2022-04-21 21:00 | 21 | 5 | 1 | 2022-04-21 21:00 | 21 | 5 | 1
2022-04-21 22:00 | 22 | 5 | 1 | 2022-04-21 22:00 | 22 | 5 | 1
2022-04-21 23:00 | 23 | 5 | 1 | 2022-04-21 23:00 | 23 | 5 | 1
2022-04-22 | 0 | 6 | 1 | 2022-04-22 | 0 | 6 | 1
2022-04-22 01:00 | 1 | 6 | 1 | 2022-04-22 01:00 | 1 | 6 | 1
2022-04-22 02:00 | 2 | 6 | 1 | 2022-04-22 02:00 | 2 | 6 | 1
2022-04-22 03:00 | 3 | 6 | 1 | 2022-04-22 03:00 | 3 | 6 | 1
2022-04-22 04:00 | 4 | 6 | 1 | 2022-04-22 04:00 | 4 | 6 | 1
2022-04-22 05:00 | 5 | 6 | 1 | 2022-04-22 05:00 | 5 | 6 | 1
2022-04-22 06:00 | 6 | 6 | 1 | 2022-04-22 06:00 | 6 | 6 | 1
2022-04-22 07:00 | 7 | 6 | 1 | 2022-04-22 07:00 | 7 | 6 | 1
2022-04-22 08:00 | 8 | 6 | 1 | 2022-04-22 08:00 | 8 | 6 | 1
2022-04-22 09:00 | 9 | 6 | 1 | 2022-04-22 09:00 | 9 | 6 | 1
2022-04-22 10:00 | 10 | 6 | 1 | 2022-04-22 10:00 | 10 | 6 | 1
2022-04-22 11:00 | 11 | 6 | 1 | 2022-04-22 11:00 | 11 | 6 | 1
2022-04-22 12:00 | 12 | 6 | 1 | 2022-04-22 12:00 | 12 | 6 | 1
2022-04-22 13:00 | 13 | 6 | 1 | 2022-04-22 13:00 | 13 | 6 | 1
2022-04-22 14:00 | 14 | 6 | 1 | 2022-04-22 14:00 | 14 | 6 | 1
2022-04-22 15:00 | 15 | 6 | 1 | 2022-04-22 15:00 | 15 | 6 | 1
2022-04-22 16:00 | 16 | 6 | 1 | 2022-04-22 16:00 | 16 | 6 | 1
2022-04-22 17:00 | 17 | 6 | 1 | 2022-04-22 17:00 | 17 | 6 | 1
2022-04-22 18:00 | 18 | 6 | 1 | 2022-04-22 18:00 | 18 | 6 | 1
2022-04-22 19:00 | 19 | 6 | 1 | 2022-04-22 19:00 | 19 | 6 | 1
2022-04-22 20:00 | 20 | 6 | 1 | 2022-04-22 20:00 | 20 | 6 | 1
2022-04-22 21:00 | 21 | 6 | 1 | 2022-04-22 21:00 | 21 | 6 | 1
2022-04-22 22:00 | 22 | 6 | 1 | 2022-04-22 22:00 | 22 | 6 | 1
2022-04-22 23:00 | 23 | 6 | 1 | 2022-04-22 23:00 | 23 | 6 | 1
2022-04-23 | 0 | 7 | 1 | 2022-04-23 | 0 | 7 | 1
2022-04-23 01:00 | 1 | 7 | 1 | 2022-04-23 01:00 | 1 | 7 | 1
2022-04-23 02:00 | 2 | 7 | 1 | 2022-04-23 02:00 | 2 | 7 | 1
2022-04-23 03:00 | 3 | 7 | 1 | 2022-04-23 03:00 | 3 | 7 | 1
2022-04-23 04:00 | 4 | 7 | 1 | 2022-04-23 04:00 | 4 | 7 | 1
2022-04-23 05:00 | 5 | 7 | 1 | 2022-04-23 05:00 | 5 | 7 | 1
2022-04-23 06:00 | 6 | 7 | 1 | 2022-04-23 06:00 | 6 | 7 | 1
2022-04-23 07:00 | 7 | 7 | 1 | 2022-04-23 07:00 | 7 | 7 | 1
2022-04-23 08:00 | 8 | 7 | 1 | 2022-04-23 08:00 | 8 | 7 | 1
2022-04-23 09:00 | 9 | 7 | 1 | 2022-04-23 09:00 | 9 | 7 | 1
2022-04-23 10:00 | 10 | 7 | 1 | 2022-04-23 10:00 | 10 | 7 | 1
2022-04-23 11:00 | 11 | 7 | 1 | 2022-04-23 11:00 | 11 | 7 | 1
2022-04-23 12:00 | 12 | 7 | 1 | 2022-04-23 12:00 | 12 | 7 | 1
2022-04-23 13:00 | 13 | 7 | 1 | 2022-04-23 13:00 | 13 | 7 | 1
2022-04-23 14:00 | 14 | 7 | 1 | 2022-04-23 14:00 | 14 | 7 | 1
2022-04-23 15:00 | 15 | 7 | 1 | 2022-04-23 15:00 | 15 | 7 | 1
2022-04-23 16:00 | 16 | 7 | 1 | 2022-04-23 16:00 | 16 | 7 | 1
2022-04-23 17:00 | 17 | 7 | 1 | 2022-04-23 17:00 | 17 | 7 | 1
2022-04-23 18:00 | 18 | 7 | 1 | 2022-04-23 18:00 | 18 | 7 | 1
2022-04-23 19:00 | 19 | 7 | 1 | 2022-04-23 19:00 | 19 | 7 | 1
2022-04-23 20:00 | 20 | 7 | 1 | 2022-04-23 20:00 | 20 | 7 | 1
2022-04-23 21:00 | 21 | 7 | 1 | 2022-04-23 21:00 | 21 | 7 | 1
2022-04-23 22:00 | 22 | 7 | 1 | 2022-04-23 22:00 | 22 | 7 | 1
2022-04-23 23:00 | 23 | 7 | 1 | 2022-04-23 23:00 | 23 | 7 | 1
2022-04-24 | 0 | 1 | 1 | 2022-04-24 | 0 | 1 | 1
2022-04-24 01:00 | 1 | 1 | 1 | 2022-04-24 01:00 | 1 | 1 | 1
2022-04-24 02:00 | 2 | 1 | 1 | 2022-04-24 02:00 | 2 | 1 | 1
2022-04-24 03:00 | 3 | 1 | 1 | 2022-04-24 03:00 | 3 | 1 | 1
2022-04-24 04:00 | 4 | 1 | 1 | 2022-04-24 04:00 | 4 | 1 | 1
2022-04-24 05:00 | 5 | 1 | 1 | 2022-04-24 05:00 | 5 | 1 | 1
2022-04-24 06:00 | 6 | 1 | 1 | 2022-04-24 06:00 | 6 | 1 | 1
2022-04-24 07:00 | 7 | 1 | 1 | 2022-04-24 07:00 | 7 | 1 | 1
2022-04-24 08:00 | 8 | 1 | 1 | 2022-04-24 08:00 | 8 | 1 | 1
2022-04-24 09:00 | 9 | 1 | 1 | 2022-04-24 09:00 | 9 | 1 | 1
2022-04-24 10:00 | 10 | 1 | 1 | 2022-04-24 10:00 | 10 | 1 | 1
2022-04-24 11:00 | 11 | 1 | 1 | 2022-04-24 11:00 | 11 | 1 | 1
2022-04-24 12:00 | 12 | 1 | 1 | 2022-04-24 12:00 | 12 | 1 | 1
2022-04-24 13:00 | 13 | 1 | 1 | 2022-04-24 13:00 | 13 | 1 | 1
2022-04-24 14:00 | 14 | 1 | 1 | 2022-04-24 14:00 | 14 | 1 | 1
2022-04-24 15:00 | 15 | 1 | 1 | 2022-04-24 15:00 | 15 | 1 | 1
2022-04-24 16:00 | 16 | 1 | 1 | 2022-04-24 16:00 | 16 | 1 | 1
2022-04-24 17:00 | 17 | 1 | 1 | 2022-04-24 17:00 | 17 | 1 | 1
2022-04-24 18:00 | 18 | 1 | 1 | 2022-04-24 18:00 | 18 | 1 | 1
2022-04-24 19:00 | 19 | 1 | 1 | 2022-04-24 19:00 | 19 | 1 | 1
2022-04-24 20:00 | 20 | 1 | 1 | 2022-04-24 20:00 | 20 | 1 | 1
2022-04-24 21:00 | 21 | 1 | 1 | 2022-04-24 21:00 | 21 | 1 | 1
2022-04-24 22:00 | 22 | 1 | 1 | 2022-04-24 22:00 | 22 | 1 | 1
2022-04-24 23:00 | 23 | 1 | 1 | 2022-04-24 23:00 | 23 | 1 | 1
2022-04-25 | 0 | 2 | 1 | 2022-04-25 | 0 | 2 | 1
2022-04-25 01:00 | 1 | 2 | 1 | 2022-04-25 01:00 | 1 | 2 | 1
2022-04-25 02:00 | 2 | 2 | 1 | 2022-04-25 02:00 | 2 | 2 | 1
2022-04-25 03:00 | 3 | 2 | 1 | 2022-04-25 03:00 | 3 | 2 | 1
2022-04-25 04:00 | 4 | 2 | 1 | 2022-04-25 04:00 | 4 | 2 | 1
2022-04-25 05:00 | 5 | 2 | 1 | 2022-04-25 05:00 | 5 | 2 | 1
2022-04-25 06:00 | 6 | 2 | 1 | 2022-04-25 06:00 | 6 | 2 | 1
2022-04-25 07:00 | 7 | 2 | 1 | 2022-04-25 07:00 | 7 | 2 | 1
2022-04-25 08:00 | 8 | 2 | 1 | 2022-04-25 08:00 | 8 | 2 | 1
2022-04-25 09:00 | 9 | 2 | 1 | 2022-04-25 09:00 | 9 | 2 | 1
2022-04-25 10:00 | 10 | 2 | 1 | 2022-04-25 10:00 | 10 | 2 | 1
2022-04-25 11:00 | 11 | 2 | 1 | 2022-04-25 11:00 | 11 | 2 | 1
2022-04-25 12:00 | 12 | 2 | 1 | 2022-04-25 12:00 | 12 | 2 | 1
2022-04-25 13:00 | 13 | 2 | 1 | 2022-04-25 13:00 | 13 | 2 | 1
2022-04-25 14:00 | 14 | 2 | 1 | 2022-04-25 14:00 | 14 | 2 | 1
2022-04-25 15:00 | 15 | 2 | 1 | 2022-04-25 15:00 | 15 | 2 | 1
2022-04-25 16:00 | 16 | 2 | 1 | 2022-04-25 16:00 | 16 | 2 | 1
2022-04-25 17:00 | 17 | 2 | 1 | 2022-04-25 17:00 | 17 | 2 | 1
2022-04-25 18:00 | 18 | 2 | 1 | 2022-04-25 18:00 | 18 | 2 | 1
2022-04-25 19:00 | 19 | 2 | 1 | 2022-04-25 19:00 | 19 | 2 | 1
2022-04-25 20:00 | 20 | 2 | 1 | 2022-04-25 20:00 | 20 | 2 | 1
2022-04-25 21:00 | 21 | 2 | 1 | 2022-04-25 21:00 | 21 | 2 | 1
2022-04-25 22:00 | 22 | 2 | 1 | 2022-04-25 22:00 | 22 | 2 | 1
2022-04-25 23:00 | 23 | 2 | 1 | 2022-04-25 23:00 | 23 | 2 | 1
2022-04-26 | 0 | 3 | 1 | 2022-04-26 | 0 | 3 | 1
2022-04-26 01:00 | 1 | 3 | 1 | 2022-04-26 01:00 | 1 | 3 | 1
2022-04-26 02:00 | 2 | 3 | 1 | 2022-04-26 02:00 | 2 | 3 | 1
2022-04-26 03:00 | 3 | 3 | 1 | 2022-04-26 03:00 | 3 | 3 | 1
2022-04-26 04:00 | 4 | 3 | 1 | 2022-04-26 04:00 | 4 | 3 | 1
2022-04-26 05:00 | 5 | 3 | 1 | 2022-04-26 05:00 | 5 | 3 | 1
2022-04-26 06:00 | 6 | 3 | 1 | 2022-04-26 06:00 | 6 | 3 | 1
2022-04-26 07:00 | 7 | 3 | 1 | 2022-04-26 07:00 | 7 | 3 | 1
2022-04-26 08:00 | 8 | 3 | 1 | 2022-04-26 08:00 | 8 | 3 | 1
2022-04-26 09:00 | 9 | 3 | 1 | 2022-04-26 09:00 | 9 | 3 | 1
2022-04-26 10:00 | 10 | 3 | 1 | 2022-04-26 10:00 | 10 | 3 | 1
2022-04-26 11:00 | 11 | 3 | 1 | 2022-04-26 11:00 | 11 | 3 | 1
2022-04-26 12:00 | 12 | 3 | 1 | 2022-04-26 12:00 | 12 | 3 | 1
2022-04-26 13:00 | 13 | 3 | 1 | 2022-04-26 13:00 | 13 | 3 | 1
2022-04-26 14:00 | 14 | 3 | 1 | 2022-04-26 14:00 | 14 | 3 | 1
2022-04-26 15:00 | 15 | 3 | 1 | 2022-04-26 15:00 | 15 | 3 | 1
2022-04-26 16:00 | 16 | 3 | 1 | 2022-04-26 16:00 | 16 | 3 | 1
2022-04-26 17:00 | 17 | 3 | 1 | 2022-04-26 17:00 | 17 | 3 | 1
2022-04-26 18:00 | 18 | 3 | 1 | 2022-04-26 18:00 | 18 | 3 | 1
2022-04-26 19:00 | 19 | 3 | 1 | 2022-04-26 19:00 | 19 | 3 | 1
2022-04-26 20:00 | 20 | 3 | 1 | 2022-04-26 20:00 | 20 | 3 | 1
2022-04-26 21:00 | 21 | 3 | 1 | 2022-04-26 21:00 | 21 | 3 | 1
2022-04-26 22:00 | 22 | 3 | 1 | 2022-04-26 22:00 | 22 | 3 | 1
2022-04-26 23:00 | 23 | 3 | 1 | 2022-04-26 23:00 | 23 | 3 | 1
2022-04-27 | 0 | 4 | 1 | 2022-04-27 | 0 | 4 | 1
2022-04-27 01:00 | 1 | 4 | 1 | 2022-04-27 01:00 | 1 | 4 | 1
2022-04-27 02:00 | 2 | 4 | 1 | 2022-04-27 02:00 | 2 | 4 | 1
2022-04-27 03:00 | 3 | 4 | 1 | 2022-04-27 03:00 | 3 | 4 | 1
2022-04-27 04:00 | 4 | 4 | 1 | 2022-04-27 04:00 | 4 | 4 | 1
2022-04-27 05:00 | 5 | 4 | 1 | 2022-04-27 05:00 | 5 | 4 | 1
2022-04-27 06:00 | 6 | 4 | 1 | 2022-04-27 06:00 | 6 | 4 | 1
2022-04-27 07:00 | 7 | 4 | 1 | 2022-04-27 07:00 | 7 | 4 | 1
2022-04-27 08:00 | 8 | 4 | 1 | 2022-04-27 08:00 | 8 | 4 | 1
2022-04-27 09:00 | 9 | 4 | 1 | 2022-04-27 09:00 | 9 | 4 | 1
2022-04-27 10:00 | 10 | 4 | 1 | 2022-04-27 10:00 | 10 | 4 | 1
2022-04-27 11:00 | 11 | 4 | 1 | 2022-04-27 11:00 | 11 | 4 | 1
2022-04-27 12:00 | 12 | 4 | 1 | 2022-04-27 12:00 | 12 | 4 | 1
2022-04-27 13:00 | 13 | 4 | 1 | 2022-04-27 13:00 | 13 | 4 | 1
2022-04-27 14:00 | 14 | 4 | 1 | 2022-04-27 14:00 | 14 | 4 | 1
2022-04-27 15:00 | 15 | 4 | 1 | 2022-04-27 15:00 | 15 | 4 | 1
2022-04-27 16:00 | 16 | 4 | 1 | 2022-04-27 16:00 | 16 | 4 | 1
2022-04-27 17:00 | 17 | 4 | 1 | 2022-04-27 17:00 | 17 | 4 | 1
2022-04-27 18:00 | 18 | 4 | 1 | 2022-04-27 18:00 | 18 | 4 | 1
2022-04-27 19:00 | 19 | 4 | 1 | 2022-04-27 19:00 | 19 | 4 | 1
2022-04-27 20:00 | 20 | 4 | 1 | 2022-04-27 20:00 | 20 | 4 | 1
2022-04-27 21:00 | 21 | 4 | 1 | 2022-04-27 21:00 | 21 | 4 | 1
2022-04-27 22:00 | 22 | 4 | 1 | 2022-04-27 22:00 | 22 | 4 | 1
2022-04-27 23:00 | 23 | 4 | 1 | 2022-04-27 23:00 | 23 | 4 | 1
2022-04-28 | 0 | 5 | 1 | 2022-04-28 | 0 | 5 | 1
2022-04-28 01:00 | 1 | 5 | 1 | 2022-04-28 01:00 | 1 | 5 | 1
2022-04-28 02:00 | 2 | 5 | 1 | 2022-04-28 02:00 | 2 | 5 | 1
2022-04-28 03:00 | 3 | 5 | 1 | 2022-04-28 03:00 | 3 | 5 | 1
2022-04-28 04:00 | 4 | 5 | 1 | 2022-04-28 04:00 | 4 | 5 | 1
2022-04-28 05:00 | 5 | 5 | 1 | 2022-04-28 05:00 | 5 | 5 | 1
2022-04-28 06:00 | 6 | 5 | 1 | 2022-04-28 06:00 | 6 | 5 | 1
2022-04-28 07:00 | 7 | 5 | 1 | 2022-04-28 07:00 | 7 | 5 | 1
2022-04-28 08:00 | 8 | 5 | 1 | 2022-04-28 08:00 | 8 | 5 | 1
2022-04-28 09:00 | 9 | 5 | 1 | 2022-04-28 09:00 | 9 | 5 | 1
2022-04-28 10:00 | 10 | 5 | 1 | 2022-04-28 10:00 | 10 | 5 | 1
2022-04-28 11:00 | 11 | 5 | 1 | 2022-04-28 11:00 | 11 | 5 | 1
2022-04-28 12:00 | 12 | 5 | 1 | 2022-04-28 12:00 | 12 | 5 | 1
2022-04-28 13:00 | 13 | 5 | 1 | 2022-04-28 13:00 | 13 | 5 | 1
2022-04-28 14:00 | 14 | 5 | 1 | 2022-04-28 14:00 | 14 | 5 | 1
2022-04-28 15:00 | 15 | 5 | 1 | 2022-04-28 15:00 | 15 | 5 | 1
2022-04-28 16:00 | 16 | 5 | 1 | 2022-04-28 16:00 | 16 | 5 | 1
2022-04-28 17:00 | 17 | 5 | 1 | 2022-04-28 17:00 | 17 | 5 | 1
2022-04-28 18:00 | 18 | 5 | 1 | 2022-04-28 18:00 | 18 | 5 | 1
2022-04-28 19:00 | 19 | 5 | 1 | 2022-04-28 19:00 | 19 | 5 | 1
2022-04-28 20:00 | 20 | 5 | 1 | 2022-04-28 20:00 | 20 | 5 | 1
2022-04-28 21:00 | 21 | 5 | 1 | 2022-04-28 21:00 | 21 | 5 | 1
2022-04-28 22:00 | 22 | 5 | 1 | 2022-04-28 22:00 | 22 | 5 | 1
2022-04-28 23:00 | 23 | 5 | 1 | 2022-04-28 23:00 | 23 | 5 | 1
2022-04-29 | 0 | 6 | 1 | 2022-04-29 | 0 | 6 | 1
2022-04-29 01:00 | 1 | 6 | 1 | 2022-04-29 01:00 | 1 | 6 | 1
2022-04-29 02:00 | 2 | 6 | 1 | 2022-04-29 02:00 | 2 | 6 | 1
2022-04-29 03:00 | 3 | 6 | 1 | 2022-04-29 03:00 | 3 | 6 | 1
2022-04-29 04:00 | 4 | 6 | 1 | 2022-04-29 04:00 | 4 | 6 | 1
2022-04-29 05:00 | 5 | 6 | 1 | 2022-04-29 05:00 | 5 | 6 | 1
2022-04-29 06:00 | 6 | 6 | 1 | 2022-04-29 06:00 | 6 | 6 | 1
2022-04-29 07:00 | 7 | 6 | 1 | 2022-04-29 07:00 | 7 | 6 | 1
2022-04-29 08:00 | 8 | 6 | 1 | 2022-04-29 08:00 | 8 | 6 | 1
2022-04-29 09:00 | 9 | 6 | 1 | 2022-04-29 09:00 | 9 | 6 | 1
2022-04-29 10:00 | 10 | 6 | 1 | 2022-04-29 10:00 | 10 | 6 | 1
2022-04-29 11:00 | 11 | 6 | 1 | 2022-04-29 11:00 | 11 | 6 | 1
2022-04-29 12:00 | 12 | 6 | 1 | 2022-04-29 12:00 | 12 | 6 | 1
2022-04-29 13:00 | 13 | 6 | 1 | 2022-04-29 13:00 | 13 | 6 | 1
2022-04-29 14:00 | 14 | 6 | 1 | 2022-04-29 14:00 | 14 | 6 | 1
2022-04-29 15:00 | 15 | 6 | 1 | 2022-04-29 15:00 | 15 | 6 | 1
2022-04-29 16:00 | 16 | 6 | 1 | 2022-04-29 16:00 | 16 | 6 | 1
2022-04-29 17:00 | 17 | 6 | 1 | 2022-04-29 17:00 | 17 | 6 | 1
2022-04-29 18:00 | 18 | 6 | 1 | 2022-04-29 18:00 | 18 | 6 | 1
2022-04-29 19:00 | 19 | 6 | 1 | 2022-04-29 19:00 | 19 | 6 | 1
2022-04-29 20:00 | 20 | 6 | 1 | 2022-04-29 20:00 | 20 | 6 | 1
2022-04-29 21:00 | 21 | 6 | 1 | 2022-04-29 21:00 | 21 | 6 | 1
2022-04-29 22:00 | 22 | 6 | 1 | 2022-04-29 22:00 | 22 | 6 | 1
2022-04-29 23:00 | 23 | 6 | 1 | 2022-04-29 23:00 | 23 | 6 | 1
2022-04-30 | 0 | 7 | 1 | 2022-04-30 | 0 | 7 | 1
2022-04-30 01:00 | 1 | 7 | 1 | 2022-04-30 01:00 | 1 | 7 | 1
2022-04-30 02:00 | 2 | 7 | 1 | 2022-04-30 02:00 | 2 | 7 | 1
2022-04-30 03:00 | 3 | 7 | 1 | 2022-04-30 03:00 | 3 | 7 | 1
2022-04-30 04:00 | 4 | 7 | 1 | 2022-04-30 04:00 | 4 | 7 | 1
2022-04-30 05:00 | 5 | 7 | 1 | 2022-04-30 05:00 | 5 | 7 | 1
2022-04-30 06:00 | 6 | 7 | 1 | 2022-04-30 06:00 | 6 | 7 | 1
2022-04-30 07:00 | 7 | 7 | 1 | 2022-04-30 07:00 | 7 | 7 | 1
2022-04-30 08:00 | 8 | 7 | 1 | 2022-04-30 08:00 | 8 | 7 | 1
2022-04-30 09:00 | 9 | 7 | 1 | 2022-04-30 09:00 | 9 | 7 | 1
2022-04-30 10:00 | 10 | 7 | 1 | 2022-04-30 10:00 | 10 | 7 | 1
2022-04-30 11:00 | 11 | 7 | 1 | 2022-04-30 11:00 | 11 | 7 | 1
2022-04-30 12:00 | 12 | 7 | 1 | 2022-04-30 12:00 | 12 | 7 | 1
2022-04-30 13:00 | 13 | 7 | 1 | 2022-04-30 13:00 | 13 | 7 | 1
2022-04-30 14:00 | 14 | 7 | 1 | 2022-04-30 14:00 | 14 | 7 | 1
2022-04-30 15:00 | 15 | 7 | 1 | 2022-04-30 15:00 | 15 | 7 | 1
2022-04-30 16:00 | 16 | 7 | 1 | 2022-04-30 16:00 | 16 | 7 | 1
2022-04-30 17:00 | 17 | 7 | 1 | 2022-04-30 17:00 | 17 | 7 | 1
2022-04-30 18:00 | 18 | 7 | 1 | 2022-04-30 18:00 | 18 | 7 | 1
2022-04-30 19:00 | 19 | 7 | 1 | 2022-04-30 19:00 | 19 | 7 | 1
2022-04-30 20:00 | 20 | 7 | 1 | 2022-04-30 20:00 | 20 | 7 | 1
2022-04-30 21:00 | 21 | 7 | 1 | 2022-04-30 21:00 | 21 | 7 | 1
2022-04-30 22:00 | 22 | 7 | 1 | 2022-04-30 22:00 | 22 | 7 | 1
2022-04-30 23:00 | 23 | 7 | 1 | 2022-04-30 23:00 | 23 | 7 | 1
2022-05-01 | 0 | 1 | 1 | 2022-05-01 | 0 | 1 | 1
2022-05-01 01:00 | 1 | 1 | 1 | 2022-05-01 01:00 | 1 | 1 | 1
2022-05-01 02:00 | 2 | 1 | 1 | 2022-05-01 02:00 | 2 | 1 | 1
2022-05-01 03:00 | 3 | 1 | 1 | 2022-05-01 03:00 | 3 | 1 | 1
2022-05-01 04:00 | 4 | 1 | 1 | 2022-05-01 04:00 | 4 | 1 | 1
2022-05-01 05:00 | 5 | 1 | 1 | 2022-05-01 05:00 | 5 | 1 | 1
2022-05-01 06:00 | 6 | 1 | 1 | 2022-05-01 06:00 | 6 | 1 | 1
2022-05-01 07:00 | 7 | 1 | 1 | 2022-05-01 07:00 | 7 | 1 | 1
2022-05-01 08:00 | 8 | 1 | 1 | 2022-05-01 08:00 | 8 | 1 | 1
2022-05-01 09:00 | 9 | 1 | 1 | 2022-05-01 09:00 | 9 | 1 | 1
2022-05-01 10:00 | 10 | 1 | 1 | 2022-05-01 10:00 | 10 | 1 | 1
2022-05-01 11:00 | 11 | 1 | 1 | 2022-05-01 11:00 | 11 | 1 | 1
2022-05-01 12:00 | 12 | 1 | 1 | 2022-05-01 12:00 | 12 | 1 | 1
2022-05-01 13:00 | 13 | 1 | 1 | 2022-05-01 13:00 | 13 | 1 | 1
2022-05-01 14:00 | 14 | 1 | 1 | 2022-05-01 14:00 | 14 | 1 | 1
2022-05-01 15:00 | 15 | 1 | 1 | 2022-05-01 15:00 | 15 | 1 | 1
2022-05-01 16:00 | 16 | 1 | 1 | 2022-05-01 16:00 | 16 | 1 | 1
2022-05-01 17:00 | 17 | 1 | 1 | 2022-05-01 17:00 | 17 | 1 | 1
2022-05-01 18:00 | 18 | 1 | 1 | 2022-05-01 18:00 | 18 | 1 | 1
2022-05-01 19:00 | 19 | 1 | 1 | 2022-05-01 19:00 | 19 | 1 | 1
2022-05-01 20:00 | 20 | 1 | 1 | 2022-05-01 20:00 | 20 | 1 | 1
2022-05-01 21:00 | 21 | 1 | 1 | 2022-05-01 21:00 | 21 | 1 | 1
2022-05-01 22:00 | 22 | 1 | 1 | 2022-05-01 22:00 | 22 | 1 | 1
2022-05-01 23:00 | 23 | 1 | 1 | 2022-05-01 23:00 | 23 | 1 | 1
2022-05-02 | 0 | 2 | 1 | 2022-05-02 | 0 | 2 | 1
2022-05-02 01:00 | 1 | 2 | 1 | 2022-05-02 01:00 | 1 | 2 | 1
2022-05-02 02:00 | 2 | 2 | 1 | 2022-05-02 02:00 | 2 | 2 | 1
2022-05-02 03:00 | 3 | 2 | 1 | 2022-05-02 03:00 | 3 | 2 | 1
2022-05-02 04:00 | 4 | 2 | 1 | 2022-05-02 04:00 | 4 | 2 | 1
2022-05-02 05:00 | 5 | 2 | 1 | 2022-05-02 05:00 | 5 | 2 | 1
2022-05-02 06:00 | 6 | 2 | 1 | 2022-05-02 06:00 | 6 | 2 | 1
2022-05-02 07:00 | 7 | 2 | 1 | 2022-05-02 07:00 | 7 | 2 | 1
2022-05-02 08:00 | 8 | 2 | 1 | 2022-05-02 08:00 | 8 | 2 | 1
2022-05-02 09:00 | 9 | 2 | 1 | 2022-05-02 09:00 | 9 | 2 | 1
2022-05-02 10:00 | 10 | 2 | 1 | 2022-05-02 10:00 | 10 | 2 | 1
2022-05-02 11:00 | 11 | 2 | 1 | 2022-05-02 11:00 | 11 | 2 | 1
2022-05-02 12:00 | 12 | 2 | 1 | 2022-05-02 12:00 | 12 | 2 | 1
2022-05-02 13:00 | 13 | 2 | 1 | 2022-05-02 13:00 | 13 | 2 | 1
2022-05-02 14:00 | 14 | 2 | 1 | 2022-05-02 14:00 | 14 | 2 | 1
2022-05-02 15:00 | 15 | 2 | 1 | 2022-05-02 15:00 | 15 | 2 | 1
2022-05-02 16:00 | 16 | 2 | 1 | 2022-05-02 16:00 | 16 | 2 | 1
2022-05-02 17:00 | 17 | 2 | 1 | 2022-05-02 17:00 | 17 | 2 | 1
2022-05-02 18:00 | 18 | 2 | 1 | 2022-05-02 18:00 | 18 | 2 | 1
2022-05-02 19:00 | 19 | 2 | 1 | 2022-05-02 19:00 | 19 | 2 | 1
2022-05-02 20:00 | 20 | 2 | 1 | 2022-05-02 20:00 | 20 | 2 | 1
2022-05-02 21:00 | 21 | 2 | 1 | 2022-05-02 21:00 | 21 | 2 | 1
2022-05-02 22:00 | 22 | 2 | 1 | 2022-05-02 22:00 | 22 | 2 | 1
2022-05-02 23:00 | 23 | 2 | 1 | 2022-05-02 23:00 | 23 | 2 | 1
2022-05-03 | 0 | 3 | 1 | 2022-05-03 | 0 | 3 | 1
2022-05-03 01:00 | 1 | 3 | 1 | 2022-05-03 01:00 | 1 | 3 | 1
2022-05-03 02:00 | 2 | 3 | 1 | 2022-05-03 02:00 | 2 | 3 | 1
2022-05-03 03:00 | 3 | 3 | 1 | 2022-05-03 03:00 | 3 | 3 | 1
2022-05-03 04:00 | 4 | 3 | 1 | 2022-05-03 04:00 | 4 | 3 | 1
2022-05-03 05:00 | 5 | 3 | 1 | 2022-05-03 05:00 | 5 | 3 | 1
2022-05-03 06:00 | 6 | 3 | 1 | 2022-05-03 06:00 | 6 | 3 | 1
2022-05-03 07:00 | 7 | 3 | 1 | 2022-05-03 07:00 | 7 | 3 | 1
2022-05-03 08:00 | 8 | 3 | 1 | 2022-05-03 08:00 | 8 | 3 | 1
2022-05-03 09:00 | 9 | 3 | 1 | 2022-05-03 09:00 | 9 | 3 | 1
2022-05-03 10:00 | 10 | 3 | 1 | 2022-05-03 10:00 | 10 | 3 | 1
2022-05-03 11:00 | 11 | 3 | 1 | 2022-05-03 11:00 | 11 | 3 | 1
2022-05-03 12:00 | 12 | 3 | 1 | 2022-05-03 12:00 | 12 | 3 | 1
2022-05-03 13:00 | 13 | 3 | 1 | 2022-05-03 13:00 | 13 | 3 | 1
2022-05-03 14:00 | 14 | 3 | 1 | 2022-05-03 14:00 | 14 | 3 | 1
2022-05-03 15:00 | 15 | 3 | 1 | 2022-05-03 15:00 | 15 | 3 | 1
2022-05-03 16:00 | 16 | 3 | 1 | 2022-05-03 16:00 | 16 | 3 | 1
2022-05-03 17:00 | 17 | 3 | 1 | 2022-05-03 17:00 | 17 | 3 | 1
2022-05-03 18:00 | 18 | 3 | 1 | 2022-05-03 18:00 | 18 | 3 | 1
2022-05-03 19:00 | 19 | 3 | 1 | 2022-05-03 19:00 | 19 | 3 | 1
2022-05-03 20:00 | 20 | 3 | 1 | 2022-05-03 20:00 | 20 | 3 | 1
2022-05-03 21:00 | 21 | 3 | 1 | 2022-05-03 21:00 | 21 | 3 | 1
2022-05-03 22:00 | 22 | 3 | 1 | 2022-05-03 22:00 | 22 | 3 | 1
2022-05-03 23:00 | 23 | 3 | 1 | 2022-05-03 23:00 | 23 | 3 | 1
2022-05-04 | 0 | 4 | 1 | 2022-05-04 | 0 | 4 | 1
2022-05-04 01:00 | 1 | 4 | 1 | 2022-05-04 01:00 | 1 | 4 | 1
2022-05-04 02:00 | 2 | 4 | 1 | 2022-05-04 02:00 | 2 | 4 | 1
2022-05-04 03:00 | 3 | 4 | 1 | 2022-05-04 03:00 | 3 | 4 | 1
2022-05-04 04:00 | 4 | 4 | 1 | 2022-05-04 04:00 | 4 | 4 | 1
2022-05-04 05:00 | 5 | 4 | 1 | 2022-05-04 05:00 | 5 | 4 | 1
2022-05-04 06:00 | 6 | 4 | 1 | 2022-05-04 06:00 | 6 | 4 | 1
2022-05-04 07:00 | 7 | 4 | 1 | 2022-05-04 07:00 | 7 | 4 | 1
2022-05-04 08:00 | 8 | 4 | 1 | 2022-05-04 08:00 | 8 | 4 | 1
2022-05-04 09:00 | 9 | 4 | 1 | 2022-05-04 09:00 | 9 | 4 | 1
2022-05-04 10:00 | 10 | 4 | 1 | 2022-05-04 10:00 | 10 | 4 | 1
2022-05-04 11:00 | 11 | 4 | 1 | 2022-05-04 11:00 | 11 | 4 | 1
2022-05-04 12:00 | 12 | 4 | 1 | 2022-05-04 12:00 | 12 | 4 | 1
2022-05-04 13:00 | 13 | 4 | 1 | 2022-05-04 13:00 | 13 | 4 | 1
2022-05-04 14:00 | 14 | 4 | 1 | 2022-05-04 14:00 | 14 | 4 | 1
2022-05-04 15:00 | 15 | 4 | 1 | 2022-05-04 15:00 | 15 | 4 | 1
2022-05-04 16:00 | 16 | 4 | 1 | 2022-05-04 16:00 | 16 | 4 | 1
2022-05-04 17:00 | 17 | 4 | 1 | 2022-05-04 17:00 | 17 | 4 | 1
2022-05-04 18:00 | 18 | 4 | 1 | 2022-05-04 18:00 | 18 | 4 | 1
2022-05-04 19:00 | 19 | 4 | 1 | 2022-05-04 19:00 | 19 | 4 | 1
2022-05-04 20:00 | 20 | 4 | 1 | 2022-05-04 20:00 | 20 | 4 | 1
2022-05-04 21:00 | 21 | 4 | 1 | 2022-05-04 21:00 | 21 | 4 | 1
2022-05-04 22:00 | 22 | 4 | 1 | 2022-05-04 22:00 | 22 | 4 | 1
2022-05-04 23:00 | 23 | 4 | 1 | 2022-05-04 23:00 | 23 | 4 | 1
2022-05-05 | 0 | 5 | 1 | 2022-05-05 | 0 | 5 | 1
2022-05-05 01:00 | 1 | 5 | 1 | 2022-05-05 01:00 | 1 | 5 | 1
2022-05-05 02:00 | 2 | 5 | 1 | 2022-05-05 02:00 | 2 | 5 | 1
2022-05-05 03:00 | 3 | 5 | 1 | 2022-05-05 03:00 | 3 | 5 | 1
2022-05-05 04:00 | 4 | 5 | 1 | 2022-05-05 04:00 | 4 | 5 | 1
2022-05-05 05:00 | 5 | 5 | 1 | 2022-05-05 05:00 | 5 | 5 | 1
2022-05-05 06:00 | 6 | 5 | 1 | 2022-05-05 06:00 | 6 | 5 | 1
2022-05-05 07:00 | 7 | 5 | 1 | 2022-05-05 07:00 | 7 | 5 | 1
2022-05-05 08:00 | 8 | 5 | 1 | 2022-05-05 08:00 | 8 | 5 | 1
2022-05-05 09:00 | 9 | 5 | 1 | 2022-05-05 09:00 | 9 | 5 | 1
2022-05-05 10:00 | 10 | 5 | 1 | 2022-05-05 10:00 | 10 | 5 | 1
2022-05-05 11:00 | 11 | 5 | 1 | 2022-05-05 11:00 | 11 | 5 | 1
2022-05-05 12:00 | 12 | 5 | 1 | 2022-05-05 12:00 | 12 | 5 | 1
2022-05-05 13:00 | 13 | 5 | 1 | 2022-05-05 13:00 | 13 | 5 | 1
2022-05-05 14:00 | 14 | 5 | 1 | 2022-05-05 14:00 | 14 | 5 | 1
2022-05-05 15:00 | 15 | 5 | 1 | 2022-05-05 15:00 | 15 | 5 | 1
2022-05-05 16:00 | 16 | 5 | 1 | 2022-05-05 16:00 | 16 | 5 | 1
2022-05-05 17:00 | 17 | 5 | 1 | 2022-05-05 17:00 | 17 | 5 | 1
2022-05-05 18:00 | 18 | 5 | 1 | 2022-05-05 18:00 | 18 | 5 | 1
2022-05-05 19:00 | 19 | 5 | 1 | 2022-05-05 19:00 | 19 | 5 | 1
2022-05-05 20:00 | 20 | 5 | 1 | 2022-05-05 20:00 | 20 | 5 | 1
2022-05-05 21:00 | 21 | 5 | 1 | 2022-05-05 21:00 | 21 | 5 | 1
2022-05-05 22:00 | 22 | 5 | 1 | 2022-05-05 22:00 | 22 | 5 | 1
2022-05-05 23:00 | 23 | 5 | 1 | 2022-05-05 23:00 | 23 | 5 | 1
2022-05-06 | 0 | 6 | 1 | 2022-05-06 | 0 | 6 | 1
2022-05-06 01:00 | 1 | 6 | 1 | 2022-05-06 01:00 | 1 | 6 | 1
2022-05-06 02:00 | 2 | 6 | 1 | 2022-05-06 02:00 | 2 | 6 | 1
2022-05-06 03:00 | 3 | 6 | 1 | 2022-05-06 03:00 | 3 | 6 | 1
2022-05-06 04:00 | 4 | 6 | 1 | 2022-05-06 04:00 | 4 | 6 | 1
2022-05-06 05:00 | 5 | 6 | 1 | 2022-05-06 05:00 | 5 | 6 | 1
2022-05-06 06:00 | 6 | 6 | 1 | 2022-05-06 06:00 | 6 | 6 | 1
2022-05-06 07:00 | 7 | 6 | 1 | 2022-05-06 07:00 | 7 | 6 | 1
2022-05-06 08:00 | 8 | 6 | 1 | 2022-05-06 08:00 | 8 | 6 | 1
2022-05-06 09:00 | 9 | 6 | 1 | 2022-05-06 09:00 | 9 | 6 | 1
2022-05-06 10:00 | 10 | 6 | 1 | 2022-05-06 10:00 | 10 | 6 | 1
2022-05-06 11:00 | 11 | 6 | 1 | 2022-05-06 11:00 | 11 | 6 | 1
2022-05-06 12:00 | 12 | 6 | 1 | 2022-05-06 12:00 | 12 | 6 | 1
2022-05-06 13:00 | 13 | 6 | 1 | 2022-05-06 13:00 | 13 | 6 | 1
2022-05-06 14:00 | 14 | 6 | 1 | 2022-05-06 14:00 | 14 | 6 | 1
2022-05-06 15:00 | 15 | 6 | 1 | 2022-05-06 15:00 | 15 | 6 | 1
2022-05-06 16:00 | 16 | 6 | 1 | 2022-05-06 16:00 | 16 | 6 | 1
2022-05-06 17:00 | 17 | 6 | 1 | 2022-05-06 17:00 | 17 | 6 | 1
2022-05-06 18:00 | 18 | 6 | 1 | 2022-05-06 18:00 | 18 | 6 | 1
2022-05-06 19:00 | 19 | 6 | 1 | 2022-05-06 19:00 | 19 | 6 | 1
2022-05-06 20:00 | 20 | 6 | 1 | 2022-05-06 20:00 | 20 | 6 | 1
2022-05-06 21:00 | 21 | 6 | 1 | 2022-05-06 21:00 | 21 | 6 | 1
2022-05-06 22:00 | 22 | 6 | 1 | 2022-05-06 22:00 | 22 | 6 | 1
2022-05-06 23:00 | 23 | 6 | 1 | 2022-05-06 23:00 | 23 | 6 | 1
2022-05-07 | 0 | 7 | 1 | 2022-05-07 | 0 | 7 | 1
2022-05-07 01:00 | 1 | 7 | 1 | 2022-05-07 01:00 | 1 | 7 | 1
2022-05-07 02:00 | 2 | 7 | 1 | 2022-05-07 02:00 | 2 | 7 | 1
2022-05-07 03:00 | 3 | 7 | 1 | 2022-05-07 03:00 | 3 | 7 | 1
2022-05-07 04:00 | 4 | 7 | 1 | 2022-05-07 04:00 | 4 | 7 | 1
2022-05-07 05:00 | 5 | 7 | 1 | 2022-05-07 05:00 | 5 | 7 | 1
2022-05-07 06:00 | 6 | 7 | 1 | 2022-05-07 06:00 | 6 | 7 | 1
2022-05-07 07:00 | 7 | 7 | 1 | 2022-05-07 07:00 | 7 | 7 | 1
2022-05-07 08:00 | 8 | 7 | 1 | 2022-05-07 08:00 | 8 | 7 | 1
2022-05-07 09:00 | 9 | 7 | 1 | 2022-05-07 09:00 | 9 | 7 | 1
2022-05-07 10:00 | 10 | 7 | 1 | 2022-05-07 10:00 | 10 | 7 | 1
2022-05-07 11:00 | 11 | 7 | 1 | 2022-05-07 11:00 | 11 | 7 | 1
2022-05-07 12:00 | 12 | 7 | 1 | 2022-05-07 12:00 | 12 | 7 | 1
2022-05-07 13:00 | 13 | 7 | 1 | 2022-05-07 13:00 | 13 | 7 | 1
2022-05-07 14:00 | 14 | 7 | 1 | 2022-05-07 14:00 | 14 | 7 | 1
2022-05-07 15:00 | 15 | 7 | 1 | 2022-05-07 15:00 | 15 | 7 | 1
2022-05-07 16:00 | 16 | 7 | 1 | 2022-05-07 16:00 | 16 | 7 | 1
2022-05-07 17:00 | 17 | 7 | 1 | 2022-05-07 17:00 | 17 | 7 | 1
2022-05-07 18:00 | 18 | 7 | 1 | 2022-05-07 18:00 | 18 | 7 | 1
2022-05-07 19:00 | 19 | 7 | 1 | 2022-05-07 19:00 | 19 | 7 | 1
2022-05-07 20:00 | 20 | 7 | 1 | 2022-05-07 20:00 | 20 | 7 | 1
2022-05-07 21:00 | 21 | 7 | 1 | 2022-05-07 21:00 | 21 | 7 | 1
2022-05-07 22:00 | 22 | 7 | 1 | 2022-05-07 22:00 | 22 | 7 | 1
2022-05-07 23:00 | 23 | 7 | 1 | 2022-05-07 23:00 | 23 | 7 | 1
2022-05-08 | 0 | 1 | 1 | 2022-05-08 | 0 | 1 | 1
2022-05-08 01:00 | 1 | 1 | 1 | 2022-05-08 01:00 | 1 | 1 | 1
2022-05-08 02:00 | 2 | 1 | 1 | 2022-05-08 02:00 | 2 | 1 | 1
2022-05-08 03:00 | 3 | 1 | 1 | 2022-05-08 03:00 | 3 | 1 | 1
2022-05-08 04:00 | 4 | 1 | 1 | 2022-05-08 04:00 | 4 | 1 | 1
2022-05-08 05:00 | 5 | 1 | 1 | 2022-05-08 05:00 | 5 | 1 | 1
2022-05-08 06:00 | 6 | 1 | 1 | 2022-05-08 06:00 | 6 | 1 | 1
2022-05-08 07:00 | 7 | 1 | 1 | 2022-05-08 07:00 | 7 | 1 | 1
2022-05-08 08:00 | 8 | 1 | 1 | 2022-05-08 08:00 | 8 | 1 | 1
2022-05-08 09:00 | 9 | 1 | 1 | 2022-05-08 09:00 | 9 | 1 | 1
2022-05-08 10:00 | 10 | 1 | 1 | 2022-05-08 10:00 | 10 | 1 | 1
2022-05-08 11:00 | 11 | 1 | 1 | 2022-05-08 11:00 | 11 | 1 | 1
2022-05-08 12:00 | 12 | 1 | 1 | 2022-05-08 12:00 | 12 | 1 | 1
2022-05-08 13:00 | 13 | 1 | 1 | 2022-05-08 13:00 | 13 | 1 | 1
2022-05-08 14:00 | 14 | 1 | 1 | 2022-05-08 14:00 | 14 | 1 | 1
2022-05-08 15:00 | 15 | 1 | 1 | 2022-05-08 15:00 | 15 | 1 | 1
2022-05-08 16:00 | 16 | 1 | 1 | 2022-05-08 16:00 | 16 | 1 | 1
2022-05-08 17:00 | 17 | 1 | 1 | 2022-05-08 17:00 | 17 | 1 | 1
2022-05-08 18:00 | 18 | 1 | 1 | 2022-05-08 18:00 | 18 | 1 | 1
2022-05-08 19:00 | 19 | 1 | 1 | 2022-05-08 19:00 | 19 | 1 | 1
2022-05-08 20:00 | 20 | 1 | 1 | 2022-05-08 20:00 | 20 | 1 | 1
2022-05-08 21:00 | 21 | 1 | 1 | 2022-05-08 21:00 | 21 | 1 | 1
2022-05-08 22:00 | 22 | 1 | 1 | 2022-05-08 22:00 | 22 | 1 | 1
2022-05-08 23:00 | 23 | 1 | 1 | 2022-05-08 23:00 | 23 | 1 | 1
2022-05-09 | 0 | 2 | 1 | 2022-05-09 | 0 | 2 | 1
2022-05-09 01:00 | 1 | 2 | 1 | 2022-05-09 01:00 | 1 | 2 | 1
2022-05-09 02:00 | 2 | 2 | 1 | 2022-05-09 02:00 | 2 | 2 | 1
2022-05-09 03:00 | 3 | 2 | 1 | 2022-05-09 03:00 | 3 | 2 | 1
2022-05-09 04:00 | 4 | 2 | 1 | 2022-05-09 04:00 | 4 | 2 | 1
2022-05-09 05:00 | 5 | 2 | 1 | 2022-05-09 05:00 | 5 | 2 | 1
2022-05-09 06:00 | 6 | 2 | 1 | 2022-05-09 06:00 | 6 | 2 | 1
2022-05-09 07:00 | 7 | 2 | 1 | 2022-05-09 07:00 | 7 | 2 | 1
2022-05-09 08:00 | 8 | 2 | 1 | 2022-05-09 08:00 | 8 | 2 | 1
2022-05-09 09:00 | 9 | 2 | 1 | 2022-05-09 09:00 | 9 | 2 | 1
2022-05-09 10:00 | 10 | 2 | 1 | 2022-05-09 10:00 | 10 | 2 | 1
2022-05-09 11:00 | 11 | 2 | 1 | 2022-05-09 11:00 | 11 | 2 | 1
2022-05-09 12:00 | 12 | 2 | 1 | 2022-05-09 12:00 | 12 | 2 | 1
2022-05-09 13:00 | 13 | 2 | 1 | 2022-05-09 13:00 | 13 | 2 | 1
2022-05-09 14:00 | 14 | 2 | 1 | 2022-05-09 14:00 | 14 | 2 | 1
2022-05-09 15:00 | 15 | 2 | 1 | 2022-05-09 15:00 | 15 | 2 | 1
2022-05-09 16:00 | 16 | 2 | 1 | 2022-05-09 16:00 | 16 | 2 | 1
2022-05-09 17:00 | 17 | 2 | 1 | 2022-05-09 17:00 | 17 | 2 | 1
2022-05-09 18:00 | 18 | 2 | 1 | 2022-05-09 18:00 | 18 | 2 | 1
2022-05-09 19:00 | 19 | 2 | 1 | 2022-05-09 19:00 | 19 | 2 | 1
2022-05-09 20:00 | 20 | 2 | 1 | 2022-05-09 20:00 | 20 | 2 | 1
2022-05-09 21:00 | 21 | 2 | 1 | 2022-05-09 21:00 | 21 | 2 | 1
2022-05-09 22:00 | 22 | 2 | 1 | 2022-05-09 22:00 | 22 | 2 | 1
2022-05-09 23:00 | 23 | 2 | 1 | 2022-05-09 23:00 | 23 | 2 | 1
2022-05-10 | 0 | 3 | 1 | 2022-05-10 | 0 | 3
2022-05-10 01:00 | 1 | 3 | 1 | 2022-05-10 01:00 | 1 | 3
2022-05-10 02:00 | 2 | 3 | 1 | 2022-05-10 02:00 | 2 | 3
2022-05-10 03:00 | 3 | 3 | 1 | 2022-05-10 03:00 | 3 | 3
2022-05-10 04:00 | 4 | 3 | 1 | 2022-05-10 04:00 | 4 | 3
2022-05-10 05:00 | 5 | 3 | 1 | 2022-05-10 05:00 | 5 | 3
2022-05-10 06:00 | 6 | 3 | 1 | 2022-05-10 06:00 | 6 | 3
2022-05-10 07:00 | 7 | 3 | 1 | 2022-05-10 07:00 | 7 | 3
2022-05-10 08:00 | 8 | 3 | 1 | 2022-05-10 08:00 | 8 | 3
2022-05-10 09:00 | 9 | 3 | 1 | 2022-05-10 09:00 | 9 | 3
2022-05-10 10:00 | 10 | 3 | 1 | 2022-05-10 10:00 | 10 | 3
2022-05-10 11:00 | 11 | 3 | 1 | 2022-05-10 11:00 | 11 | 3
2022-05-10 12:00 | 12 | 3 | 1 | 2022-05-10 12:00 | 12 | 3
2022-05-10 13:00 | 13 | 3 | 1 | 2022-05-10 13:00 | 13 | 3
2022-05-10 14:00 | 14 | 3 | 1 | 2022-05-10 14:00 | 14 | 3
2022-05-10 15:00 | 15 | 3 | 1 | 2022-05-10 15:00 | 15 | 3
2022-05-10 16:00 | 16 | 3 | 1 | 2022-05-10 16:00 | 16 | 3
2022-05-10 17:00 | 17 | 3 | 1 | 2022-05-10 17:00 | 17 | 3
2022-05-10 18:00 | 18 | 3 | 1 | 2022-05-10 18:00 | 18 | 3
2022-05-10 19:00 | 19 | 3 | 1 | 2022-05-10 19:00 | 19 | 3
2022-05-10 20:00 | 20 | 3 | 1 | 2022-05-10 20:00 | 20 | 3
2022-05-10 21:00 | 21 | 3 | 1 | 2022-05-10 21:00 | 21 | 3
2022-05-10 22:00 | 22 | 3 | 1 | 2022-05-10 22:00 | 22 | 3
2022-05-10 23:00 | 23 | 3 | 1 | 2022-05-10 23:00 | 23 | 3
2022-05-11 | 0 | 4 | 1 | 2022-05-11 | 0 | 4
2022-05-11 01:00 | 1 | 4 | 1 | 2022-05-11 01:00 | 1 | 4
2022-05-11 02:00 | 2 | 4 | 1 | 2022-05-11 02:00 | 2 | 4
2022-05-11 03:00 | 3 | 4 | 1 | 2022-05-11 03:00 | 3 | 4
2022-05-11 04:00 | 4 | 4 | 1 | 2022-05-11 04:00 | 4 | 4
2022-05-11 05:00 | 5 | 4 | 1 | 2022-05-11 05:00 | 5 | 4
2022-05-11 06:00 | 6 | 4 | 1 | 2022-05-11 06:00 | 6 | 4
2022-05-11 07:00 | 7 | 4 | 1 | 2022-05-11 07:00 | 7 | 4
2022-05-11 08:00 | 8 | 4 | 1 | 2022-05-11 08:00 | 8 | 4
2022-05-11 09:00 | 9 | 4 | 1 | 2022-05-11 09:00 | 9 | 4
2022-05-11 10:00 | 10 | 4 | 1 | 2022-05-11 10:00 | 10 | 4
2022-05-11 11:00 | 11 | 4 | 1 | 2022-05-11 11:00 | 11 | 4
2022-05-11 12:00 | 12 | 4 | 1 | 2022-05-11 12:00 | 12 | 4
2022-05-11 13:00 | 13 | 4 | 1 | 2022-05-11 13:00 | 13 | 4
2022-05-11 14:00 | 14 | 4 | 1 | 2022-05-11 14:00 | 14 | 4
2022-05-11 15:00 | 15 | 4 | 1 | 2022-05-11 15:00 | 15 | 4
2022-05-11 16:00 | 16 | 4 | 1 | 2022-05-11 16:00 | 16 | 4
2022-05-11 17:00 | 17 | 4 | 1 | 2022-05-11 17:00 | 17 | 4
2022-05-11 18:00 | 18 | 4 | 1 | 2022-05-11 18:00 | 18 | 4
2022-05-11 19:00 | 19 | 4 | 1 | 2022-05-11 19:00 | 19 | 4
2022-05-11 20:00 | 20 | 4 | 1 | 2022-05-11 20:00 | 20 | 4
2022-05-11 21:00 | 21 | 4 | 1 | 2022-05-11 21:00 | 21 | 4
2022-05-11 22:00 | 22 | 4 | 1 | 2022-05-11 22:00 | 22 | 4
2022-05-11 23:00 | 23 | 4 | 1 | 2022-05-11 23:00 | 23 | 4
2022-05-12 | 0 | 5 | 1 | 2022-05-12 | 0 | 5
2022-05-12 01:00 | 1 | 5 | 1 | 2022-05-12 01:00 | 1 | 5
2022-05-12 02:00 | 2 | 5 | 1 | 2022-05-12 02:00 | 2 | 5
2022-05-12 03:00 | 3 | 5 | 1 | 2022-05-12 03:00 | 3 | 5
2022-05-12 04:00 | 4 | 5 | 1 | 2022-05-12 04:00 | 4 | 5
2022-05-12 05:00 | 5 | 5 | 1 | 2022-05-12 05:00 | 5 | 5
2022-05-12 06:00 | 6 | 5 | 1 | 2022-05-12 06:00 | 6 | 5
2022-05-12 07:00 | 7 | 5 | 1 | 2022-05-12 07:00 | 7 | 5
2022-05-12 08:00 | 8 | 5 | 1 | 2022-05-12 08:00 | 8 | 5
2022-05-12 09:00 | 9 | 5 | 1 | 2022-05-12 09:00 | 9 | 5
2022-05-12 10:00 | 10 | 5 | 1 | 2022-05-12 10:00 | 10 | 5
2022-05-12 11:00 | 11 | 5 | 1 | 2022-05-12 11:00 | 11 | 5
2022-05-12 12:00 | 12 | 5 | 1 | 2022-05-12 12:00 | 12 | 5
2022-05-12 13:00 | 13 | 5 | 1 | 2022-05-12 13:00 | 13 | 5
2022-05-12 14:00 | 14 | 5 | 1 | 2022-05-12 14:00 | 14 | 5
2022-05-12 15:00 | 15 | 5 | 1 | 2022-05-12 15:00 | 15 | 5
2022-05-12 16:00 | 16 | 5 | 1 | 2022-05-12 16:00 | 16 | 5
2022-05-12 17:00 | 17 | 5 | 1 | 2022-05-12 17:00 | 17 | 5
2022-05-12 18:00 | 18 | 5 | 1 | 2022-05-12 18:00 | 18 | 5
2022-05-12 19:00 | 19 | 5 | 1 | 2022-05-12 19:00 | 19 | 5
2022-05-12 20:00 | 20 | 5 | 1 | 2022-05-12 20:00 | 20 | 5
2022-05-12 21:00 | 21 | 5 | 1 | 2022-05-12 21:00 | 21 | 5
2022-05-12 22:00 | 22 | 5 | 1 | 2022-05-12 22:00 | 22 | 5
2022-05-12 23:00 | 23 | 5 | 1 | 2022-05-12 23:00 | 23 | 5
2022-05-13 | 0 | 6 | 1 | 2022-05-13 | 0 | 6
2022-05-13 01:00 | 1 | 6 | 1 | 2022-05-13 01:00 | 1 | 6
2022-05-13 02:00 | 2 | 6 | 1 | 2022-05-13 02:00 | 2 | 6
2022-05-13 03:00 | 3 | 6 | 1 | 2022-05-13 03:00 | 3 | 6
2022-05-13 04:00 | 4 | 6 | 1 | 2022-05-13 04:00 | 4 | 6
2022-05-13 05:00 | 5 | 6 | 1 | 2022-05-13 05:00 | 5 | 6
2022-05-13 06:00 | 6 | 6 | 1 | 2022-05-13 06:00 | 6 | 6
2022-05-13 07:00 | 7 | 6 | 1 | 2022-05-13 07:00 | 7 | 6
2022-05-13 08:00 | 8 | 6 | 1 | 2022-05-13 08:00 | 8 | 6
2022-05-13 09:00 | 9 | 6 | 1 | 2022-05-13 09:00 | 9 | 6
2022-05-13 10:00 | 10 | 6 | 1 | 2022-05-13 10:00 | 10 | 6
2022-05-13 11:00 | 11 | 6 | 1 | 2022-05-13 11:00 | 11 | 6
2022-05-13 12:00 | 12 | 6 | 1 | 2022-05-13 12:00 | 12 | 6
2022-05-13 13:00 | 13 | 6 | 1 | 2022-05-13 13:00 | 13 | 6
2022-05-13 14:00 | 14 | 6 | 1 | 2022-05-13 14:00 | 14 | 6
2022-05-13 15:00 | 15 | 6 | 1 | 2022-05-13 15:00 | 15 | 6
2022-05-13 16:00 | 16 | 6 | 1 | 2022-05-13 16:00 | 16 | 6
2022-05-13 17:00 | 17 | 6 | 1 | 2022-05-13 17:00 | 17 | 6
2022-05-13 18:00 | 18 | 6 | 1 | 2022-05-13 18:00 | 18 | 6
2022-05-13 19:00 | 19 | 6 | 1 | 2022-05-13 19:00 | 19 | 6
2022-05-13 20:00 | 20 | 6 | 1 | 2022-05-13 20:00 | 20 | 6
2022-05-13 21:00 | 21 | 6 | 1 | 2022-05-13 21:00 | 21 | 6
2022-05-13 22:00 | 22 | 6 | 1 | 2022-05-13 22:00 | 22 | 6
2022-05-13 23:00 | 23 | 6 | 1 | 2022-05-13 23:00 | 23 | 6
2022-05-14 | 0 | 7 | 1 | 2022-05-14 | 0 | 7
2022-05-14 01:00 | 1 | 7 | 1 | 2022-05-14 01:00 | 1 | 7
2022-05-14 02:00 | 2 | 7 | 1 | 2022-05-14 02:00 | 2 | 7
2022-05-14 03:00 | 3 | 7 | 1 | 2022-05-14 03:00 | 3 | 7
2022-05-14 04:00 | 4 | 7 | 1 | 2022-05-14 04:00 | 4 | 7
2022-05-14 05:00 | 5 | 7 | 1 | 2022-05-14 05:00 | 5 | 7
2022-05-14 06:00 | 6 | 7 | 1 | 2022-05-14 06:00 | 6 | 7
2022-05-14 07:00 | 7 | 7 | 1 | 2022-05-14 07:00 | 7 | 7
2022-05-14 08:00 | 8 | 7 | 1 | 2022-05-14 08:00 | 8 | 7
2022-05-14 09:00 | 9 | 7 | 1 | 2022-05-14 09:00 | 9 | 7
2022-05-14 10:00 | 10 | 7 | 1 | 2022-05-14 10:00 | 10 | 7
2022-05-14 11:00 | 11 | 7 | 1 | 2022-05-14 11:00 | 11 | 7
2022-05-14 12:00 | 12 | 7 | 1 | 2022-05-14 12:00 | 12 | 7
2022-05-14 13:00 | 13 | 7 | 1 | 2022-05-14 13:00 | 13 | 7
2022-05-14 14:00 | 14 | 7 | 1 | 2022-05-14 14:00 | 14 | 7
2022-05-14 15:00 | 15 | 7 | 1 | 2022-05-14 15:00 | 15 | 7
2022-05-14 16:00 | 16 | 7 | 1 | 2022-05-14 16:00 | 16 | 7
2022-05-14 17:00 | 17 | 7 | 1 | 2022-05-14 17:00 | 17 | 7
2022-05-14 18:00 | 18 | 7 | 1 | 2022-05-14 18:00 | 18 | 7
2022-05-14 19:00 | 19 | 7 | 1 | 2022-05-14 19:00 | 19 | 7
2022-05-14 20:00 | 20 | 7 | 1 | 2022-05-14 20:00 | 20 | 7
2022-05-14 21:00 | 21 | 7 | 1 | 2022-05-14 21:00 | 21 | 7
2022-05-14 22:00 | 22 | 7 | 1 | 2022-05-14 22:00 | 22 | 7
2022-05-14 23:00 | 23 | 7 | 1 | 2022-05-14 23:00 | 23 | 7
2022-05-15 | 0 | 1 | 1 | 2022-05-15 | 0 | 1
2022-05-15 01:00 | 1 | 1 | 1 | 2022-05-15 01:00 | 1 | 1
2022-05-15 02:00 | 2 | 1 | 1 | 2022-05-15 02:00 | 2 | 1
2022-05-15 03:00 | 3 | 1 | 1 | 2022-05-15 03:00 | 3 | 1
2022-05-15 04:00 | 4 | 1 | 1 | 2022-05-15 04:00 | 4 | 1
2022-05-15 05:00 | 5 | 1 | 1 | 2022-05-15 05:00 | 5 | 1
2022-05-15 06:00 | 6 | 1 | 1 | 2022-05-15 06:00 | 6 | 1
2022-05-15 07:00 | 7 | 1 | 1 | 2022-05-15 07:00 | 7 | 1
2022-05-15 08:00 | 8 | 1 | 1 | 2022-05-15 08:00 | 8 | 1
2022-05-15 09:00 | 9 | 1 | 1 | 2022-05-15 09:00 | 9 | 1
2022-05-15 10:00 | 10 | 1 | 1 | 2022-05-15 10:00 | 10 | 1
2022-05-15 11:00 | 11 | 1 | 1 | 2022-05-15 11:00 | 11 | 1
2022-05-15 12:00 | 12 | 1 | 1 | 2022-05-15 12:00 | 12 | 1
2022-05-15 13:00 | 13 | 1 | 1 | 2022-05-15 13:00 | 13 | 1
2022-05-15 14:00 | 14 | 1 | 1 | 2022-05-15 14:00 | 14 | 1
2022-05-15 15:00 | 15 | 1 | 1 | 2022-05-15 15:00 | 15 | 1
2022-05-15 16:00 | 16 | 1 | 1 | 2022-05-15 16:00 | 16 | 1
2022-05-15 17:00 | 17 | 1 | 1 | 2022-05-15 17:00 | 17 | 1
2022-05-15 18:00 | 18 | 1 | 1 | 2022-05-15 18:00 | 18 | 1
2022-05-15 19:00 | 19 | 1 | 1 | 2022-05-15 19:00 | 19 | 1
2022-05-15 20:00 | 20 | 1 | 1 | 2022-05-15 20:00 | 20 | 1
2022-05-15 21:00 | 21 | 1 | 1 | 2022-05-15 21:00 | 21 | 1
2022-05-15 22:00 | 22 | 1 | 1 | 2022-05-15 22:00 | 22 | 1
2022-05-15 23:00 | 23 | 1 | 1 | 2022-05-15 23:00 | 23 | 1
2022-05-16 | 0 | 2 | 1 | 2022-05-16 | 0 | 2
2022-05-16 01:00 | 1 | 2 | 1 | 2022-05-16 01:00 | 1 | 2
2022-05-16 02:00 | 2 | 2 | 1 | 2022-05-16 02:00 | 2 | 2
2022-05-16 03:00 | 3 | 2 | 1 | 2022-05-16 03:00 | 3 | 2
2022-05-16 04:00 | 4 | 2 | 1 | 2022-05-16 04:00 | 4 | 2
2022-05-16 05:00 | 5 | 2 | 1 | 2022-05-16 05:00 | 5 | 2
2022-05-16 06:00 | 6 | 2 | 1 | 2022-05-16 06:00 | 6 | 2
2022-05-16 07:00 | 7 | 2 | 1 | 2022-05-16 07:00 | 7 | 2
2022-05-16 08:00 | 8 | 2 | 1 | 2022-05-16 08:00 | 8 | 2
2022-05-16 09:00 | 9 | 2 | 1 | 2022-05-16 09:00 | 9 | 2
2022-05-16 10:00 | 10 | 2 | 1 | 2022-05-16 10:00 | 10 | 2
2022-05-16 11:00 | 11 | 2 | 1 | 2022-05-16 11:00 | 11 | 2
2022-05-16 12:00 | 12 | 2 | 1 | 2022-05-16 12:00 | 12 | 2
2022-05-16 13:00 | 13 | 2 | 1 | 2022-05-16 13:00 | 13 | 2
2022-05-16 14:00 | 14 | 2 | 1 | 2022-05-16 14:00 | 14 | 2
2022-05-16 15:00 | 15 | 2 | 1 | 2022-05-16 15:00 | 15 | 2
2022-05-16 16:00 | 16 | 2 | 1 | 2022-05-16 16:00 | 16 | 2
2022-05-16 17:00 | 17 | 2 | 1 | 2022-05-16 17:00 | 17 | 2
2022-05-16 18:00 | 18 | 2 | 1 | 2022-05-16 18:00 | 18 | 2
2022-05-16 19:00 | 19 | 2 | 1 | 2022-05-16 19:00 | 19 | 2
2022-05-16 20:00 | 20 | 2 | 1 | 2022-05-16 20:00 | 20 | 2
2022-05-16 21:00 | 21 | 2 | 1 | 2022-05-16 21:00 | 21 | 2
2022-05-16 22:00 | 22 | 2 | 1 | 2022-05-16 22:00 | 22 | 2
2022-05-16 23:00 | 23 | 2 | 1 | 2022-05-16 23:00 | 23 | 2
2022-05-17 | 0 | 3 | 1 | 2022-05-17 | 0 | 3
2022-05-17 01:00 | 1 | 3 | 1 | 2022-05-17 01:00 | 1 | 3
2022-05-17 02:00 | 2 | 3 | 1 | 2022-05-17 02:00 | 2 | 3
2022-05-17 03:00 | 3 | 3 | 1 | 2022-05-17 03:00 | 3 | 3
2022-05-17 04:00 | 4 | 3 | 1 | 2022-05-17 04:00 | 4 | 3
2022-05-17 05:00 | 5 | 3 | 1 | 2022-05-17 05:00 | 5 | 3
2022-05-17 06:00 | 6 | 3 | 1 | 2022-05-17 06:00 | 6 | 3
2022-05-17 07:00 | 7 | 3 | 1 | 2022-05-17 07:00 | 7 | 3
2022-05-17 08:00 | 8 | 3 | 1 | 2022-05-17 08:00 | 8 | 3
2022-05-17 09:00 | 9 | 3 | 1 | 2022-05-17 09:00 | 9 | 3
2022-05-17 10:00 | 10 | 3 | 1 | 2022-05-17 10:00 | 10 | 3
2022-05-17 11:00 | 11 | 3 | 1 | 2022-05-17 11:00 | 11 | 3
2022-05-17 12:00 | 12 | 3 | 1 | 2022-05-17 12:00 | 12 | 3
2022-05-17 13:00 | 13 | 3 | 1 | 2022-05-17 13:00 | 13 | 3
2022-05-17 14:00 | 14 | 3 | 1 | 2022-05-17 14:00 | 14 | 3
2022-05-17 15:00 | 15 | 3 | 1 | 2022-05-17 15:00 | 15 | 3
2022-05-17 16:00 | 16 | 3 | 1 | 2022-05-17 16:00 | 16 | 3
2022-05-17 17:00 | 17 | 3 | 1 | 2022-05-17 17:00 | 17 | 3
2022-05-17 18:00 | 18 | 3 | 1 | 2022-05-17 18:00 | 18 | 3
2022-05-17 19:00 | 19 | 3 | 1 | 2022-05-17 19:00 | 19 | 3
2022-05-17 20:00 | 20 | 3 | 1 | 2022-05-17 20:00 | 20 | 3
2022-05-17 21:00 | 21 | 3 | 1 | 2022-05-17 21:00 | 21 | 3
2022-05-17 22:00 | 22 | 3 | 1 | 2022-05-17 22:00 | 22 | 3
2022-05-17 23:00 | 23 | 3 | 1 | 2022-05-17 23:00 | 23 | 3
2022-05-18 | 0 | 4 | 1 | 2022-05-18 | 0 | 4
2022-05-18 01:00 | 1 | 4 | 1 | 2022-05-18 01:00 | 1 | 4
2022-05-18 02:00 | 2 | 4 | 1 | 2022-05-18 02:00 | 2 | 4
2022-05-18 03:00 | 3 | 4 | 1 | 2022-05-18 03:00 | 3 | 4
2022-05-18 04:00 | 4 | 4 | 1 | 2022-05-18 04:00 | 4 | 4
2022-05-18 05:00 | 5 | 4 | 1 | 2022-05-18 05:00 | 5 | 4
2022-05-18 06:00 | 6 | 4 | 1 | 2022-05-18 06:00 | 6 | 4
2022-05-18 07:00 | 7 | 4 | 1 | 2022-05-18 07:00 | 7 | 4
2022-05-18 08:00 | 8 | 4 | 1 | 2022-05-18 08:00 | 8 | 4
2022-05-18 09:00 | 9 | 4 | 1 | 2022-05-18 09:00 | 9 | 4
2022-05-18 10:00 | 10 | 4 | 1 | 2022-05-18 10:00 | 10 | 4
2022-05-18 11:00 | 11 | 4 | 1 | 2022-05-18 11:00 | 11 | 4
2022-05-18 12:00 | 12 | 4 | 1 | 2022-05-18 12:00 | 12 | 4
2022-05-18 13:00 | 13 | 4 | 1 | 2022-05-18 13:00 | 13 | 4
2022-05-18 14:00 | 14 | 4 | 1 | 2022-05-18 14:00 | 14 | 4
2022-05-18 15:00 | 15 | 4 | 1 | 2022-05-18 15:00 | 15 | 4
2022-05-18 16:00 | 16 | 4 | 1 | 2022-05-18 16:00 | 16 | 4
2022-05-18 17:00 | 17 | 4 | 1 | 2022-05-18 17:00 | 17 | 4
2022-05-18 18:00 | 18 | 4 | 1 | 2022-05-18 18:00 | 18 | 4
2022-05-18 19:00 | 19 | 4 | 1 | 2022-05-18 19:00 | 19 | 4
2022-05-18 20:00 | 20 | 4 | 1 | 2022-05-18 20:00 | 20 | 4
2022-05-18 21:00 | 21 | 4 | 1 | 2022-05-18 21:00 | 21 | 4
2022-05-18 22:00 | 22 | 4 | 1 | 2022-05-18 22:00 | 22 | 4
2022-05-18 23:00 | 23 | 4 | 1 | 2022-05-18 23:00 | 23 | 4
2022-05-19 | 0 | 5 | 1 | 2022-05-19 | 0 | 5
2022-05-19 01:00 | 1 | 5 | 1 | 2022-05-19 01:00 | 1 | 5
2022-05-19 02:00 | 2 | 5 | 1 | 2022-05-19 02:00 | 2 | 5
2022-05-19 03:00 | 3 | 5 | 1 | 2022-05-19 03:00 | 3 | 5
2022-05-19 04:00 | 4 | 5 | 1 | 2022-05-19 04:00 | 4 | 5
2022-05-19 05:00 | 5 | 5 | 1 | 2022-05-19 05:00 | 5 | 5
2022-05-19 06:00 | 6 | 5 | 1 | 2022-05-19 06:00 | 6 | 5
2022-05-19 07:00 | 7 | 5 | 1 | 2022-05-19 07:00 | 7 | 5
2022-05-19 08:00 | 8 | 5 | 1 | 2022-05-19 08:00 | 8 | 5
2022-05-19 09:00 | 9 | 5 | 1 | 2022-05-19 09:00 | 9 | 5
2022-05-19 10:00 | 10 | 5 | 1 | 2022-05-19 10:00 | 10 | 5
2022-05-19 11:00 | 11 | 5 | 1 | 2022-05-19 11:00 | 11 | 5
2022-05-19 12:00 | 12 | 5 | 1 | 2022-05-19 12:00 | 12 | 5
2022-05-19 13:00 | 13 | 5 | 1 | 2022-05-19 13:00 | 13 | 5
2022-05-19 14:00 | 14 | 5 | 1 | 2022-05-19 14:00 | 14 | 5
2022-05-19 15:00 | 15 | 5 | 1 | 2022-05-19 15:00 | 15 | 5
2022-05-19 16:00 | 16 | 5 | 1 | 2022-05-19 16:00 | 16 | 5
2022-05-19 17:00 | 17 | 5 | 1 | 2022-05-19 17:00 | 17 | 5
2022-05-19 18:00 | 18 | 5 | 1 | 2022-05-19 18:00 | 18 | 5
2022-05-19 19:00 | 19 | 5 | 1 | 2022-05-19 19:00 | 19 | 5
2022-05-19 20:00 | 20 | 5 | 1 | 2022-05-19 20:00 | 20 | 5
2022-05-19 21:00 | 21 | 5 | 1 | 2022-05-19 21:00 | 21 | 5
2022-05-19 22:00 | 22 | 5 | 1 | 2022-05-19 22:00 | 22 | 5
2022-05-19 23:00 | 23 | 5 | 1 | 2022-05-19 23:00 | 23 | 5
2022-05-20 | 0 | 6 | 1 | 2022-05-20 | 0 | 6
2022-05-20 01:00 | 1 | 6 | 1 | 2022-05-20 01:00 | 1 | 6
2022-05-20 02:00 | 2 | 6 | 1 | 2022-05-20 02:00 | 2 | 6
2022-05-20 03:00 | 3 | 6 | 1 | 2022-05-20 03:00 | 3 | 6
2022-05-20 04:00 | 4 | 6 | 1 | 2022-05-20 04:00 | 4 | 6
2022-05-20 05:00 | 5 | 6 | 1 | 2022-05-20 05:00 | 5 | 6
2022-05-20 06:00 | 6 | 6 | 1 | 2022-05-20 06:00 | 6 | 6
2022-05-20 07:00 | 7 | 6 | 1 | 2022-05-20 07:00 | 7 | 6
2022-05-20 08:00 | 8 | 6 | 1 | 2022-05-20 08:00 | 8 | 6
2022-05-20 09:00 | 9 | 6 | 1 | 2022-05-20 09:00 | 9 | 6
2022-05-20 10:00 | 10 | 6 | 1 | 2022-05-20 10:00 | 10 | 6
2022-05-20 11:00 | 11 | 6 | 1 | 2022-05-20 11:00 | 11 | 6
2022-05-20 12:00 | 12 | 6 | 1 | 2022-05-20 12:00 | 12 | 6
2022-05-20 13:00 | 13 | 6 | 1 | 2022-05-20 13:00 | 13 | 6
2022-05-20 14:00 | 14 | 6 | 1 | 2022-05-20 14:00 | 14 | 6
2022-05-20 15:00 | 15 | 6 | 1 | 2022-05-20 15:00 | 15 | 6
2022-05-20 16:00 | 16 | 6 | 1 | 2022-05-20 16:00 | 16 | 6
2022-05-20 17:00 | 17 | 6 | 1 | 2022-05-20 17:00 | 17 | 6
2022-05-20 18:00 | 18 | 6 | 1 | 2022-05-20 18:00 | 18 | 6
2022-05-20 19:00 | 19 | 6 | 1 | 2022-05-20 19:00 | 19 | 6
2022-05-20 20:00 | 20 | 6 | 1 | 2022-05-20 20:00 | 20 | 6
2022-05-20 21:00 | 21 | 6 | 1 | 2022-05-20 21:00 | 21 | 6
2022-05-20 22:00 | 22 | 6 | 1 | 2022-05-20 22:00 | 22 | 6
2022-05-20 23:00 | 23 | 6 | 1 | 2022-05-20 23:00 | 23 | 6
2022-05-21 | 0 | 7 | 1 | 2022-05-21 | 0 | 7
2022-05-21 01:00 | 1 | 7 | 1 | 2022-05-21 01:00 | 1 | 7
2022-05-21 02:00 | 2 | 7 | 1 | 2022-05-21 02:00 | 2 | 7
2022-05-21 03:00 | 3 | 7 | 1 | 2022-05-21 03:00 | 3 | 7
2022-05-21 04:00 | 4 | 7 | 1 | 2022-05-21 04:00 | 4 | 7
2022-05-21 05:00 | 5 | 7 | 1 | 2022-05-21 05:00 | 5 | 7
2022-05-21 06:00 | 6 | 7 | 1 | 2022-05-21 06:00 | 6 | 7
2022-05-21 07:00 | 7 | 7 | 1 | 2022-05-21 07:00 | 7 | 7
2022-05-21 08:00 | 8 | 7 | 1 | 2022-05-21 08:00 | 8 | 7
2022-05-21 09:00 | 9 | 7 | 1 | 2022-05-21 09:00 | 9 | 7
2022-05-21 10:00 | 10 | 7 | 1 | 2022-05-21 10:00 | 10 | 7
2022-05-21 11:00 | 11 | 7 | 1 | 2022-05-21 11:00 | 11 | 7
2022-05-21 12:00 | 12 | 7 | 1 | 2022-05-21 12:00 | 12 | 7
2022-05-21 13:00 | 13 | 7 | 1 | 2022-05-21 13:00 | 13 | 7
2022-05-21 14:00 | 14 | 7 | 1 | 2022-05-21 14:00 | 14 | 7
2022-05-21 15:00 | 15 | 7 | 1 | 2022-05-21 15:00 | 15 | 7
2022-05-21 16:00 | 16 | 7 | 1 | 2022-05-21 16:00 | 16 | 7
2022-05-21 17:00 | 17 | 7 | 1 | 2022-05-21 17:00 | 17 | 7
2022-05-21 18:00 | 18 | 7 | 1 | 2022-05-21 18:00 | 18 | 7
2022-05-21 19:00 | 19 | 7 | 1 | 2022-05-21 19:00 | 19 | 7
2022-05-21 20:00 | 20 | 7 | 1 | 2022-05-21 20:00 | 20 | 7
2022-05-21 21:00 | 21 | 7 | 1 | 2022-05-21 21:00 | 21 | 7
2022-05-21 22:00 | 22 | 7 | 1 | 2022-05-21 22:00 | 22 | 7
2022-05-21 23:00 | 23 | 7 | 1 | 2022-05-21 23:00 | 23 | 7
2022-05-22 | 0 | 1 | 1 | 2022-05-22 | 0 | 1
2022-05-22 01:00 | 1 | 1 | 1 | 2022-05-22 01:00 | 1 | 1
2022-05-22 02:00 | 2 | 1 | 1 | 2022-05-22 02:00 | 2 | 1
2022-05-22 03:00 | 3 | 1 | 1 | 2022-05-22 03:00 | 3 | 1
2022-05-22 04:00 | 4 | 1 | 1 | 2022-05-22 04:00 | 4 | 1
2022-05-22 05:00 | 5 | 1 | 1 | 2022-05-22 05:00 | 5 | 1
2022-05-22 06:00 | 6 | 1 | 1 | 2022-05-22 06:00 | 6 | 1
2022-05-22 07:00 | 7 | 1 | 1 | 2022-05-22 07:00 | 7 | 1
2022-05-22 08:00 | 8 | 1 | 1 | 2022-05-22 08:00 | 8 | 1
2022-05-22 09:00 | 9 | 1 | 1 | 2022-05-22 09:00 | 9 | 1
2022-05-22 10:00 | 10 | 1 | 1 | 2022-05-22 10:00 | 10 | 1
2022-05-22 11:00 | 11 | 1 | 1 | 2022-05-22 11:00 | 11 | 1
2022-05-22 12:00 | 12 | 1 | 1 | 2022-05-22 12:00 | 12 | 1
2022-05-22 13:00 | 13 | 1 | 1 | 2022-05-22 13:00 | 13 | 1
2022-05-22 14:00 | 14 | 1 | 1 | 2022-05-22 14:00 | 14 | 1
2022-05-22 15:00 | 15 | 1 | 1 | 2022-05-22 15:00 | 15 | 1
2022-05-22 16:00 | 16 | 1 | 1 | 2022-05-22 16:00 | 16 | 1
2022-05-22 17:00 | 17 | 1 | 1 | 2022-05-22 17:00 | 17 | 1
2022-05-22 18:00 | 18 | 1 | 1 | 2022-05-22 18:00 | 18 | 1
2022-05-22 19:00 | 19 | 1 | 1 | 2022-05-22 19:00 | 19 | 1
2022-05-22 20:00 | 20 | 1 | 1 | 2022-05-22 20:00 | 20 | 1
2022-05-22 21:00 | 21 | 1 | 1 | 2022-05-22 21:00 | 21 | 1
2022-05-22 22:00 | 22 | 1 | 1 | 2022-05-22 22:00 | 22 | 1
2022-05-22 23:00 | 23 | 1 | 1 | 2022-05-22 23:00 | 23 | 1
2022-05-23 | 0 | 2 | 1 | 2022-05-23 | 0 | 2
2022-05-23 01:00 | 1 | 2 | 1 | 2022-05-23 01:00 | 1 | 2
2022-05-23 02:00 | 2 | 2 | 1 | 2022-05-23 02:00 | 2 | 2
2022-05-23 03:00 | 3 | 2 | 1 | 2022-05-23 03:00 | 3 | 2
2022-05-23 04:00 | 4 | 2 | 1 | 2022-05-23 04:00 | 4 | 2
2022-05-23 05:00 | 5 | 2 | 1 | 2022-05-23 05:00 | 5 | 2
2022-05-23 06:00 | 6 | 2 | 1 | 2022-05-23 06:00 | 6 | 2
2022-05-23 07:00 | 7 | 2 | 1 | 2022-05-23 07:00 | 7 | 2
2022-05-23 08:00 | 8 | 2 | 1 | 2022-05-23 08:00 | 8 | 2
2022-05-23 09:00 | 9 | 2 | 1 | 2022-05-23 09:00 | 9 | 2
2022-05-23 10:00 | 10 | 2 | 1 | 2022-05-23 10:00 | 10 | 2
2022-05-23 11:00 | 11 | 2 | 1 | 2022-05-23 11:00 | 11 | 2
2022-05-23 12:00 | 12 | 2 | 1 | 2022-05-23 12:00 | 12 | 2
2022-05-23 13:00 | 13 | 2 | 1 | 2022-05-23 13:00 | 13 | 2
2022-05-23 14:00 | 14 | 2 | 1 | 2022-05-23 14:00 | 14 | 2
2022-05-23 15:00 | 15 | 2 | 1 | 2022-05-23 15:00 | 15 | 2
2022-05-23 16:00 | 16 | 2 | 1 | 2022-05-23 16:00 | 16 | 2
2022-05-23 17:00 | 17 | 2 | 1 | 2022-05-23 17:00 | 17 | 2
2022-05-23 18:00 | 18 | 2 | 1 | 2022-05-23 18:00 | 18 | 2
2022-05-23 19:00 | 19 | 2 | 1 | 2022-05-23 19:00 | 19 | 2
2022-05-23 20:00 | 20 | 2 | 1 | 2022-05-23 20:00 | 20 | 2
2022-05-23 21:00 | 21 | 2 | 1 | 2022-05-23 21:00 | 21 | 2
2022-05-23 22:00 | 22 | 2 | 1 | 2022-05-23 22:00 | 22 | 2
2022-05-23 23:00 | 23 | 2 | 1 | 2022-05-23 23:00 | 23 | 2
2022-05-24 | 0 | 3 | 1 | 2022-05-24 | 0 | 3
2022-05-24 01:00 | 1 | 3 | 1 | 2022-05-24 01:00 | 1 | 3
2022-05-24 02:00 | 2 | 3 | 1 | 2022-05-24 02:00 | 2 | 3
2022-05-24 03:00 | 3 | 3 | 1 | 2022-05-24 03:00 | 3 | 3
2022-05-24 04:00 | 4 | 3 | 1 | 2022-05-24 04:00 | 4 | 3
2022-05-24 05:00 | 5 | 3 | 1 | 2022-05-24 05:00 | 5 | 3
2022-05-24 06:00 | 6 | 3 | 1 | 2022-05-24 06:00 | 6 | 3
2022-05-24 07:00 | 7 | 3 | 1 | 2022-05-24 07:00 | 7 | 3
2022-05-24 08:00 | 8 | 3 | 1 | 2022-05-24 08:00 | 8 | 3
2022-05-24 09:00 | 9 | 3 | 1 | 2022-05-24 09:00 | 9 | 3
2022-05-24 10:00 | 10 | 3 | 1 | 2022-05-24 10:00 | 10 | 3
2022-05-24 11:00 | 11 | 3 | 1 | 2022-05-24 11:00 | 11 | 3
2022-05-24 12:00 | 12 | 3 | 1 | 2022-05-24 12:00 | 12 | 3
2022-05-24 13:00 | 13 | 3 | 1 | 2022-05-24 13:00 | 13 | 3
2022-05-24 14:00 | 14 | 3 | 1 | 2022-05-24 14:00 | 14 | 3
2022-05-24 15:00 | 15 | 3 | 1 | 2022-05-24 15:00 | 15 | 3
2022-05-24 16:00 | 16 | 3 | 1 | 2022-05-24 16:00 | 16 | 3
2022-05-24 17:00 | 17 | 3 | 1 | 2022-05-24 17:00 | 17 | 3
2022-05-24 18:00 | 18 | 3 | 1 | 2022-05-24 18:00 | 18 | 3
2022-05-24 19:00 | 19 | 3 | 1 | 2022-05-24 19:00 | 19 | 3
2022-05-24 20:00 | 20 | 3 | 1 | 2022-05-24 20:00 | 20 | 3
2022-05-24 21:00 | 21 | 3 | 1 | 2022-05-24 21:00 | 21 | 3
2022-05-24 22:00 | 22 | 3 | 1 | 2022-05-24 22:00 | 22 | 3
2022-05-24 23:00 | 23 | 3 | 1 | 2022-05-24 23:00 | 23 | 3
2022-05-25 | 0 | 4 | 1 | 2022-05-25 | 0 | 4
2022-05-25 01:00 | 1 | 4 | 1 | 2022-05-25 01:00 | 1 | 4
2022-05-25 02:00 | 2 | 4 | 1 | 2022-05-25 02:00 | 2 | 4
2022-05-25 03:00 | 3 | 4 | 1 | 2022-05-25 03:00 | 3 | 4
2022-05-25 04:00 | 4 | 4 | 1 | 2022-05-25 04:00 | 4 | 4
2022-05-25 05:00 | 5 | 4 | 1 | 2022-05-25 05:00 | 5 | 4
2022-05-25 06:00 | 6 | 4 | 1 | 2022-05-25 06:00 | 6 | 4
2022-05-25 07:00 | 7 | 4 | 1 | 2022-05-25 07:00 | 7 | 4
2022-05-25 08:00 | 8 | 4 | 1 | 2022-05-25 08:00 | 8 | 4
2022-05-25 09:00 | 9 | 4 | 1 | 2022-05-25 09:00 | 9 | 4
2022-05-25 10:00 | 10 | 4 | 1 | 2022-05-25 10:00 | 10 | 4
2022-05-25 11:00 | 11 | 4 | 1 | 2022-05-25 11:00 | 11 | 4
2022-05-25 12:00 | 12 | 4 | 1 | 2022-05-25 12:00 | 12 | 4
2022-05-25 13:00 | 13 | 4 | 1 | 2022-05-25 13:00 | 13 | 4
2022-05-25 14:00 | 14 | 4 | 1 | 2022-05-25 14:00 | 14 | 4
2022-05-25 15:00 | 15 | 4 | 1 | 2022-05-25 15:00 | 15 | 4
2022-05-25 16:00 | 16 | 4 | 1 | 2022-05-25 16:00 | 16 | 4
2022-05-25 17:00 | 17 | 4 | 1 | 2022-05-25 17:00 | 17 | 4
2022-05-25 18:00 | 18 | 4 | 1 | 2022-05-25 18:00 | 18 | 4
2022-05-25 19:00 | 19 | 4 | 1 | 2022-05-25 19:00 | 19 | 4
2022-05-25 20:00 | 20 | 4 | 1 | 2022-05-25 20:00 | 20 | 4
2022-05-25 21:00 | 21 | 4 | 1 | 2022-05-25 21:00 | 21 | 4
2022-05-25 22:00 | 22 | 4 | 1 | 2022-05-25 22:00 | 22 | 4
2022-05-25 23:00 | 23 | 4 | 1 | 2022-05-25 23:00 | 23 | 4
2022-05-26 | 0 | 5 | 1 | 2022-05-26 | 0 | 5
2022-05-26 01:00 | 1 | 5 | 1 | 2022-05-26 01:00 | 1 | 5
2022-05-26 02:00 | 2 | 5 | 1 | 2022-05-26 02:00 | 2 | 5
2022-05-26 03:00 | 3 | 5 | 1 | 2022-05-26 03:00 | 3 | 5
2022-05-26 04:00 | 4 | 5 | 1 | 2022-05-26 04:00 | 4 | 5
2022-05-26 05:00 | 5 | 5 | 1 | 2022-05-26 05:00 | 5 | 5
2022-05-26 06:00 | 6 | 5 | 1 | 2022-05-26 06:00 | 6 | 5
2022-05-26 07:00 | 7 | 5 | 1 | 2022-05-26 07:00 | 7 | 5
2022-05-26 08:00 | 8 | 5 | 1 | 2022-05-26 08:00 | 8 | 5
2022-05-26 09:00 | 9 | 5 | 1 | 2022-05-26 09:00 | 9 | 5
2022-05-26 10:00 | 10 | 5 | 1 | 2022-05-26 10:00 | 10 | 5
2022-05-26 11:00 | 11 | 5 | 1 | 2022-05-26 11:00 | 11 | 5
2022-05-26 12:00 | 12 | 5 | 1 | 2022-05-26 12:00 | 12 | 5
2022-05-26 13:00 | 13 | 5 | 1 | 2022-05-26 13:00 | 13 | 5
2022-05-26 14:00 | 14 | 5 | 1 | 2022-05-26 14:00 | 14 | 5
2022-05-26 15:00 | 15 | 5 | 1 | 2022-05-26 15:00 | 15 | 5
2022-05-26 16:00 | 16 | 5 | 1 | 2022-05-26 16:00 | 16 | 5
2022-05-26 17:00 | 17 | 5 | 1 | 2022-05-26 17:00 | 17 | 5
2022-05-26 18:00 | 18 | 5 | 1 | 2022-05-26 18:00 | 18 | 5
2022-05-26 19:00 | 19 | 5 | 1 | 2022-05-26 19:00 | 19 | 5
2022-05-26 20:00 | 20 | 5 | 1 | 2022-05-26 20:00 | 20 | 5
2022-05-26 21:00 | 21 | 5 | 1 | 2022-05-26 21:00 | 21 | 5
2022-05-26 22:00 | 22 | 5 | 1 | 2022-05-26 22:00 | 22 | 5
2022-05-26 23:00 | 23 | 5 | 1 | 2022-05-26 23:00 | 23 | 5
2022-05-27 | 0 | 6 | 1 | 2022-05-27 | 0 | 6
2022-05-27 01:00 | 1 | 6 | 1 | 2022-05-27 01:00 | 1 | 6
2022-05-27 02:00 | 2 | 6 | 1 | 2022-05-27 02:00 | 2 | 6
2022-05-27 03:00 | 3 | 6 | 1 | 2022-05-27 03:00 | 3 | 6
2022-05-27 04:00 | 4 | 6 | 1 | 2022-05-27 04:00 | 4 | 6
2022-05-27 05:00 | 5 | 6 | 1 | 2022-05-27 05:00 | 5 | 6
2022-05-27 06:00 | 6 | 6 | 1 | 2022-05-27 06:00 | 6 | 6
2022-05-27 07:00 | 7 | 6 | 1 | 2022-05-27 07:00 | 7 | 6
2022-05-27 08:00 | 8 | 6 | 1 | 2022-05-27 08:00 | 8 | 6
2022-05-27 09:00 | 9 | 6 | 1 | 2022-05-27 09:00 | 9 | 6
2022-05-27 10:00 | 10 | 6 | 1 | 2022-05-27 10:00 | 10 | 6
2022-05-27 11:00 | 11 | 6 | 1 | 2022-05-27 11:00 | 11 | 6
2022-05-27 12:00 | 12 | 6 | 1 | 2022-05-27 12:00 | 12 | 6
2022-05-27 13:00 | 13 | 6 | 1 | 2022-05-27 13:00 | 13 | 6
2022-05-27 14:00 | 14 | 6 | 1 | 2022-05-27 14:00 | 14 | 6
2022-05-27 15:00 | 15 | 6 | 1 | 2022-05-27 15:00 | 15 | 6
2022-05-27 16:00 | 16 | 6 | 1 | 2022-05-27 16:00 | 16 | 6
2022-05-27 17:00 | 17 | 6 | 1 | 2022-05-27 17:00 | 17 | 6
2022-05-27 18:00 | 18 | 6 | 1 | 2022-05-27 18:00 | 18 | 6
2022-05-27 19:00 | 19 | 6 | 1 | 2022-05-27 19:00 | 19 | 6
2022-05-27 20:00 | 20 | 6 | 1 | 2022-05-27 20:00 | 20 | 6
2022-05-27 21:00 | 21 | 6 | 1 | 2022-05-27 21:00 | 21 | 6
2022-05-27 22:00 | 22 | 6 | 1 | 2022-05-27 22:00 | 22 | 6
2022-05-27 23:00 | 23 | 6 | 1 | 2022-05-27 23:00 | 23 | 6
2022-05-28 | 0 | 7 | 1 | 2022-05-28 | 0 | 7
2022-05-28 01:00 | 1 | 7 | 1 | 2022-05-28 01:00 | 1 | 7
2022-05-28 02:00 | 2 | 7 | 1 | 2022-05-28 02:00 | 2 | 7
2022-05-28 03:00 | 3 | 7 | 1 | 2022-05-28 03:00 | 3 | 7
2022-05-28 04:00 | 4 | 7 | 1 | 2022-05-28 04:00 | 4 | 7
2022-05-28 05:00 | 5 | 7 | 1 | 2022-05-28 05:00 | 5 | 7
2022-05-28 06:00 | 6 | 7 | 1 | 2022-05-28 06:00 | 6 | 7
2022-05-28 07:00 | 7 | 7 | 1 | 2022-05-28 07:00 | 7 | 7
2022-05-28 08:00 | 8 | 7 | 1 | 2022-05-28 08:00 | 8 | 7
2022-05-28 09:00 | 9 | 7 | 1 | 2022-05-28 09:00 | 9 | 7
2022-05-28 10:00 | 10 | 7 | 1 | 2022-05-28 10:00 | 10 | 7
2022-05-28 11:00 | 11 | 7 | 1 | 2022-05-28 11:00 | 11 | 7
2022-05-28 12:00 | 12 | 7 | 1 | 2022-05-28 12:00 | 12 | 7
2022-05-28 13:00 | 13 | 7 | 1 | 2022-05-28 13:00 | 13 | 7
2022-05-28 14:00 | 14 | 7 | 1 | 2022-05-28 14:00 | 14 | 7
2022-05-28 15:00 | 15 | 7 | 1 | 2022-05-28 15:00 | 15 | 7
2022-05-28 16:00 | 16 | 7 | 1 | 2022-05-28 16:00 | 16 | 7
2022-05-28 17:00 | 17 | 7 | 1 | 2022-05-28 17:00 | 17 | 7
2022-05-28 18:00 | 18 | 7 | 1 | 2022-05-28 18:00 | 18 | 7
2022-05-28 19:00 | 19 | 7 | 1 | 2022-05-28 19:00 | 19 | 7
2022-05-28 20:00 | 20 | 7 | 1 | 2022-05-28 20:00 | 20 | 7
2022-05-28 21:00 | 21 | 7 | 1 | 2022-05-28 21:00 | 21 | 7
2022-05-28 22:00 | 22 | 7 | 1 | 2022-05-28 22:00 | 22 | 7
2022-05-28 23:00 | 23 | 7 | 1 | 2022-05-28 23:00 | 23 | 7
2022-05-29 | 0 | 1 | 1 | 2022-05-29 | 0 | 1
2022-05-29 01:00 | 1 | 1 | 1 | 2022-05-29 01:00 | 1 | 1
2022-05-29 02:00 | 2 | 1 | 1 | 2022-05-29 02:00 | 2 | 1
2022-05-29 03:00 | 3 | 1 | 1 | 2022-05-29 03:00 | 3 | 1
2022-05-29 04:00 | 4 | 1 | 1 | 2022-05-29 04:00 | 4 | 1
2022-05-29 05:00 | 5 | 1 | 1 | 2022-05-29 05:00 | 5 | 1
2022-05-29 06:00 | 6 | 1 | 1 | 2022-05-29 06:00 | 6 | 1
2022-05-29 07:00 | 7 | 1 | 1 | 2022-05-29 07:00 | 7 | 1
2022-05-29 08:00 | 8 | 1 | 1 | 2022-05-29 08:00 | 8 | 1
2022-05-29 09:00 | 9 | 1 | 1 | 2022-05-29 09:00 | 9 | 1
2022-05-29 10:00 | 10 | 1 | 1 | 2022-05-29 10:00 | 10 | 1
2022-05-29 11:00 | 11 | 1 | 1 | 2022-05-29 11:00 | 11 | 1
2022-05-29 12:00 | 12 | 1 | 1 | 2022-05-29 12:00 | 12 | 1
2022-05-29 13:00 | 13 | 1 | 1 | 2022-05-29 13:00 | 13 | 1
2022-05-29 14:00 | 14 | 1 | 1 | 2022-05-29 14:00 | 14 | 1
2022-05-29 15:00 | 15 | 1 | 1 | 2022-05-29 15:00 | 15 | 1
2022-05-29 16:00 | 16 | 1 | 1 | 2022-05-29 16:00 | 16 | 1
2022-05-29 17:00 | 17 | 1 | 1 | 2022-05-29 17:00 | 17 | 1
2022-05-29 18:00 | 18 | 1 | 1 | 2022-05-29 18:00 | 18 | 1
2022-05-29 19:00 | 19 | 1 | 1 | 2022-05-29 19:00 | 19 | 1
2022-05-29 20:00 | 20 | 1 | 1 | 2022-05-29 20:00 | 20 | 1
2022-05-29 21:00 | 21 | 1 | 1 | 2022-05-29 21:00 | 21 | 1
2022-05-29 22:00 | 22 | 1 | 1 | 2022-05-29 22:00 | 22 | 1
2022-05-29 23:00 | 23 | 1 | 1 | 2022-05-29 23:00 | 23 | 1
2022-05-30 | 0 | 2 | 1 | 2022-05-30 | 0 | 2
2022-05-30 01:00 | 1 | 2 | 1 | 2022-05-30 01:00 | 1 | 2
2022-05-30 02:00 | 2 | 2 | 1 | 2022-05-30 02:00 | 2 | 2
2022-05-30 03:00 | 3 | 2 | 1 | 2022-05-30 03:00 | 3 | 2
2022-05-30 04:00 | 4 | 2 | 1 | 2022-05-30 04:00 | 4 | 2
2022-05-30 05:00 | 5 | 2 | 1 | 2022-05-30 05:00 | 5 | 2
2022-05-30 06:00 | 6 | 2 | 1 | 2022-05-30 06:00 | 6 | 2
2022-05-30 07:00 | 7 | 2 | 1 | 2022-05-30 07:00 | 7 | 2
2022-05-30 08:00 | 8 | 2 | 1 | 2022-05-30 08:00 | 8 | 2
2022-05-30 09:00 | 9 | 2 | 1 | 2022-05-30 09:00 | 9 | 2
2022-05-30 10:00 | 10 | 2 | 1 | 2022-05-30 10:00 | 10 | 2
2022-05-30 11:00 | 11 | 2 | 1 | 2022-05-30 11:00 | 11 | 2
2022-05-30 12:00 | 12 | 2 | 1 | 2022-05-30 12:00 | 12 | 2
2022-05-30 13:00 | 13 | 2 | 1 | 2022-05-30 13:00 | 13 | 2
2022-05-30 14:00 | 14 | 2 | 1 | 2022-05-30 14:00 | 14 | 2
2022-05-30 15:00 | 15 | 2 | 1 | 2022-05-30 15:00 | 15 | 2
2022-05-30 16:00 | 16 | 2 | 1 | 2022-05-30 16:00 | 16 | 2
2022-05-30 17:00 | 17 | 2 | 1 | 2022-05-30 17:00 | 17 | 2
2022-05-30 18:00 | 18 | 2 | 1 | 2022-05-30 18:00 | 18 | 2
2022-05-30 19:00 | 19 | 2 | 1 | 2022-05-30 19:00 | 19 | 2
2022-05-30 20:00 | 20 | 2 | 1 | 2022-05-30 20:00 | 20 | 2
2022-05-30 21:00 | 21 | 2 | 1 | 2022-05-30 21:00 | 21 | 2
2022-05-30 22:00 | 22 | 2 | 1 | 2022-05-30 22:00 | 22 | 2
2022-05-30 23:00 | 23 | 2 | 1 | 2022-05-30 23:00 | 23 | 2
2022-05-31 | 0 | 3 | 1 | 2022-05-31 | 0 | 3
2022-05-31 01:00 | 1 | 3 | 1 | 2022-05-31 01:00 | 1 | 3
2022-05-31 02:00 | 2 | 3 | 1 | 2022-05-31 02:00 | 2 | 3
2022-05-31 03:00 | 3 | 3 | 1 | 2022-05-31 03:00 | 3 | 3
2022-05-31 04:00 | 4 | 3 | 1 | 2022-05-31 04:00 | 4 | 3
2022-05-31 05:00 | 5 | 3 | 1 | 2022-05-31 05:00 | 5 | 3
2022-05-31 06:00 | 6 | 3 | 1 | 2022-05-31 06:00 | 6 | 3
2022-05-31 07:00 | 7 | 3 | 1 | 2022-05-31 07:00 | 7 | 3
2022-05-31 08:00 | 8 | 3 | 1 | 2022-05-31 08:00 | 8 | 3
2022-05-31 09:00 | 9 | 3 | 1 | 2022-05-31 09:00 | 9 | 3
2022-05-31 10:00 | 10 | 3 | 1 | 2022-05-31 10:00 | 10 | 3
2022-05-31 11:00 | 11 | 3 | 1 | 2022-05-31 11:00 | 11 | 3
2022-05-31 12:00 | 12 | 3 | 1 | 2022-05-31 12:00 | 12 | 3
2022-05-31 13:00 | 13 | 3 | 1 | 2022-05-31 13:00 | 13 | 3
2022-05-31 14:00 | 14 | 3 | 1 | 2022-05-31 14:00 | 14 | 3
2022-05-31 15:00 | 15 | 3 | 1 | 2022-05-31 15:00 | 15 | 3
2022-05-31 16:00 | 16 | 3 | 1 | 2022-05-31 16:00 | 16 | 3
2022-05-31 17:00 | 17 | 3 | 1 | 2022-05-31 17:00 | 17 | 3
2022-05-31 18:00 | 18 | 3 | 1 | 2022-05-31 18:00 | 18 | 3
2022-05-31 19:00 | 19 | 3 | 1 | 2022-05-31 19:00 | 19 | 3
2022-05-31 20:00 | 20 | 3 | 1 | 2022-05-31 20:00 | 20 | 3
2022-05-31 21:00 | 21 | 3 | 1 | 2022-05-31 21:00 | 21 | 3
2022-05-31 22:00 | 22 | 3 | 1 | 2022-05-31 22:00 | 22 | 3
2022-05-31 23:00 | 23 | 3 | 1 | 2022-05-31 23:00 | 23 | 3
2022-06-01 | 0 | 4 | 1 | 2022-06-01 | 0 | 4
2022-06-01 01:00 | 1 | 4 | 1 | 2022-06-01 01:00 | 1 | 4
2022-06-01 02:00 | 2 | 4 | 1 | 2022-06-01 02:00 | 2 | 4
2022-06-01 03:00 | 3 | 4 | 1 | 2022-06-01 03:00 | 3 | 4
2022-06-01 04:00 | 4 | 4 | 1 | 2022-06-01 04:00 | 4 | 4
2022-06-01 05:00 | 5 | 4 | 1 | 2022-06-01 05:00 | 5 | 4
2022-06-01 06:00 | 6 | 4 | 1 | 2022-06-01 06:00 | 6 | 4
2022-06-01 07:00 | 7 | 4 | 1 | 2022-06-01 07:00 | 7 | 4
2022-06-01 08:00 | 8 | 4 | 1 | 2022-06-01 08:00 | 8 | 4
2022-06-01 09:00 | 9 | 4 | 1 | 2022-06-01 09:00 | 9 | 4
2022-06-01 10:00 | 10 | 4 | 1 | 2022-06-01 10:00 | 10 | 4
2022-06-01 11:00 | 11 | 4 | 1 | 2022-06-01 11:00 | 11 | 4
2022-06-01 12:00 | 12 | 4 | 1 | 2022-06-01 12:00 | 12 | 4
2022-06-01 13:00 | 13 | 4 | 1 | 2022-06-01 13:00 | 13 | 4
2022-06-01 14:00 | 14 | 4 | 1 | 2022-06-01 14:00 | 14 | 4
2022-06-01 15:00 | 15 | 4 | 1 | 2022-06-01 15:00 | 15 | 4
2022-06-01 16:00 | 16 | 4 | 1 | 2022-06-01 16:00 | 16 | 4
2022-06-01 17:00 | 17 | 4 | 1 | 2022-06-01 17:00 | 17 | 4
2022-06-01 18:00 | 18 | 4 | 1 | 2022-06-01 18:00 | 18 | 4
2022-06-01 19:00 | 19 | 4 | 1 | 2022-06-01 19:00 | 19 | 4
2022-06-01 20:00 | 20 | 4 | 1 | 2022-06-01 20:00 | 20 | 4
2022-06-01 21:00 | 21 | 4 | 1 | 2022-06-01 21:00 | 21 | 4
2022-06-01 22:00 | 22 | 4 | 1 | 2022-06-01 22:00 | 22 | 4
2022-06-01 23:00 | 23 | 4 | 1 | 2022-06-01 23:00 | 23 | 4
2022-06-02 | 0 | 5 | 1 | 2022-06-02 | 0 | 5
2022-06-02 01:00 | 1 | 5 | 1 | 2022-06-02 01:00 | 1 | 5
2022-06-02 02:00 | 2 | 5 | 1 | 2022-06-02 02:00 | 2 | 5
2022-06-02 03:00 | 3 | 5 | 1 | 2022-06-02 03:00 | 3 | 5
2022-06-02 04:00 | 4 | 5 | 1 | 2022-06-02 04:00 | 4 | 5
2022-06-02 05:00 | 5 | 5 | 1 | 2022-06-02 05:00 | 5 | 5
2022-06-02 06:00 | 6 | 5 | 1 | 2022-06-02 06:00 | 6 | 5
2022-06-02 07:00 | 7 | 5 | 1 | 2022-06-02 07:00 | 7 | 5
2022-06-02 08:00 | 8 | 5 | 1 | 2022-06-02 08:00 | 8 | 5
2022-06-02 09:00 | 9 | 5 | 1 | 2022-06-02 09:00 | 9 | 5
2022-06-02 10:00 | 10 | 5 | 1 | 2022-06-02 10:00 | 10 | 5
2022-06-02 11:00 | 11 | 5 | 1 | 2022-06-02 11:00 | 11 | 5
2022-06-02 12:00 | 12 | 5 | 1 | 2022-06-02 12:00 | 12 | 5
2022-06-02 13:00 | 13 | 5 | 1 | 2022-06-02 13:00 | 13 | 5
2022-06-02 14:00 | 14 | 5 | 1 | 2022-06-02 14:00 | 14 | 5
2022-06-02 15:00 | 15 | 5 | 1 | 2022-06-02 15:00 | 15 | 5
2022-06-02 16:00 | 16 | 5 | 1 | 2022-06-02 16:00 | 16 | 5
2022-06-02 17:00 | 17 | 5 | 1 | 2022-06-02 17:00 | 17 | 5
2022-06-02 18:00 | 18 | 5 | 1 | 2022-06-02 18:00 | 18 | 5
2022-06-02 19:00 | 19 | 5 | 1 | 2022-06-02 19:00 | 19 | 5
2022-06-02 20:00 | 20 | 5 | 1 | 2022-06-02 20:00 | 20 | 5
2022-06-02 21:00 | 21 | 5 | 1 | 2022-06-02 21:00 | 21 | 5
2022-06-02 22:00 | 22 | 5 | 1 | 2022-06-02 22:00 | 22 | 5
2022-06-02 23:00 | 23 | 5 | 1 | 2022-06-02 23:00 | 23 | 5
2022-06-03 | 0 | 6 | 1 | 2022-06-03 | 0 | 6
2022-06-03 01:00 | 1 | 6 | 1 | 2022-06-03 01:00 | 1 | 6
2022-06-03 02:00 | 2 | 6 | 1 | 2022-06-03 02:00 | 2 | 6
2022-06-03 03:00 | 3 | 6 | 1 | 2022-06-03 03:00 | 3 | 6
2022-06-03 04:00 | 4 | 6 | 1 | 2022-06-03 04:00 | 4 | 6
2022-06-03 05:00 | 5 | 6 | 1 | 2022-06-03 05:00 | 5 | 6
2022-06-03 06:00 | 6 | 6 | 1 | 2022-06-03 06:00 | 6 | 6
2022-06-03 07:00 | 7 | 6 | 1 | 2022-06-03 07:00 | 7 | 6
2022-06-03 08:00 | 8 | 6 | 1 | 2022-06-03 08:00 | 8 | 6
2022-06-03 09:00 | 9 | 6 | 1 | 2022-06-03 09:00 | 9 | 6
2022-06-03 10:00 | 10 | 6 | 1 | 2022-06-03 10:00 | 10 | 6
2022-06-03 11:00 | 11 | 6 | 1 | 2022-06-03 11:00 | 11 | 6
2022-06-03 12:00 | 12 | 6 | 1 | 2022-06-03 12:00 | 12 | 6
2022-06-03 13:00 | 13 | 6 | 1 | 2022-06-03 13:00 | 13 | 6
2022-06-03 14:00 | 14 | 6 | 1 | 2022-06-03 14:00 | 14 | 6
2022-06-03 15:00 | 15 | 6 | 1 | 2022-06-03 15:00 | 15 | 6
2022-06-03 16:00 | 16 | 6 | 1 | 2022-06-03 16:00 | 16 | 6
2022-06-03 17:00 | 17 | 6 | 1 | 2022-06-03 17:00 | 17 | 6
2022-06-03 18:00 | 18 | 6 | 1 | 2022-06-03 18:00 | 18 | 6
2022-06-03 19:00 | 19 | 6 | 1 | 2022-06-03 19:00 | 19 | 6
2022-06-03 20:00 | 20 | 6 | 1 | 2022-06-03 20:00 | 20 | 6
2022-06-03 21:00 | 21 | 6 | 1 | 2022-06-03 21:00 | 21 | 6
2022-06-03 22:00 | 22 | 6 | 1 | 2022-06-03 22:00 | 22 | 6
2022-06-03 23:00 | 23 | 6 | 1 | 2022-06-03 23:00 | 23 | 6
2022-06-04 | 0 | 7 | 1 | 2022-06-04 | 0 | 7
2022-06-04 01:00 | 1 | 7 | 1 | 2022-06-04 01:00 | 1 | 7
2022-06-04 02:00 | 2 | 7 | 1 | 2022-06-04 02:00 | 2 | 7
2022-06-04 03:00 | 3 | 7 | 1 | 2022-06-04 03:00 | 3 | 7
2022-06-04 04:00 | 4 | 7 | 1 | 2022-06-04 04:00 | 4 | 7
2022-06-04 05:00 | 5 | 7 | 1 | 2022-06-04 05:00 | 5 | 7
2022-06-04 06:00 | 6 | 7 | 1 | 2022-06-04 06:00 | 6 | 7
2022-06-04 07:00 | 7 | 7 | 1 | 2022-06-04 07:00 | 7 | 7
2022-06-04 08:00 | 8 | 7 | 1 | 2022-06-04 08:00 | 8 | 7
2022-06-04 09:00 | 9 | 7 | 1 | 2022-06-04 09:00 | 9 | 7
2022-06-04 10:00 | 10 | 7 | 1 | 2022-06-04 10:00 | 10 | 7
2022-06-04 11:00 | 11 | 7 | 1 | 2022-06-04 11:00 | 11 | 7
2022-06-04 12:00 | 12 | 7 | 1 | 2022-06-04 12:00 | 12 | 7
2022-06-04 13:00 | 13 | 7 | 1 | 2022-06-04 13:00 | 13 | 7
2022-06-04 14:00 | 14 | 7 | 1 | 2022-06-04 14:00 | 14 | 7
2022-06-04 15:00 | 15 | 7 | 1 | 2022-06-04 15:00 | 15 | 7
2022-06-04 16:00 | 16 | 7 | 1 | 2022-06-04 16:00 | 16 | 7
2022-06-04 17:00 | 17 | 7 | 1 | 2022-06-04 17:00 | 17 | 7
2022-06-04 18:00 | 18 | 7 | 1 | 2022-06-04 18:00 | 18 | 7
2022-06-04 19:00 | 19 | 7 | 1 | 2022-06-04 19:00 | 19 | 7
2022-06-04 20:00 | 20 | 7 | 1 | 2022-06-04 20:00 | 20 | 7
2022-06-04 21:00 | 21 | 7 | 1 | 2022-06-04 21:00 | 21 | 7
2022-06-04 22:00 | 22 | 7 | 1 | 2022-06-04 22:00 | 22 | 7
2022-06-04 23:00 | 23 | 7 | 1 | 2022-06-04 23:00 | 23 | 7
2022-06-05 | 0 | 1 | 1 | 2022-06-05 | 0 | 1
2022-06-05 01:00 | 1 | 1 | 1 | 2022-06-05 01:00 | 1 | 1
2022-06-05 02:00 | 2 | 1 | 1 | 2022-06-05 02:00 | 2 | 1
2022-06-05 03:00 | 3 | 1 | 1 | 2022-06-05 03:00 | 3 | 1
2022-06-05 04:00 | 4 | 1 | 1 | 2022-06-05 04:00 | 4 | 1
2022-06-05 05:00 | 5 | 1 | 1 | 2022-06-05 05:00 | 5 | 1
2022-06-05 06:00 | 6 | 1 | 1 | 2022-06-05 06:00 | 6 | 1
2022-06-05 07:00 | 7 | 1 | 1 | 2022-06-05 07:00 | 7 | 1
2022-06-05 08:00 | 8 | 1 | 1 | 2022-06-05 08:00 | 8 | 1
2022-06-05 09:00 | 9 | 1 | 1 | 2022-06-05 09:00 | 9 | 1
2022-06-05 10:00 | 10 | 1 | 1 | 2022-06-05 10:00 | 10 | 1
2022-06-05 11:00 | 11 | 1 | 1 | 2022-06-05 11:00 | 11 | 1
2022-06-05 12:00 | 12 | 1 | 1 | 2022-06-05 12:00 | 12 | 1
2022-06-05 13:00 | 13 | 1 | 1 | 2022-06-05 13:00 | 13 | 1
2022-06-05 14:00 | 14 | 1 | 1 | 2022-06-05 14:00 | 14 | 1
2022-06-05 15:00 | 15 | 1 | 1 | 2022-06-05 15:00 | 15 | 1
2022-06-05 16:00 | 16 | 1 | 1 | 2022-06-05 16:00 | 16 | 1
2022-06-05 17:00 | 17 | 1 | 1 | 2022-06-05 17:00 | 17 | 1
2022-06-05 18:00 | 18 | 1 | 1 | 2022-06-05 18:00 | 18 | 1
2022-06-05 19:00 | 19 | 1 | 1 | 2022-06-05 19:00 | 19 | 1
2022-06-05 20:00 | 20 | 1 | 1 | 2022-06-05 20:00 | 20 | 1
2022-06-05 21:00 | 21 | 1 | 1 | 2022-06-05 21:00 | 21 | 1
2022-06-05 22:00 | 22 | 1 | 1 | 2022-06-05 22:00 | 22 | 1
2022-06-05 23:00 | 23 | 1 | 1 | 2022-06-05 23:00 | 23 | 1
2022-06-06 | 0 | 2 | 1 | 2022-06-06 | 0 | 2
2022-06-06 01:00 | 1 | 2 | 1 | 2022-06-06 01:00 | 1 | 2
2022-06-06 02:00 | 2 | 2 | 1 | 2022-06-06 02:00 | 2 | 2
2022-06-06 03:00 | 3 | 2 | 1 | 2022-06-06 03:00 | 3 | 2
2022-06-06 04:00 | 4 | 2 | 1 | 2022-06-06 04:00 | 4 | 2
2022-06-06 05:00 | 5 | 2 | 1 | 2022-06-06 05:00 | 5 | 2
2022-06-06 06:00 | 6 | 2 | 1 | 2022-06-06 06:00 | 6 | 2
2022-06-06 07:00 | 7 | 2 | 1 | 2022-06-06 07:00 | 7 | 2
2022-06-06 08:00 | 8 | 2 | 1 | 2022-06-06 08:00 | 8 | 2
2022-06-06 09:00 | 9 | 2 | 1 | 2022-06-06 09:00 | 9 | 2
2022-06-06 10:00 | 10 | 2 | 1 | 2022-06-06 10:00 | 10 | 2
2022-06-06 11:00 | 11 | 2 | 1 | 2022-06-06 11:00 | 11 | 2
2022-06-06 12:00 | 12 | 2 | 1 | 2022-06-06 12:00 | 12 | 2
2022-06-06 13:00 | 13 | 2 | 1 | 2022-06-06 13:00 | 13 | 2
2022-06-06 14:00 | 14 | 2 | 1 | 2022-06-06 14:00 | 14 | 2
2022-06-06 15:00 | 15 | 2 | 1 | 2022-06-06 15:00 | 15 | 2
2022-06-06 16:00 | 16 | 2 | 1 | 2022-06-06 16:00 | 16 | 2
2022-06-06 17:00 | 17 | 2 | 1 | 2022-06-06 17:00 | 17 | 2
2022-06-06 18:00 | 18 | 2 | 1 | 2022-06-06 18:00 | 18 | 2
2022-06-06 19:00 | 19 | 2 | 1 | 2022-06-06 19:00 | 19 | 2
2022-06-06 20:00 | 20 | 2 | 1 | 2022-06-06 20:00 | 20 | 2
2022-06-06 21:00 | 21 | 2 | 1 | 2022-06-06 21:00 | 21 | 2
2022-06-06 22:00 | 22 | 2 | 1 | 2022-06-06 22:00 | 22 | 2
2022-06-06 23:00 | 23 | 2 | 1 | 2022-06-06 23:00 | 23 | 2
2022-06-07 | 0 | 3 | 1 | 2022-06-07 | 0 | 3
2022-06-07 01:00 | 1 | 3 | 1 | 2022-06-07 01:00 | 1 | 3
2022-06-07 02:00 | 2 | 3 | 1 | 2022-06-07 02:00 | 2 | 3
2022-06-07 03:00 | 3 | 3 | 1 | 2022-06-07 03:00 | 3 | 3
2022-06-07 04:00 | 4 | 3 | 1 | 2022-06-07 04:00 | 4 | 3
2022-06-07 05:00 | 5 | 3 | 1 | 2022-06-07 05:00 | 5 | 3
2022-06-07 06:00 | 6 | 3 | 1 | 2022-06-07 06:00 | 6 | 3
2022-06-07 07:00 | 7 | 3 | 1 | 2022-06-07 07:00 | 7 | 3
2022-06-07 08:00 | 8 | 3 | 1 | 2022-06-07 08:00 | 8 | 3
2022-06-07 09:00 | 9 | 3 | 1 | 2022-06-07 09:00 | 9 | 3
2022-06-07 10:00 | 10 | 3 | 1 | 2022-06-07 10:00 | 10 | 3
2022-06-07 11:00 | 11 | 3 | 1 | 2022-06-07 11:00 | 11 | 3
2022-06-07 12:00 | 12 | 3 | 1 | 2022-06-07 12:00 | 12 | 3
2022-06-07 13:00 | 13 | 3 | 1 | 2022-06-07 13:00 | 13 | 3
2022-06-07 14:00 | 14 | 3 | 1 | 2022-06-07 14:00 | 14 | 3
2022-06-07 15:00 | 15 | 3 | 1 | 2022-06-07 15:00 | 15 | 3
2022-06-07 16:00 | 16 | 3 | 1 | 2022-06-07 16:00 | 16 | 3
2022-06-07 17:00 | 17 | 3 | 1 | 2022-06-07 17:00 | 17 | 3
2022-06-07 18:00 | 18 | 3 | 1 | 2022-06-07 18:00 | 18 | 3
2022-06-07 19:00 | 19 | 3 | 1 | 2022-06-07 19:00 | 19 | 3
2022-06-07 20:00 | 20 | 3 | 1 | 2022-06-07 20:00 | 20 | 3
2022-06-07 21:00 | 21 | 3 | 1 | 2022-06-07 21:00 | 21 | 3
2022-06-07 22:00 | 22 | 3 | 1 | 2022-06-07 22:00 | 22 | 3
2022-06-07 23:00 | 23 | 3 | 1 | 2022-06-07 23:00 | 23 | 3
2022-06-08 | 0 | 4 | 1 | 2022-06-08 | 0 | 4
2022-06-08 01:00 | 1 | 4 | 1 | 2022-06-08 01:00 | 1 | 4
2022-06-08 02:00 | 2 | 4 | 1 | 2022-06-08 02:00 | 2 | 4
2022-06-08 03:00 | 3 | 4 | 1 | 2022-06-08 03:00 | 3 | 4
2022-06-08 04:00 | 4 | 4 | 1 | 2022-06-08 04:00 | 4 | 4
2022-06-08 05:00 | 5 | 4 | 1 | 2022-06-08 05:00 | 5 | 4
2022-06-08 06:00 | 6 | 4 | 1 | 2022-06-08 06:00 | 6 | 4
2022-06-08 07:00 | 7 | 4 | 1 | 2022-06-08 07:00 | 7 | 4
2022-06-08 08:00 | 8 | 4 | 1 | 2022-06-08 08:00 | 8 | 4
2022-06-08 09:00 | 9 | 4 | 1 | 2022-06-08 09:00 | 9 | 4
2022-06-08 10:00 | 10 | 4 | 1 | 2022-06-08 10:00 | 10 | 4
2022-06-08 11:00 | 11 | 4 | 1 | 2022-06-08 11:00 | 11 | 4
2022-06-08 12:00 | 12 | 4 | 1 | 2022-06-08 12:00 | 12 | 4
2022-06-08 13:00 | 13 | 4 | 1 | 2022-06-08 13:00 | 13 | 4
2022-06-08 14:00 | 14 | 4 | 1 | 2022-06-08 14:00 | 14 | 4
2022-06-08 15:00 | 15 | 4 | 1 | 2022-06-08 15:00 | 15 | 4
2022-06-08 16:00 | 16 | 4 | 1 | 2022-06-08 16:00 | 16 | 4
2022-06-08 17:00 | 17 | 4 | 1 | 2022-06-08 17:00 | 17 | 4
2022-06-08 18:00 | 18 | 4 | 1 | 2022-06-08 18:00 | 18 | 4
2022-06-08 19:00 | 19 | 4 | 1 | 2022-06-08 19:00 | 19 | 4
2022-06-08 20:00 | 20 | 4 | 1 | 2022-06-08 20:00 | 20 | 4
2022-06-08 21:00 | 21 | 4 | 1 | 2022-06-08 21:00 | 21 | 4
2022-06-08 22:00 | 22 | 4 | 1 | 2022-06-08 22:00 | 22 | 4
2022-06-08 23:00 | 23 | 4 | 1 | 2022-06-08 23:00 | 23 | 4
2022-06-09 | 0 | 5 | 1 | 2022-06-09 | 0 | 5
2022-06-09 01:00 | 1 | 5 | 1 | 2022-06-09 01:00 | 1 | 5
2022-06-09 02:00 | 2 | 5 | 1 | 2022-06-09 02:00 | 2 | 5
2022-06-09 03:00 | 3 | 5 | 1 | 2022-06-09 03:00 | 3 | 5
2022-06-09 04:00 | 4 | 5 | 1 | 2022-06-09 04:00 | 4 | 5
2022-06-09 05:00 | 5 | 5 | 1 | 2022-06-09 05:00 | 5 | 5
2022-06-09 06:00 | 6 | 5 | 1 | 2022-06-09 06:00 | 6 | 5
2022-06-09 07:00 | 7 | 5 | 1 | 2022-06-09 07:00 | 7 | 5
2022-06-09 08:00 | 8 | 5 | 1 | 2022-06-09 08:00 | 8 | 5
2022-06-09 09:00 | 9 | 5 | 1 | 2022-06-09 09:00 | 9 | 5
2022-06-09 10:00 | 10 | 5 | 1 | 2022-06-09 10:00 | 10 | 5
2022-06-09 11:00 | 11 | 5 | 1 | 2022-06-09 11:00 | 11 | 5
2022-06-09 12:00 | 12 | 5 | 1 | 2022-06-09 12:00 | 12 | 5
2022-06-09 13:00 | 13 | 5 | 1 | 2022-06-09 13:00 | 13 | 5
2022-06-09 14:00 | 14 | 5 | 1 | 2022-06-09 14:00 | 14 | 5
2022-06-09 15:00 | 15 | 5 | 1 | 2022-06-09 15:00 | 15 | 5
2022-06-09 16:00 | 16 | 5 | 1 | 2022-06-09 16:00 | 16 | 5
2022-06-09 17:00 | 17 | 5 | 1 | 2022-06-09 17:00 | 17 | 5
2022-06-09 18:00 | 18 | 5 | 1 | 2022-06-09 18:00 | 18 | 5
2022-06-09 19:00 | 19 | 5 | 1 | 2022-06-09 19:00 | 19 | 5
2022-06-09 20:00 | 20 | 5 | 1 | 2022-06-09 20:00 | 20 | 5
2022-06-09 21:00 | 21 | 5 | 1 | 2022-06-09 21:00 | 21 | 5
2022-06-09 22:00 | 22 | 5 | 1 | 2022-06-09 22:00 | 22 | 5
2022-06-09 23:00 | 23 | 5 | 1 | 2022-06-09 23:00 | 23 | 5
2022-06-10 | 0 | 6 | 1 | 2022-06-10 | 0 | 6
2022-06-10 01:00 | 1 | 6 | 1 | 2022-06-10 01:00 | 1 | 6
2022-06-10 02:00 | 2 | 6 | 1 | 2022-06-10 02:00 | 2 | 6
2022-06-10 03:00 | 3 | 6 | 1 | 2022-06-10 03:00 | 3 | 6
2022-06-10 04:00 | 4 | 6 | 1 | 2022-06-10 04:00 | 4 | 6
2022-06-10 05:00 | 5 | 6 | 1 | 2022-06-10 05:00 | 5 | 6
2022-06-10 06:00 | 6 | 6 | 1 | 2022-06-10 06:00 | 6 | 6
2022-06-10 07:00 | 7 | 6 | 1 | 2022-06-10 07:00 | 7 | 6
2022-06-10 08:00 | 8 | 6 | 1 | 2022-06-10 08:00 | 8 | 6
2022-06-10 09:00 | 9 | 6 | 1 | 2022-06-10 09:00 | 9 | 6
2022-06-10 10:00 | 10 | 6 | 1 | 2022-06-10 10:00 | 10 | 6
2022-06-10 11:00 | 11 | 6 | 1 | 2022-06-10 11:00 | 11 | 6
2022-06-10 12:00 | 12 | 6 | 1 | 2022-06-10 12:00 | 12 | 6
2022-06-10 13:00 | 13 | 6 | 1 | 2022-06-10 13:00 | 13 | 6
2022-06-10 14:00 | 14 | 6 | 1 | 2022-06-10 14:00 | 14 | 6
2022-06-10 15:00 | 15 | 6 | 1 | 2022-06-10 15:00 | 15 | 6
2022-06-10 16:00 | 16 | 6 | 1 | 2022-06-10 16:00 | 16 | 6
2022-06-10 17:00 | 17 | 6 | 1 | 2022-06-10 17:00 | 17 | 6
2022-06-10 18:00 | 18 | 6 | 1 | 2022-06-10 18:00 | 18 | 6
2022-06-10 19:00 | 19 | 6 | 1 | 2022-06-10 19:00 | 19 | 6
2022-06-10 20:00 | 20 | 6 | 1 | 2022-06-10 20:00 | 20 | 6
2022-06-10 21:00 | 21 | 6 | 1 | 2022-06-10 21:00 | 21 | 6
2022-06-10 22:00 | 22 | 6 | 1 | 2022-06-10 22:00 | 22 | 6
2022-06-10 23:00 | 23 | 6 | 1 | 2022-06-10 23:00 | 23 | 6
2022-06-11 | 0 | 7 | 1 | 2022-06-11 | 0 | 7
2022-06-11 01:00 | 1 | 7 | 1 | 2022-06-11 01:00 | 1 | 7
2022-06-11 02:00 | 2 | 7 | 1 | 2022-06-11 02:00 | 2 | 7
2022-06-11 03:00 | 3 | 7 | 1 | 2022-06-11 03:00 | 3 | 7
2022-06-11 04:00 | 4 | 7 | 1 | 2022-06-11 04:00 | 4 | 7
2022-06-11 05:00 | 5 | 7 | 1 | 2022-06-11 05:00 | 5 | 7
2022-06-11 06:00 | 6 | 7 | 1 | 2022-06-11 06:00 | 6 | 7
2022-06-11 07:00 | 7 | 7 | 1 | 2022-06-11 07:00 | 7 | 7
2022-06-11 08:00 | 8 | 7 | 1 | 2022-06-11 08:00 | 8 | 7
2022-06-11 09:00 | 9 | 7 | 1 | 2022-06-11 09:00 | 9 | 7
2022-06-11 10:00 | 10 | 7 | 1 | 2022-06-11 10:00 | 10 | 7
2022-06-11 11:00 | 11 | 7 | 1 | 2022-06-11 11:00 | 11 | 7
2022-06-11 12:00 | 12 | 7 | 1 | 2022-06-11 12:00 | 12 | 7
2022-06-11 13:00 | 13 | 7 | 1 | 2022-06-11 13:00 | 13 | 7
2022-06-11 14:00 | 14 | 7 | 1 | 2022-06-11 14:00 | 14 | 7
2022-06-11 15:00 | 15 | 7 | 1 | 2022-06-11 15:00 | 15 | 7
2022-06-11 16:00 | 16 | 7 | 1 | 2022-06-11 16:00 | 16 | 7
2022-06-11 17:00 | 17 | 7 | 1 | 2022-06-11 17:00 | 17 | 7
2022-06-11 18:00 | 18 | 7 | 1 | 2022-06-11 18:00 | 18 | 7
2022-06-11 19:00 | 19 | 7 | 1 | 2022-06-11 19:00 | 19 | 7
2022-06-11 20:00 | 20 | 7 | 1 | 2022-06-11 20:00 | 20 | 7
2022-06-11 21:00 | 21 | 7 | 1 | 2022-06-11 21:00 | 21 | 7
2022-06-11 22:00 | 22 | 7 | 1 | 2022-06-11 22:00 | 22 | 7
2022-06-11 23:00 | 23 | 7 | 1 | 2022-06-11 23:00 | 23 | 7
2022-06-12 | 0 | 1 | 1 | 2022-06-12 | 0 | 1
2022-06-12 01:00 | 1 | 1 | 1 | 2022-06-12 01:00 | 1 | 1
2022-06-12 02:00 | 2 | 1 | 1 | 2022-06-12 02:00 | 2 | 1
2022-06-12 03:00 | 3 | 1 | 1 | 2022-06-12 03:00 | 3 | 1
2022-06-12 04:00 | 4 | 1 | 1 | 2022-06-12 04:00 | 4 | 1
2022-06-12 05:00 | 5 | 1 | 1 | 2022-06-12 05:00 | 5 | 1
2022-06-12 06:00 | 6 | 1 | 1 | 2022-06-12 06:00 | 6 | 1
2022-06-12 07:00 | 7 | 1 | 1 | 2022-06-12 07:00 | 7 | 1
2022-06-12 08:00 | 8 | 1 | 1 | 2022-06-12 08:00 | 8 | 1
2022-06-12 09:00 | 9 | 1 | 1 | 2022-06-12 09:00 | 9 | 1
2022-06-12 10:00 | 10 | 1 | 1 | 2022-06-12 10:00 | 10 | 1
2022-06-12 11:00 | 11 | 1 | 1 | 2022-06-12 11:00 | 11 | 1
2022-06-12 12:00 | 12 | 1 | 1 | 2022-06-12 12:00 | 12 | 1
2022-06-12 13:00 | 13 | 1 | 1 | 2022-06-12 13:00 | 13 | 1
2022-06-12 14:00 | 14 | 1 | 1 | 2022-06-12 14:00 | 14 | 1
2022-06-12 15:00 | 15 | 1 | 1 | 2022-06-12 15:00 | 15 | 1
2022-06-12 16:00 | 16 | 1 | 1 | 2022-06-12 16:00 | 16 | 1
2022-06-12 17:00 | 17 | 1 | 1 | 2022-06-12 17:00 | 17 | 1
2022-06-12 18:00 | 18 | 1 | 1 | 2022-06-12 18:00 | 18 | 1
2022-06-12 19:00 | 19 | 1 | 1 | 2022-06-12 19:00 | 19 | 1
2022-06-12 20:00 | 20 | 1 | 1 | 2022-06-12 20:00 | 20 | 1
2022-06-12 21:00 | 21 | 1 | 1 | 2022-06-12 21:00 | 21 | 1
2022-06-12 22:00 | 22 | 1 | 1 | 2022-06-12 22:00 | 22 | 1
2022-06-12 23:00 | 23 | 1 | 1 | 2022-06-12 23:00 | 23 | 1
2022-06-13 | 0 | 2 | 1 | 2022-06-13 | 0 | 2
2022-06-13 01:00 | 1 | 2 | 1 | 2022-06-13 01:00 | 1 | 2
2022-06-13 02:00 | 2 | 2 | 1 | 2022-06-13 02:00 | 2 | 2
2022-06-13 03:00 | 3 | 2 | 1 | 2022-06-13 03:00 | 3 | 2
2022-06-13 04:00 | 4 | 2 | 1 | 2022-06-13 04:00 | 4 | 2
2022-06-13 05:00 | 5 | 2 | 1 | 2022-06-13 05:00 | 5 | 2
2022-06-13 06:00 | 6 | 2 | 1 | 2022-06-13 06:00 | 6 | 2
2022-06-13 07:00 | 7 | 2 | 1 | 2022-06-13 07:00 | 7 | 2
2022-06-13 08:00 | 8 | 2 | 1 | 2022-06-13 08:00 | 8 | 2
2022-06-13 09:00 | 9 | 2 | 1 | 2022-06-13 09:00 | 9 | 2
2022-06-13 10:00 | 10 | 2 | 1 | 2022-06-13 10:00 | 10 | 2
2022-06-13 11:00 | 11 | 2 | 1 | 2022-06-13 11:00 | 11 | 2
2022-06-13 12:00 | 12 | 2 | 1 | 2022-06-13 12:00 | 12 | 2
2022-06-13 13:00 | 13 | 2 | 1 | 2022-06-13 13:00 | 13 | 2
2022-06-13 14:00 | 14 | 2 | 1 | 2022-06-13 14:00 | 14 | 2
2022-06-13 15:00 | 15 | 2 | 1 | 2022-06-13 15:00 | 15 | 2
2022-06-13 16:00 | 16 | 2 | 1 | 2022-06-13 16:00 | 16 | 2
2022-06-13 17:00 | 17 | 2 | 1 | 2022-06-13 17:00 | 17 | 2
2022-06-13 18:00 | 18 | 2 | 1 | 2022-06-13 18:00 | 18 | 2
2022-06-13 19:00 | 19 | 2 | 1 | 2022-06-13 19:00 | 19 | 2
2022-06-13 20:00 | 20 | 2 | 1 | 2022-06-13 20:00 | 20 | 2
2022-06-13 21:00 | 21 | 2 | 1 | 2022-06-13 21:00 | 21 | 2
2022-06-13 22:00 | 22 | 2 | 1 | 2022-06-13 22:00 | 22 | 2
2022-06-13 23:00 | 23 | 2 | 1 | 2022-06-13 23:00 | 23 | 2
2022-06-14 | 0 | 3 | 1 | 2022-06-14 | 0 | 3
2022-06-14 01:00 | 1 | 3 | 1 | 2022-06-14 01:00 | 1 | 3
2022-06-14 02:00 | 2 | 3 | 1 | 2022-06-14 02:00 | 2 | 3
2022-06-14 03:00 | 3 | 3 | 1 | 2022-06-14 03:00 | 3 | 3
2022-06-14 04:00 | 4 | 3 | 1 | 2022-06-14 04:00 | 4 | 3
2022-06-14 05:00 | 5 | 3 | 1 | 2022-06-14 05:00 | 5 | 3
2022-06-14 06:00 | 6 | 3 | 1 | 2022-06-14 06:00 | 6 | 3
2022-06-14 07:00 | 7 | 3 | 1 | 2022-06-14 07:00 | 7 | 3
2022-06-14 08:00 | 8 | 3 | 1 | 2022-06-14 08:00 | 8 | 3
2022-06-14 09:00 | 9 | 3 | 1 | 2022-06-14 09:00 | 9 | 3
2022-06-14 10:00 | 10 | 3 | 1 | 2022-06-14 10:00 | 10 | 3
2022-06-14 11:00 | 11 | 3 | 1 | 2022-06-14 11:00 | 11 | 3
2022-06-14 12:00 | 12 | 3 | 1 | 2022-06-14 12:00 | 12 | 3
2022-06-14 13:00 | 13 | 3 | 1 | 2022-06-14 13:00 | 13 | 3
2022-06-14 14:00 | 14 | 3 | 1 | 2022-06-14 14:00 | 14 | 3
2022-06-14 15:00 | 15 | 3 | 1 | 2022-06-14 15:00 | 15 | 3
2022-06-14 16:00 | 16 | 3 | 1 | 2022-06-14 16:00 | 16 | 3
2022-06-14 17:00 | 17 | 3 | 1 | 2022-06-14 17:00 | 17 | 3
2022-06-14 18:00 | 18 | 3 | 1 | 2022-06-14 18:00 | 18 | 3
2022-06-14 19:00 | 19 | 3 | 1 | 2022-06-14 19:00 | 19 | 3
2022-06-14 20:00 | 20 | 3 | 1 | 2022-06-14 20:00 | 20 | 3
2022-06-14 21:00 | 21 | 3 | 1 | 2022-06-14 21:00 | 21 | 3
2022-06-14 22:00 | 22 | 3 | 1 | 2022-06-14 22:00 | 22 | 3
2022-06-14 23:00 | 23 | 3 | 1 | 2022-06-14 23:00 | 23 | 3
2022-06-15 | 0 | 4 | 1 | 2022-06-15 | 0 | 4
2022-06-15 01:00 | 1 | 4 | 1 | 2022-06-15 01:00 | 1 | 4
2022-06-15 02:00 | 2 | 4 | 1 | 2022-06-15 02:00 | 2 | 4
2022-06-15 03:00 | 3 | 4 | 1 | 2022-06-15 03:00 | 3 | 4
2022-06-15 04:00 | 4 | 4 | 1 | 2022-06-15 04:00 | 4 | 4
2022-06-15 05:00 | 5 | 4 | 1 | 2022-06-15 05:00 | 5 | 4
2022-06-15 06:00 | 6 | 4 | 1 | 2022-06-15 06:00 | 6 | 4
2022-06-15 07:00 | 7 | 4 | 1 | 2022-06-15 07:00 | 7 | 4
2022-06-15 08:00 | 8 | 4 | 1 | 2022-06-15 08:00 | 8 | 4
2022-06-15 09:00 | 9 | 4 | 1 | 2022-06-15 09:00 | 9 | 4
2022-06-15 10:00 | 10 | 4 | 1 | 2022-06-15 10:00 | 10 | 4
2022-06-15 11:00 | 11 | 4 | 1 | 2022-06-15 11:00 | 11 | 4
2022-06-15 12:00 | 12 | 4 | 1 | 2022-06-15 12:00 | 12 | 4
2022-06-15 13:00 | 13 | 4 | 1 | 2022-06-15 13:00 | 13 | 4
2022-06-15 14:00 | 14 | 4 | 1 | 2022-06-15 14:00 | 14 | 4
2022-06-15 15:00 | 15 | 4 | 1 | 2022-06-15 15:00 | 15 | 4
2022-06-15 16:00 | 16 | 4 | 1 | 2022-06-15 16:00 | 16 | 4
2022-06-15 17:00 | 17 | 4 | 1 | 2022-06-15 17:00 | 17 | 4
2022-06-15 18:00 | 18 | 4 | 1 | 2022-06-15 18:00 | 18 | 4
2022-06-15 19:00 | 19 | 4 | 1 | 2022-06-15 19:00 | 19 | 4
2022-06-15 20:00 | 20 | 4 | 1 | 2022-06-15 20:00 | 20 | 4
2022-06-15 21:00 | 21 | 4 | 1 | 2022-06-15 21:00 | 21 | 4
2022-06-15 22:00 | 22 | 4 | 1 | 2022-06-15 22:00 | 22 | 4
2022-06-15 23:00 | 23 | 4 | 1 | 2022-06-15 23:00 | 23 | 4
2022-06-16 | 0 | 5 | 1 | 2022-06-16 | 0 | 5
2022-06-16 01:00 | 1 | 5 | 1 | 2022-06-16 01:00 | 1 | 5
2022-06-16 02:00 | 2 | 5 | 1 | 2022-06-16 02:00 | 2 | 5
2022-06-16 03:00 | 3 | 5 | 1 | 2022-06-16 03:00 | 3 | 5
2022-06-16 04:00 | 4 | 5 | 1 | 2022-06-16 04:00 | 4 | 5
2022-06-16 05:00 | 5 | 5 | 1 | 2022-06-16 05:00 | 5 | 5
2022-06-16 06:00 | 6 | 5 | 1 | 2022-06-16 06:00 | 6 | 5
2022-06-16 07:00 | 7 | 5 | 1 | 2022-06-16 07:00 | 7 | 5
2022-06-16 08:00 | 8 | 5 | 1 | 2022-06-16 08:00 | 8 | 5
2022-06-16 09:00 | 9 | 5 | 1 | 2022-06-16 09:00 | 9 | 5
2022-06-16 10:00 | 10 | 5 | 1 | 2022-06-16 10:00 | 10 | 5
2022-06-16 11:00 | 11 | 5 | 1 | 2022-06-16 11:00 | 11 | 5
2022-06-16 12:00 | 12 | 5 | 1 | 2022-06-16 12:00 | 12 | 5
2022-06-16 13:00 | 13 | 5 | 1 | 2022-06-16 13:00 | 13 | 5
2022-06-16 14:00 | 14 | 5 | 1 | 2022-06-16 14:00 | 14 | 5
2022-06-16 15:00 | 15 | 5 | 1 | 2022-06-16 15:00 | 15 | 5
2022-06-16 16:00 | 16 | 5 | 1 | 2022-06-16 16:00 | 16 | 5
2022-06-16 17:00 | 17 | 5 | 1 | 2022-06-16 17:00 | 17 | 5
2022-06-16 18:00 | 18 | 5 | 1 | 2022-06-16 18:00 | 18 | 5
2022-06-16 19:00 | 19 | 5 | 1 | 2022-06-16 19:00 | 19 | 5
2022-06-16 20:00 | 20 | 5 | 1 | 2022-06-16 20:00 | 20 | 5
2022-06-16 21:00 | 21 | 5 | 1 | 2022-06-16 21:00 | 21 | 5
2022-06-16 22:00 | 22 | 5 | 1 | 2022-06-16 22:00 | 22 | 5
2022-06-16 23:00 | 23 | 5 | 1 | 2022-06-16 23:00 | 23 | 5
2022-06-17 | 0 | 6 | 1 | 2022-06-17 | 0 | 6
2022-06-17 01:00 | 1 | 6 | 1 | 2022-06-17 01:00 | 1 | 6
2022-06-17 02:00 | 2 | 6 | 1 | 2022-06-17 02:00 | 2 | 6
2022-06-17 03:00 | 3 | 6 | 1 | 2022-06-17 03:00 | 3 | 6
2022-06-17 04:00 | 4 | 6 | 1 | 2022-06-17 04:00 | 4 | 6
2022-06-17 05:00 | 5 | 6 | 1 | 2022-06-17 05:00 | 5 | 6
2022-06-17 06:00 | 6 | 6 | 1 | 2022-06-17 06:00 | 6 | 6
2022-06-17 07:00 | 7 | 6 | 1 | 2022-06-17 07:00 | 7 | 6
2022-06-17 08:00 | 8 | 6 | 1 | 2022-06-17 08:00 | 8 | 6
2022-06-17 09:00 | 9 | 6 | 1 | 2022-06-17 09:00 | 9 | 6
2022-06-17 10:00 | 10 | 6 | 1 | 2022-06-17 10:00 | 10 | 6
2022-06-17 11:00 | 11 | 6 | 1 | 2022-06-17 11:00 | 11 | 6
2022-06-17 12:00 | 12 | 6 | 1 | 2022-06-17 12:00 | 12 | 6
2022-06-17 13:00 | 13 | 6 | 1 | 2022-06-17 13:00 | 13 | 6
2022-06-17 14:00 | 14 | 6 | 1 | 2022-06-17 14:00 | 14 | 6
2022-06-17 15:00 | 15 | 6 | 1 | 2022-06-17 15:00 | 15 | 6
2022-06-17 16:00 | 16 | 6 | 1 | 2022-06-17 16:00 | 16 | 6
2022-06-17 17:00 | 17 | 6 | 1 | 2022-06-17 17:00 | 17 | 6
2022-06-17 18:00 | 18 | 6 | 1 | 2022-06-17 18:00 | 18 | 6
2022-06-17 19:00 | 19 | 6 | 1 | 2022-06-17 19:00 | 19 | 6
2022-06-17 20:00 | 20 | 6 | 1 | 2022-06-17 20:00 | 20 | 6
2022-06-17 21:00 | 21 | 6 | 1 | 2022-06-17 21:00 | 21 | 6
2022-06-17 22:00 | 22 | 6 | 1 | 2022-06-17 22:00 | 22 | 6
2022-06-17 23:00 | 23 | 6 | 1 | 2022-06-17 23:00 | 23 | 6
2022-06-18 | 0 | 7 | 1 | 2022-06-18 | 0 | 7
2022-06-18 01:00 | 1 | 7 | 1 | 2022-06-18 01:00 | 1 | 7
2022-06-18 02:00 | 2 | 7 | 1 | 2022-06-18 02:00 | 2 | 7
2022-06-18 03:00 | 3 | 7 | 1 | 2022-06-18 03:00 | 3 | 7
2022-06-18 04:00 | 4 | 7 | 1 | 2022-06-18 04:00 | 4 | 7
2022-06-18 05:00 | 5 | 7 | 1 | 2022-06-18 05:00 | 5 | 7
2022-06-18 06:00 | 6 | 7 | 1 | 2022-06-18 06:00 | 6 | 7
2022-06-18 07:00 | 7 | 7 | 1 | 2022-06-18 07:00 | 7 | 7
2022-06-18 08:00 | 8 | 7 | 1 | 2022-06-18 08:00 | 8 | 7
2022-06-18 09:00 | 9 | 7 | 1 | 2022-06-18 09:00 | 9 | 7
2022-06-18 10:00 | 10 | 7 | 1 | 2022-06-18 10:00 | 10 | 7
2022-06-18 11:00 | 11 | 7 | 1 | 2022-06-18 11:00 | 11 | 7
2022-06-18 12:00 | 12 | 7 | 1 | 2022-06-18 12:00 | 12 | 7
2022-06-18 13:00 | 13 | 7 | 1 | 2022-06-18 13:00 | 13 | 7
2022-06-18 14:00 | 14 | 7 | 1 | 2022-06-18 14:00 | 14 | 7
2022-06-18 15:00 | 15 | 7 | 1 | 2022-06-18 15:00 | 15 | 7
2022-06-18 16:00 | 16 | 7 | 1 | 2022-06-18 16:00 | 16 | 7
2022-06-18 17:00 | 17 | 7 | 1 | 2022-06-18 17:00 | 17 | 7
2022-06-18 18:00 | 18 | 7 | 1 | 2022-06-18 18:00 | 18 | 7
2022-06-18 19:00 | 19 | 7 | 1 | 2022-06-18 19:00 | 19 | 7
2022-06-18 20:00 | 20 | 7 | 1 | 2022-06-18 20:00 | 20 | 7
2022-06-18 21:00 | 21 | 7 | 1 | 2022-06-18 21:00 | 21 | 7
2022-06-18 22:00 | 22 | 7 | 1 | 2022-06-18 22:00 | 22 | 7
2022-06-18 23:00 | 23 | 7 | 1 | 2022-06-18 23:00 | 23 | 7
2022-06-19 | 0 | 1 | 1 | 2022-06-19 | 0 | 1
2022-06-19 01:00 | 1 | 1 | 1 | 2022-06-19 01:00 | 1 | 1
2022-06-19 02:00 | 2 | 1 | 1 | 2022-06-19 02:00 | 2 | 1
2022-06-19 03:00 | 3 | 1 | 1 | 2022-06-19 03:00 | 3 | 1
2022-06-19 04:00 | 4 | 1 | 1 | 2022-06-19 04:00 | 4 | 1
2022-06-19 05:00 | 5 | 1 | 1 | 2022-06-19 05:00 | 5 | 1
2022-06-19 06:00 | 6 | 1 | 1 | 2022-06-19 06:00 | 6 | 1
2022-06-19 07:00 | 7 | 1 | 1 | 2022-06-19 07:00 | 7 | 1
2022-06-19 08:00 | 8 | 1 | 1 | 2022-06-19 08:00 | 8 | 1
2022-06-19 09:00 | 9 | 1 | 1 | 2022-06-19 09:00 | 9 | 1
2022-06-19 10:00 | 10 | 1 | 1 | 2022-06-19 10:00 | 10 | 1
2022-06-19 11:00 | 11 | 1 | 1 | 2022-06-19 11:00 | 11 | 1
2022-06-19 12:00 | 12 | 1 | 1 | 2022-06-19 12:00 | 12 | 1
2022-06-19 13:00 | 13 | 1 | 1 | 2022-06-19 13:00 | 13 | 1
2022-06-19 14:00 | 14 | 1 | 1 | 2022-06-19 14:00 | 14 | 1
2022-06-19 15:00 | 15 | 1 | 1 | 2022-06-19 15:00 | 15 | 1
2022-06-19 16:00 | 16 | 1 | 1 | 2022-06-19 16:00 | 16 | 1
2022-06-19 17:00 | 17 | 1 | 1 | 2022-06-19 17:00 | 17 | 1
2022-06-19 18:00 | 18 | 1 | 1 | 2022-06-19 18:00 | 18 | 1
2022-06-19 19:00 | 19 | 1 | 1 | 2022-06-19 19:00 | 19 | 1
2022-06-19 20:00 | 20 | 1 | 1 | 2022-06-19 20:00 | 20 | 1
2022-06-19 21:00 | 21 | 1 | 1 | 2022-06-19 21:00 | 21 | 1
2022-06-19 22:00 | 22 | 1 | 1 | 2022-06-19 22:00 | 22 | 1
2022-06-19 23:00 | 23 | 1 | 1 | 2022-06-19 23:00 | 23 | 1
2022-06-20 | 0 | 2 | 1 | 2022-06-20 | 0 | 2
2022-06-20 01:00 | 1 | 2 | 1 | 2022-06-20 01:00 | 1 | 2
2022-06-20 02:00 | 2 | 2 | 1 | 2022-06-20 02:00 | 2 | 2
2022-06-20 03:00 | 3 | 2 | 1 | 2022-06-20 03:00 | 3 | 2
2022-06-20 04:00 | 4 | 2 | 1 | 2022-06-20 04:00 | 4 | 2
2022-06-20 05:00 | 5 | 2 | 1 | 2022-06-20 05:00 | 5 | 2
2022-06-20 06:00 | 6 | 2 | 1 | 2022-06-20 06:00 | 6 | 2
2022-06-20 07:00 | 7 | 2 | 1 | 2022-06-20 07:00 | 7 | 2
2022-06-20 08:00 | 8 | 2 | 1 | 2022-06-20 08:00 | 8 | 2
2022-06-20 09:00 | 9 | 2 | 1 | 2022-06-20 09:00 | 9 | 2
2022-06-20 10:00 | 10 | 2 | 1 | 2022-06-20 10:00 | 10 | 2
2022-06-20 11:00 | 11 | 2 | 1 | 2022-06-20 11:00 | 11 | 2
2022-06-20 12:00 | 12 | 2 | 1 | 2022-06-20 12:00 | 12 | 2
2022-06-20 13:00 | 13 | 2 | 1 | 2022-06-20 13:00 | 13 | 2
2022-06-20 14:00 | 14 | 2 | 1 | 2022-06-20 14:00 | 14 | 2
2022-06-20 15:00 | 15 | 2 | 1 | 2022-06-20 15:00 | 15 | 2
2022-06-20 16:00 | 16 | 2 | 1 | 2022-06-20 16:00 | 16 | 2
2022-06-20 17:00 | 17 | 2 | 1 | 2022-06-20 17:00 | 17 | 2
2022-06-20 18:00 | 18 | 2 | 1 | 2022-06-20 18:00 | 18 | 2
2022-06-20 19:00 | 19 | 2 | 1 | 2022-06-20 19:00 | 19 | 2
2022-06-20 20:00 | 20 | 2 | 1 | 2022-06-20 20:00 | 20 | 2
2022-06-20 21:00 | 21 | 2 | 1 | 2022-06-20 21:00 | 21 | 2
2022-06-20 22:00 | 22 | 2 | 1 | 2022-06-20 22:00 | 22 | 2
2022-06-20 23:00 | 23 | 2 | 1 | 2022-06-20 23:00 | 23 | 2
2022-06-21 | 0 | 3 | 1 | 2022-06-21 | 0 | 3
2022-06-21 01:00 | 1 | 3 | 1 | 2022-06-21 01:00 | 1 | 3
2022-06-21 02:00 | 2 | 3 | 1 | 2022-06-21 02:00 | 2 | 3
2022-06-21 03:00 | 3 | 3 | 1 | 2022-06-21 03:00 | 3 | 3
2022-06-21 04:00 | 4 | 3 | 1 | 2022-06-21 04:00 | 4 | 3
2022-06-21 05:00 | 5 | 3 | 1 | 2022-06-21 05:00 | 5 | 3
2022-06-21 06:00 | 6 | 3 | 1 | 2022-06-21 06:00 | 6 | 3
2022-06-21 07:00 | 7 | 3 | 1 | 2022-06-21 07:00 | 7 | 3
2022-06-21 08:00 | 8 | 3 | 1 | 2022-06-21 08:00 | 8 | 3
2022-06-21 09:00 | 9 | 3 | 1 | 2022-06-21 09:00 | 9 | 3
2022-06-21 10:00 | 10 | 3 | 1 | 2022-06-21 10:00 | 10 | 3
2022-06-21 11:00 | 11 | 3 | 1 | 2022-06-21 11:00 | 11 | 3
2022-06-21 12:00 | 12 | 3 | 1 | 2022-06-21 12:00 | 12 | 3
2022-06-21 13:00 | 13 | 3 | 1 | 2022-06-21 13:00 | 13 | 3
2022-06-21 14:00 | 14 | 3 | 1 | 2022-06-21 14:00 | 14 | 3
2022-06-21 15:00 | 15 | 3 | 1 | 2022-06-21 15:00 | 15 | 3
2022-06-21 16:00 | 16 | 3 | 1 | 2022-06-21 16:00 | 16 | 3
2022-06-21 17:00 | 17 | 3 | 1 | 2022-06-21 17:00 | 17 | 3
2022-06-21 18:00 | 18 | 3 | 1 | 2022-06-21 18:00 | 18 | 3
2022-06-21 19:00 | 19 | 3 | 1 | 2022-06-21 19:00 | 19 | 3
2022-06-21 20:00 | 20 | 3 | 1 | 2022-06-21 20:00 | 20 | 3
2022-06-21 21:00 | 21 | 3 | 1 | 2022-06-21 21:00 | 21 | 3
2022-06-21 22:00 | 22 | 3 | 1 | 2022-06-21 22:00 | 22 | 3
2022-06-21 23:00 | 23 | 3 | 1 | 2022-06-21 23:00 | 23 | 3
2022-06-22 | 0 | 4 | 1 | 2022-06-22 | 0 | 4
2022-06-22 01:00 | 1 | 4 | 1 | 2022-06-22 01:00 | 1 | 4
2022-06-22 02:00 | 2 | 4 | 1 | 2022-06-22 02:00 | 2 | 4
2022-06-22 03:00 | 3 | 4 | 1 | 2022-06-22 03:00 | 3 | 4
2022-06-22 04:00 | 4 | 4 | 1 | 2022-06-22 04:00 | 4 | 4
2022-06-22 05:00 | 5 | 4 | 1 | 2022-06-22 05:00 | 5 | 4
2022-06-22 06:00 | 6 | 4 | 1 | 2022-06-22 06:00 | 6 | 4
2022-06-22 07:00 | 7 | 4 | 1 | 2022-06-22 07:00 | 7 | 4
2022-06-22 08:00 | 8 | 4 | 1 | 2022-06-22 08:00 | 8 | 4
2022-06-22 09:00 | 9 | 4 | 1 | 2022-06-22 09:00 | 9 | 4
2022-06-22 10:00 | 10 | 4 | 1 | 2022-06-22 10:00 | 10 | 4
2022-06-22 11:00 | 11 | 4 | 1 | 2022-06-22 11:00 | 11 | 4
2022-06-22 12:00 | 12 | 4 | 1 | 2022-06-22 12:00 | 12 | 4
2022-06-22 13:00 | 13 | 4 | 1 | 2022-06-22 13:00 | 13 | 4
2022-06-22 14:00 | 14 | 4 | 1 | 2022-06-22 14:00 | 14 | 4
2022-06-22 15:00 | 15 | 4 | 1 | 2022-06-22 15:00 | 15 | 4
2022-06-22 16:00 | 16 | 4 | 1 | 2022-06-22 16:00 | 16 | 4
2022-06-22 17:00 | 17 | 4 | 1 | 2022-06-22 17:00 | 17 | 4
2022-06-22 18:00 | 18 | 4 | 1 | 2022-06-22 18:00 | 18 | 4
2022-06-22 19:00 | 19 | 4 | 1 | 2022-06-22 19:00 | 19 | 4
2022-06-22 20:00 | 20 | 4 | 1 | 2022-06-22 20:00 | 20 | 4
2022-06-22 21:00 | 21 | 4 | 1 | 2022-06-22 21:00 | 21 | 4
2022-06-22 22:00 | 22 | 4 | 1 | 2022-06-22 22:00 | 22 | 4
2022-06-22 23:00 | 23 | 4 | 1 | 2022-06-22 23:00 | 23 | 4
2022-06-23 | 0 | 5 | 1 | 2022-06-23 | 0 | 5
2022-06-23 01:00 | 1 | 5 | 1 | 2022-06-23 01:00 | 1 | 5
2022-06-23 02:00 | 2 | 5 | 1 | 2022-06-23 02:00 | 2 | 5
2022-06-23 03:00 | 3 | 5 | 1 | 2022-06-23 03:00 | 3 | 5
2022-06-23 04:00 | 4 | 5 | 1 | 2022-06-23 04:00 | 4 | 5
2022-06-23 05:00 | 5 | 5 | 1 | 2022-06-23 05:00 | 5 | 5
2022-06-23 06:00 | 6 | 5 | 1 | 2022-06-23 06:00 | 6 | 5
2022-06-23 07:00 | 7 | 5 | 1 | 2022-06-23 07:00 | 7 | 5
2022-06-23 08:00 | 8 | 5 | 1 | 2022-06-23 08:00 | 8 | 5
2022-06-23 09:00 | 9 | 5 | 1 | 2022-06-23 09:00 | 9 | 5
2022-06-23 10:00 | 10 | 5 | 1 | 2022-06-23 10:00 | 10 | 5
2022-06-23 11:00 | 11 | 5 | 1 | 2022-06-23 11:00 | 11 | 5
2022-06-23 12:00 | 12 | 5 | 1 | 2022-06-23 12:00 | 12 | 5
2022-06-23 13:00 | 13 | 5 | 1 | 2022-06-23 13:00 | 13 | 5
2022-06-23 14:00 | 14 | 5 | 1 | 2022-06-23 14:00 | 14 | 5
2022-06-23 15:00 | 15 | 5 | 1 | 2022-06-23 15:00 | 15 | 5
2022-06-23 16:00 | 16 | 5 | 1 | 2022-06-23 16:00 | 16 | 5
2022-06-23 17:00 | 17 | 5 | 1 | 2022-06-23 17:00 | 17 | 5
2022-06-23 18:00 | 18 | 5 | 1 | 2022-06-23 18:00 | 18 | 5
2022-06-23 19:00 | 19 | 5 | 1 | 2022-06-23 19:00 | 19 | 5
2022-06-23 20:00 | 20 | 5 | 1 | 2022-06-23 20:00 | 20 | 5
2022-06-23 21:00 | 21 | 5 | 1 | 2022-06-23 21:00 | 21 | 5
2022-06-23 22:00 | 22 | 5 | 1 | 2022-06-23 22:00 | 22 | 5
2022-06-23 23:00 | 23 | 5 | 1 | 2022-06-23 23:00 | 23 | 5
2022-06-24 | 0 | 6 | 1 | 2022-06-24 | 0 | 6
2022-06-24 01:00 | 1 | 6 | 1 | 2022-06-24 01:00 | 1 | 6
2022-06-24 02:00 | 2 | 6 | 1 | 2022-06-24 02:00 | 2 | 6
2022-06-24 03:00 | 3 | 6 | 1 | 2022-06-24 03:00 | 3 | 6
2022-06-24 04:00 | 4 | 6 | 1 | 2022-06-24 04:00 | 4 | 6
2022-06-24 05:00 | 5 | 6 | 1 | 2022-06-24 05:00 | 5 | 6
2022-06-24 06:00 | 6 | 6 | 1 | 2022-06-24 06:00 | 6 | 6
2022-06-24 07:00 | 7 | 6 | 1 | 2022-06-24 07:00 | 7 | 6
2022-06-24 08:00 | 8 | 6 | 1 | 2022-06-24 08:00 | 8 | 6
2022-06-24 09:00 | 9 | 6 | 1 | 2022-06-24 09:00 | 9 | 6
2022-06-24 10:00 | 10 | 6 | 1 | 2022-06-24 10:00 | 10 | 6
2022-06-24 11:00 | 11 | 6 | 1 | 2022-06-24 11:00 | 11 | 6
2022-06-24 12:00 | 12 | 6 | 1 | 2022-06-24 12:00 | 12 | 6
2022-06-24 13:00 | 13 | 6 | 1 | 2022-06-24 13:00 | 13 | 6
2022-06-24 14:00 | 14 | 6 | 1 | 2022-06-24 14:00 | 14 | 6
2022-06-24 15:00 | 15 | 6 | 1 | 2022-06-24 15:00 | 15 | 6
2022-06-24 16:00 | 16 | 6 | 1 | 2022-06-24 16:00 | 16 | 6
2022-06-24 17:00 | 17 | 6 | 1 | 2022-06-24 17:00 | 17 | 6
2022-06-24 18:00 | 18 | 6 | 1 | 2022-06-24 18:00 | 18 | 6
2022-06-24 19:00 | 19 | 6 | 1 | 2022-06-24 19:00 | 19 | 6
2022-06-24 20:00 | 20 | 6 | 1 | 2022-06-24 20:00 | 20 | 6
2022-06-24 21:00 | 21 | 6 | 1 | 2022-06-24 21:00 | 21 | 6
2022-06-24 22:00 | 22 | 6 | 1 | 2022-06-24 22:00 | 22 | 6
2022-06-24 23:00 | 23 | 6 | 1 | 2022-06-24 23:00 | 23 | 6
2022-06-25 | 0 | 7 | 1 | 2022-06-25 | 0 | 7
2022-06-25 01:00 | 1 | 7 | 1 | 2022-06-25 01:00 | 1 | 7
2022-06-25 02:00 | 2 | 7 | 1 | 2022-06-25 02:00 | 2 | 7
2022-06-25 03:00 | 3 | 7 | 1 | 2022-06-25 03:00 | 3 | 7
2022-06-25 04:00 | 4 | 7 | 1 | 2022-06-25 04:00 | 4 | 7
2022-06-25 05:00 | 5 | 7 | 1 | 2022-06-25 05:00 | 5 | 7
2022-06-25 06:00 | 6 | 7 | 1 | 2022-06-25 06:00 | 6 | 7
2022-06-25 07:00 | 7 | 7 | 1 | 2022-06-25 07:00 | 7 | 7
2022-06-25 08:00 | 8 | 7 | 1 | 2022-06-25 08:00 | 8 | 7
2022-06-25 09:00 | 9 | 7 | 1 | 2022-06-25 09:00 | 9 | 7
2022-06-25 10:00 | 10 | 7 | 1 | 2022-06-25 10:00 | 10 | 7
2022-06-25 11:00 | 11 | 7 | 1 | 2022-06-25 11:00 | 11 | 7
2022-06-25 12:00 | 12 | 7 | 1 | 2022-06-25 12:00 | 12 | 7
2022-06-25 13:00 | 13 | 7 | 1 | 2022-06-25 13:00 | 13 | 7
2022-06-25 14:00 | 14 | 7 | 1 | 2022-06-25 14:00 | 14 | 7
2022-06-25 15:00 | 15 | 7 | 1 | 2022-06-25 15:00 | 15 | 7
2022-06-25 16:00 | 16 | 7 | 1 | 2022-06-25 16:00 | 16 | 7
2022-06-25 17:00 | 17 | 7 | 1 | 2022-06-25 17:00 | 17 | 7
2022-06-25 18:00 | 18 | 7 | 1 | 2022-06-25 18:00 | 18 | 7
2022-06-25 19:00 | 19 | 7 | 1 | 2022-06-25 19:00 | 19 | 7
2022-06-25 20:00 | 20 | 7 | 1 | 2022-06-25 20:00 | 20 | 7
2022-06-25 21:00 | 21 | 7 | 1 | 2022-06-25 21:00 | 21 | 7
2022-06-25 22:00 | 22 | 7 | 1 | 2022-06-25 22:00 | 22 | 7
2022-06-25 23:00 | 23 | 7 | 1 | 2022-06-25 23:00 | 23 | 7
2022-06-26 | 0 | 1 | 1 | 2022-06-26 | 0 | 1
2022-06-26 01:00 | 1 | 1 | 1 | 2022-06-26 01:00 | 1 | 1
2022-06-26 02:00 | 2 | 1 | 1 | 2022-06-26 02:00 | 2 | 1
2022-06-26 03:00 | 3 | 1 | 1 | 2022-06-26 03:00 | 3 | 1
2022-06-26 04:00 | 4 | 1 | 1 | 2022-06-26 04:00 | 4 | 1
2022-06-26 05:00 | 5 | 1 | 1 | 2022-06-26 05:00 | 5 | 1
2022-06-26 06:00 | 6 | 1 | 1 | 2022-06-26 06:00 | 6 | 1
2022-06-26 07:00 | 7 | 1 | 1 | 2022-06-26 07:00 | 7 | 1
2022-06-26 08:00 | 8 | 1 | 1 | 2022-06-26 08:00 | 8 | 1
2022-06-26 09:00 | 9 | 1 | 1 | 2022-06-26 09:00 | 9 | 1
2022-06-26 10:00 | 10 | 1 | 1 | 2022-06-26 10:00 | 10 | 1
2022-06-26 11:00 | 11 | 1 | 1 | 2022-06-26 11:00 | 11 | 1
2022-06-26 12:00 | 12 | 1 | 1 | 2022-06-26 12:00 | 12 | 1
2022-06-26 13:00 | 13 | 1 | 1 | 2022-06-26 13:00 | 13 | 1
2022-06-26 14:00 | 14 | 1 | 1 | 2022-06-26 14:00 | 14 | 1
2022-06-26 15:00 | 15 | 1 | 1 | 2022-06-26 15:00 | 15 | 1
2022-06-26 16:00 | 16 | 1 | 1 | 2022-06-26 16:00 | 16 | 1
2022-06-26 17:00 | 17 | 1 | 1 | 2022-06-26 17:00 | 17 | 1
2022-06-26 18:00 | 18 | 1 | 1 | 2022-06-26 18:00 | 18 | 1
2022-06-26 19:00 | 19 | 1 | 1 | 2022-06-26 19:00 | 19 | 1
2022-06-26 20:00 | 20 | 1 | 1 | 2022-06-26 20:00 | 20 | 1
2022-06-26 21:00 | 21 | 1 | 1 | 2022-06-26 21:00 | 21 | 1
2022-06-26 22:00 | 22 | 1 | 1 | 2022-06-26 22:00 | 22 | 1
2022-06-26 23:00 | 23 | 1 | 1 | 2022-06-26 23:00 | 23 | 1
2022-06-27 | 0 | 2 | 1 | 2022-06-27 | 0 | 2
2022-06-27 01:00 | 1 | 2 | 1 | 2022-06-27 01:00 | 1 | 2
2022-06-27 02:00 | 2 | 2 | 1 | 2022-06-27 02:00 | 2 | 2
2022-06-27 03:00 | 3 | 2 | 1 | 2022-06-27 03:00 | 3 | 2
2022-06-27 04:00 | 4 | 2 | 1 | 2022-06-27 04:00 | 4 | 2
2022-06-27 05:00 | 5 | 2 | 1 | 2022-06-27 05:00 | 5 | 2
2022-06-27 06:00 | 6 | 2 | 1 | 2022-06-27 06:00 | 6 | 2
2022-06-27 07:00 | 7 | 2 | 1 | 2022-06-27 07:00 | 7 | 2
2022-06-27 08:00 | 8 | 2 | 1 | 2022-06-27 08:00 | 8 | 2
2022-06-27 09:00 | 9 | 2 | 1 | 2022-06-27 09:00 | 9 | 2
2022-06-27 10:00 | 10 | 2 | 1 | 2022-06-27 10:00 | 10 | 2
2022-06-27 11:00 | 11 | 2 | 1 | 2022-06-27 11:00 | 11 | 2
2022-06-27 12:00 | 12 | 2 | 1 | 2022-06-27 12:00 | 12 | 2
2022-06-27 13:00 | 13 | 2 | 1 | 2022-06-27 13:00 | 13 | 2
2022-06-27 14:00 | 14 | 2 | 1 | 2022-06-27 14:00 | 14 | 2
2022-06-27 15:00 | 15 | 2 | 1 | 2022-06-27 15:00 | 15 | 2
2022-06-27 16:00 | 16 | 2 | 1 | 2022-06-27 16:00 | 16 | 2
2022-06-27 17:00 | 17 | 2 | 1 | 2022-06-27 17:00 | 17 | 2
2022-06-27 18:00 | 18 | 2 | 1 | 2022-06-27 18:00 | 18 | 2
2022-06-27 19:00 | 19 | 2 | 1 | 2022-06-27 19:00 | 19 | 2
2022-06-27 20:00 | 20 | 2 | 1 | 2022-06-27 20:00 | 20 | 2
2022-06-27 21:00 | 21 | 2 | 1 | 2022-06-27 21:00 | 21 | 2
2022-06-27 22:00 | 22 | 2 | 1 | 2022-06-27 22:00 | 22 | 2
2022-06-27 23:00 | 23 | 2 | 1 | 2022-06-27 23:00 | 23 | 2
2022-06-28 | 0 | 3 | 1 | 2022-06-28 | 0 | 3
2022-06-28 01:00 | 1 | 3 | 1 | 2022-06-28 01:00 | 1 | 3
2022-06-28 02:00 | 2 | 3 | 1 | 2022-06-28 02:00 | 2 | 3
2022-06-28 03:00 | 3 | 3 | 1 | 2022-06-28 03:00 | 3 | 3
2022-06-28 04:00 | 4 | 3 | 1 | 2022-06-28 04:00 | 4 | 3
2022-06-28 05:00 | 5 | 3 | 1 | 2022-06-28 05:00 | 5 | 3
2022-06-28 06:00 | 6 | 3 | 1 | 2022-06-28 06:00 | 6 | 3
2022-06-28 07:00 | 7 | 3 | 1 | 2022-06-28 07:00 | 7 | 3
2022-06-28 08:00 | 8 | 3 | 1 | 2022-06-28 08:00 | 8 | 3
2022-06-28 09:00 | 9 | 3 | 1 | 2022-06-28 09:00 | 9 | 3
2022-06-28 10:00 | 10 | 3 | 1 | 2022-06-28 10:00 | 10 | 3
2022-06-28 11:00 | 11 | 3 | 1 | 2022-06-28 11:00 | 11 | 3
2022-06-28 12:00 | 12 | 3 | 1 | 2022-06-28 12:00 | 12 | 3
2022-06-28 13:00 | 13 | 3 | 1 | 2022-06-28 13:00 | 13 | 3
2022-06-28 14:00 | 14 | 3 | 1 | 2022-06-28 14:00 | 14 | 3
2022-06-28 15:00 | 15 | 3 | 1 | 2022-06-28 15:00 | 15 | 3
2022-06-28 16:00 | 16 | 3 | 1 | 2022-06-28 16:00 | 16 | 3
2022-06-28 17:00 | 17 | 3 | 1 | 2022-06-28 17:00 | 17 | 3
2022-06-28 18:00 | 18 | 3 | 1 | 2022-06-28 18:00 | 18 | 3
2022-06-28 19:00 | 19 | 3 | 1 | 2022-06-28 19:00 | 19 | 3
2022-06-28 20:00 | 20 | 3 | 1 | 2022-06-28 20:00 | 20 | 3
2022-06-28 21:00 | 21 | 3 | 1 | 2022-06-28 21:00 | 21 | 3
2022-06-28 22:00 | 22 | 3 | 1 | 2022-06-28 22:00 | 22 | 3
2022-06-28 23:00 | 23 | 3 | 1 | 2022-06-28 23:00 | 23 | 3
2022-06-29 | 0 | 4 | 1 | 2022-06-29 | 0 | 4
2022-06-29 01:00 | 1 | 4 | 1 | 2022-06-29 01:00 | 1 | 4
2022-06-29 02:00 | 2 | 4 | 1 | 2022-06-29 02:00 | 2 | 4
2022-06-29 03:00 | 3 | 4 | 1 | 2022-06-29 03:00 | 3 | 4
2022-06-29 04:00 | 4 | 4 | 1 | 2022-06-29 04:00 | 4 | 4
2022-06-29 05:00 | 5 | 4 | 1 | 2022-06-29 05:00 | 5 | 4
2022-06-29 06:00 | 6 | 4 | 1 | 2022-06-29 06:00 | 6 | 4
2022-06-29 07:00 | 7 | 4 | 1 | 2022-06-29 07:00 | 7 | 4
2022-06-29 08:00 | 8 | 4 | 1 | 2022-06-29 08:00 | 8 | 4
2022-06-29 09:00 | 9 | 4 | 1 | 2022-06-29 09:00 | 9 | 4
2022-06-29 10:00 | 10 | 4 | 1 | 2022-06-29 10:00 | 10 | 4
2022-06-29 11:00 | 11 | 4 | 1 | 2022-06-29 11:00 | 11 | 4
2022-06-29 12:00 | 12 | 4 | 1 | 2022-06-29 12:00 | 12 | 4
2022-06-29 13:00 | 13 | 4 | 1 | 2022-06-29 13:00 | 13 | 4
2022-06-29 14:00 | 14 | 4 | 1 | 2022-06-29 14:00 | 14 | 4
2022-06-29 15:00 | 15 | 4 | 1 | 2022-06-29 15:00 | 15 | 4
2022-06-29 16:00 | 16 | 4 | 1 | 2022-06-29 16:00 | 16 | 4
2022-06-29 17:00 | 17 | 4 | 1 | 2022-06-29 17:00 | 17 | 4
2022-06-29 18:00 | 18 | 4 | 1 | 2022-06-29 18:00 | 18 | 4
2022-06-29 19:00 | 19 | 4 | 1 | 2022-06-29 19:00 | 19 | 4
2022-06-29 20:00 | 20 | 4 | 1 | 2022-06-29 20:00 | 20 | 4
2022-06-29 21:00 | 21 | 4 | 1 | 2022-06-29 21:00 | 21 | 4
2022-06-29 22:00 | 22 | 4 | 1 | 2022-06-29 22:00 | 22 | 4
2022-06-29 23:00 | 23 | 4 | 1 | 2022-06-29 23:00 | 23 | 4
2022-06-30 | 0 | 5 | 1 | 2022-06-30 | 0 | 5
2022-06-30 01:00 | 1 | 5 | 1 | 2022-06-30 01:00 | 1 | 5
2022-06-30 02:00 | 2 | 5 | 1 | 2022-06-30 02:00 | 2 | 5
2022-06-30 03:00 | 3 | 5 | 1 | 2022-06-30 03:00 | 3 | 5
2022-06-30 04:00 | 4 | 5 | 1 | 2022-06-30 04:00 | 4 | 5
2022-06-30 05:00 | 5 | 5 | 1 | 2022-06-30 05:00 | 5 | 5
2022-06-30 06:00 | 6 | 5 | 1 | 2022-06-30 06:00 | 6 | 5
2022-06-30 07:00 | 7 | 5 | 1 | 2022-06-30 07:00 | 7 | 5
2022-06-30 08:00 | 8 | 5 | 1 | 2022-06-30 08:00 | 8 | 5
2022-06-30 09:00 | 9 | 5 | 1 | 2022-06-30 09:00 | 9 | 5
2022-06-30 10:00 | 10 | 5 | 1 | 2022-06-30 10:00 | 10 | 5
2022-06-30 11:00 | 11 | 5 | 1 | 2022-06-30 11:00 | 11 | 5
2022-06-30 12:00 | 12 | 5 | 1 | 2022-06-30 12:00 | 12 | 5
2022-06-30 13:00 | 13 | 5 | 1 | 2022-06-30 13:00 | 13 | 5
2022-06-30 14:00 | 14 | 5 | 1 | 2022-06-30 14:00 | 14 | 5
2022-06-30 15:00 | 15 | 5 | 1 | 2022-06-30 15:00 | 15 | 5
2022-06-30 16:00 | 16 | 5 | 1 | 2022-06-30 16:00 | 16 | 5
2022-06-30 17:00 | 17 | 5 | 1 | 2022-06-30 17:00 | 17 | 5
2022-06-30 18:00 | 18 | 5 | 1 | 2022-06-30 18:00 | 18 | 5
2022-06-30 19:00 | 19 | 5 | 1 | 2022-06-30 19:00 | 19 | 5
2022-06-30 20:00 | 20 | 5 | 1 | 2022-06-30 20:00 | 20 | 5
2022-06-30 21:00 | 21 | 5 | 1 | 2022-06-30 21:00 | 21 | 5
2022-06-30 22:00 | 22 | 5 | 1 | 2022-06-30 22:00 | 22 | 5
2022-06-30 23:00 | 23 | 5 | 1 | 2022-06-30 23:00 | 23 | 5
2022-07-01 | 0 | 6 | 1 | 2022-07-01 | 0 | 6
2022-07-01 01:00 | 1 | 6 | 1 | 2022-07-01 01:00 | 1 | 6
2022-07-01 02:00 | 2 | 6 | 1 | 2022-07-01 02:00 | 2 | 6
2022-07-01 03:00 | 3 | 6 | 1 | 2022-07-01 03:00 | 3 | 6
2022-07-01 04:00 | 4 | 6 | 1 | 2022-07-01 04:00 | 4 | 6
2022-07-01 05:00 | 5 | 6 | 1 | 2022-07-01 05:00 | 5 | 6
2022-07-01 06:00 | 6 | 6 | 1 | 2022-07-01 06:00 | 6 | 6
2022-07-01 07:00 | 7 | 6 | 1 | 2022-07-01 07:00 | 7 | 6
2022-07-01 08:00 | 8 | 6 | 1 | 2022-07-01 08:00 | 8 | 6
2022-07-01 09:00 | 9 | 6 | 1 | 2022-07-01 09:00 | 9 | 6
2022-07-01 10:00 | 10 | 6 | 1 | 2022-07-01 10:00 | 10 | 6
2022-07-01 11:00 | 11 | 6 | 1 | 2022-07-01 11:00 | 11 | 6
2022-07-01 12:00 | 12 | 6 | 1 | 2022-07-01 12:00 | 12 | 6
2022-07-01 13:00 | 13 | 6 | 1 | 2022-07-01 13:00 | 13 | 6
2022-07-01 14:00 | 14 | 6 | 1 | 2022-07-01 14:00 | 14 | 6
2022-07-01 15:00 | 15 | 6 | 1 | 2022-07-01 15:00 | 15 | 6
2022-07-01 16:00 | 16 | 6 | 1 | 2022-07-01 16:00 | 16 | 6
2022-07-01 17:00 | 17 | 6 | 1 | 2022-07-01 17:00 | 17 | 6
2022-07-01 18:00 | 18 | 6 | 1 | 2022-07-01 18:00 | 18 | 6
2022-07-01 19:00 | 19 | 6 | 1 | 2022-07-01 19:00 | 19 | 6
2022-07-01 20:00 | 20 | 6 | 1 | 2022-07-01 20:00 | 20 | 6
2022-07-01 21:00 | 21 | 6 | 1 | 2022-07-01 21:00 | 21 | 6
2022-07-01 22:00 | 22 | 6 | 1 | 2022-07-01 22:00 | 22 | 6
2022-07-01 23:00 | 23 | 6 | 1 | 2022-07-01 23:00 | 23 | 6
2022-07-02 | 0 | 7 | 1 | 2022-07-02 | 0 | 7
2022-07-02 01:00 | 1 | 7 | 1 | 2022-07-02 01:00 | 1 | 7
2022-07-02 02:00 | 2 | 7 | 1 | 2022-07-02 02:00 | 2 | 7
2022-07-02 03:00 | 3 | 7 | 1 | 2022-07-02 03:00 | 3 | 7
2022-07-02 04:00 | 4 | 7 | 1 | 2022-07-02 04:00 | 4 | 7
2022-07-02 05:00 | 5 | 7 | 1 | 2022-07-02 05:00 | 5 | 7
2022-07-02 06:00 | 6 | 7 | 1 | 2022-07-02 06:00 | 6 | 7
2022-07-02 07:00 | 7 | 7 | 1 | 2022-07-02 07:00 | 7 | 7
2022-07-02 08:00 | 8 | 7 | 1 | 2022-07-02 08:00 | 8 | 7
2022-07-02 09:00 | 9 | 7 | 1 | 2022-07-02 09:00 | 9 | 7
2022-07-02 10:00 | 10 | 7 | 1 | 2022-07-02 10:00 | 10 | 7
2022-07-02 11:00 | 11 | 7 | 1 | 2022-07-02 11:00 | 11 | 7
2022-07-02 12:00 | 12 | 7 | 1 | 2022-07-02 12:00 | 12 | 7
2022-07-02 13:00 | 13 | 7 | 1 | 2022-07-02 13:00 | 13 | 7
2022-07-02 14:00 | 14 | 7 | 1 | 2022-07-02 14:00 | 14 | 7
2022-07-02 15:00 | 15 | 7 | 1 | 2022-07-02 15:00 | 15 | 7
2022-07-02 16:00 | 16 | 7 | 1 | 2022-07-02 16:00 | 16 | 7
2022-07-02 17:00 | 17 | 7 | 1 | 2022-07-02 17:00 | 17 | 7
2022-07-02 18:00 | 18 | 7 | 1 | 2022-07-02 18:00 | 18 | 7
2022-07-02 19:00 | 19 | 7 | 1 | 2022-07-02 19:00 | 19 | 7
2022-07-02 20:00 | 20 | 7 | 1 | 2022-07-02 20:00 | 20 | 7
2022-07-02 21:00 | 21 | 7 | 1 | 2022-07-02 21:00 | 21 | 7
2022-07-02 22:00 | 22 | 7 | 1 | 2022-07-02 22:00 | 22 | 7
2022-07-02 23:00 | 23 | 7 | 1 | 2022-07-02 23:00 | 23 | 7
2022-07-03 | 0 | 1 | 1 | 2022-07-03 | 0 | 1
2022-07-03 01:00 | 1 | 1 | 1 | 2022-07-03 01:00 | 1 | 1
2022-07-03 02:00 | 2 | 1 | 1 | 2022-07-03 02:00 | 2 | 1
2022-07-03 03:00 | 3 | 1 | 1 | 2022-07-03 03:00 | 3 | 1
2022-07-03 04:00 | 4 | 1 | 1 | 2022-07-03 04:00 | 4 | 1
2022-07-03 05:00 | 5 | 1 | 1 | 2022-07-03 05:00 | 5 | 1
2022-07-03 06:00 | 6 | 1 | 1 | 2022-07-03 06:00 | 6 | 1
2022-07-03 07:00 | 7 | 1 | 1 | 2022-07-03 07:00 | 7 | 1
2022-07-03 08:00 | 8 | 1 | 1 | 2022-07-03 08:00 | 8 | 1
2022-07-03 09:00 | 9 | 1 | 1 | 2022-07-03 09:00 | 9 | 1
2022-07-03 10:00 | 10 | 1 | 1 | 2022-07-03 10:00 | 10 | 1
2022-07-03 11:00 | 11 | 1 | 1 | 2022-07-03 11:00 | 11 | 1
2022-07-03 12:00 | 12 | 1 | 1 | 2022-07-03 12:00 | 12 | 1
2022-07-03 13:00 | 13 | 1 | 1 | 2022-07-03 13:00 | 13 | 1
2022-07-03 14:00 | 14 | 1 | 1 | 2022-07-03 14:00 | 14 | 1
2022-07-03 15:00 | 15 | 1 | 1 | 2022-07-03 15:00 | 15 | 1
2022-07-03 16:00 | 16 | 1 | 1 | 2022-07-03 16:00 | 16 | 1
2022-07-03 17:00 | 17 | 1 | 1 | 2022-07-03 17:00 | 17 | 1
2022-07-03 18:00 | 18 | 1 | 1 | 2022-07-03 18:00 | 18 | 1
2022-07-03 19:00 | 19 | 1 | 1 | 2022-07-03 19:00 | 19 | 1
2022-07-03 20:00 | 20 | 1 | 1 | 2022-07-03 20:00 | 20 | 1
2022-07-03 21:00 | 21 | 1 | 1 | 2022-07-03 21:00 | 21 | 1
2022-07-03 22:00 | 22 | 1 | 1 | 2022-07-03 22:00 | 22 | 1
2022-07-03 23:00 | 23 | 1 | 1 | 2022-07-03 23:00 | 23 | 1
2022-07-04 | 0 | 2 | 1 | 2022-07-04 | 0 | 2
2022-07-04 01:00 | 1 | 2 | 1 | 2022-07-04 01:00 | 1 | 2
2022-07-04 02:00 | 2 | 2 | 1 | 2022-07-04 02:00 | 2 | 2
2022-07-04 03:00 | 3 | 2 | 1 | 2022-07-04 03:00 | 3 | 2
2022-07-04 04:00 | 4 | 2 | 1 | 2022-07-04 04:00 | 4 | 2
2022-07-04 05:00 | 5 | 2 | 1 | 2022-07-04 05:00 | 5 | 2
2022-07-04 06:00 | 6 | 2 | 1 | 2022-07-04 06:00 | 6 | 2
2022-07-04 07:00 | 7 | 2 | 1 | 2022-07-04 07:00 | 7 | 2
2022-07-04 08:00 | 8 | 2 | 1 | 2022-07-04 08:00 | 8 | 2
2022-07-04 09:00 | 9 | 2 | 1 | 2022-07-04 09:00 | 9 | 2
2022-07-04 10:00 | 10 | 2 | 1 | 2022-07-04 10:00 | 10 | 2
2022-07-04 11:00 | 11 | 2 | 1 | 2022-07-04 11:00 | 11 | 2
2022-07-04 12:00 | 12 | 2 | 1 | 2022-07-04 12:00 | 12 | 2
2022-07-04 13:00 | 13 | 2 | 1 | 2022-07-04 13:00 | 13 | 2
2022-07-04 14:00 | 14 | 2 | 1 | 2022-07-04 14:00 | 14 | 2
2022-07-04 15:00 | 15 | 2 | 1 | 2022-07-04 15:00 | 15 | 2
2022-07-04 16:00 | 16 | 2 | 1 | 2022-07-04 16:00 | 16 | 2
2022-07-04 17:00 | 17 | 2 | 1 | 2022-07-04 17:00 | 17 | 2
2022-07-04 18:00 | 18 | 2 | 1 | 2022-07-04 18:00 | 18 | 2
2022-07-04 19:00 | 19 | 2 | 1 | 2022-07-04 19:00 | 19 | 2
2022-07-04 20:00 | 20 | 2 | 1 | 2022-07-04 20:00 | 20 | 2
2022-07-04 21:00 | 21 | 2 | 1 | 2022-07-04 21:00 | 21 | 2
2022-07-04 22:00 | 22 | 2 | 1 | 2022-07-04 22:00 | 22 | 2
2022-07-04 23:00 | 23 | 2 | 1 | 2022-07-04 23:00 | 23 | 2
2022-07-05 | 0 | 3 | 1 | 2022-07-05 | 0 | 3
2022-07-05 01:00 | 1 | 3 | 1 | 2022-07-05 01:00 | 1 | 3
2022-07-05 02:00 | 2 | 3 | 1 | 2022-07-05 02:00 | 2 | 3
2022-07-05 03:00 | 3 | 3 | 1 | 2022-07-05 03:00 | 3 | 3
2022-07-05 04:00 | 4 | 3 | 1 | 2022-07-05 04:00 | 4 | 3
2022-07-05 05:00 | 5 | 3 | 1 | 2022-07-05 05:00 | 5 | 3
2022-07-05 06:00 | 6 | 3 | 1 | 2022-07-05 06:00 | 6 | 3
2022-07-05 07:00 | 7 | 3 | 1 | 2022-07-05 07:00 | 7 | 3
2022-07-05 08:00 | 8 | 3 | 1 | 2022-07-05 08:00 | 8 | 3
2022-07-05 09:00 | 9 | 3 | 1 | 2022-07-05 09:00 | 9 | 3
2022-07-05 10:00 | 10 | 3 | 1 | 2022-07-05 10:00 | 10 | 3
2022-07-05 11:00 | 11 | 3 | 1 | 2022-07-05 11:00 | 11 | 3
2022-07-05 12:00 | 12 | 3 | 1 | 2022-07-05 12:00 | 12 | 3
2022-07-05 13:00 | 13 | 3 | 1 | 2022-07-05 13:00 | 13 | 3
2022-07-05 14:00 | 14 | 3 | 1 | 2022-07-05 14:00 | 14 | 3
2022-07-05 15:00 | 15 | 3 | 1 | 2022-07-05 15:00 | 15 | 3
2022-07-05 16:00 | 16 | 3 | 1 | 2022-07-05 16:00 | 16 | 3
2022-07-05 17:00 | 17 | 3 | 1 | 2022-07-05 17:00 | 17 | 3
2022-07-05 18:00 | 18 | 3 | 1 | 2022-07-05 18:00 | 18 | 3
2022-07-05 19:00 | 19 | 3 | 1 | 2022-07-05 19:00 | 19 | 3
2022-07-05 20:00 | 20 | 3 | 1 | 2022-07-05 20:00 | 20 | 3
2022-07-05 21:00 | 21 | 3 | 1 | 2022-07-05 21:00 | 21 | 3
2022-07-05 22:00 | 22 | 3 | 1 | 2022-07-05 22:00 | 22 | 3
2022-07-05 23:00 | 23 | 3 | 1 | 2022-07-05 23:00 | 23 | 3
2022-07-06 | 0 | 4 | 1 | 2022-07-06 | 0 | 4
2022-07-06 01:00 | 1 | 4 | 1 | 2022-07-06 01:00 | 1 | 4
2022-07-06 02:00 | 2 | 4 | 1 | 2022-07-06 02:00 | 2 | 4
2022-07-06 03:00 | 3 | 4 | 1 | 2022-07-06 03:00 | 3 | 4
2022-07-06 04:00 | 4 | 4 | 1 | 2022-07-06 04:00 | 4 | 4
2022-07-06 05:00 | 5 | 4 | 1 | 2022-07-06 05:00 | 5 | 4
2022-07-06 06:00 | 6 | 4 | 1 | 2022-07-06 06:00 | 6 | 4
2022-07-06 07:00 | 7 | 4 | 1 | 2022-07-06 07:00 | 7 | 4
2022-07-06 08:00 | 8 | 4 | 1 | 2022-07-06 08:00 | 8 | 4
2022-07-06 09:00 | 9 | 4 | 1 | 2022-07-06 09:00 | 9 | 4
2022-07-06 10:00 | 10 | 4 | 1 | 2022-07-06 10:00 | 10 | 4
2022-07-06 11:00 | 11 | 4 | 1 | 2022-07-06 11:00 | 11 | 4
2022-07-06 12:00 | 12 | 4 | 1 | 2022-07-06 12:00 | 12 | 4
2022-07-06 13:00 | 13 | 4 | 1 | 2022-07-06 13:00 | 13 | 4
2022-07-06 14:00 | 14 | 4 | 1 | 2022-07-06 14:00 | 14 | 4
2022-07-06 15:00 | 15 | 4 | 1 | 2022-07-06 15:00 | 15 | 4
2022-07-06 16:00 | 16 | 4 | 1 | 2022-07-06 16:00 | 16 | 4
2022-07-06 17:00 | 17 | 4 | 1 | 2022-07-06 17:00 | 17 | 4
2022-07-06 18:00 | 18 | 4 | 1 | 2022-07-06 18:00 | 18 | 4
2022-07-06 19:00 | 19 | 4 | 1 | 2022-07-06 19:00 | 19 | 4
2022-07-06 20:00 | 20 | 4 | 1 | 2022-07-06 20:00 | 20 | 4
2022-07-06 21:00 | 21 | 4 | 1 | 2022-07-06 21:00 | 21 | 4
2022-07-06 22:00 | 22 | 4 | 1 | 2022-07-06 22:00 | 22 | 4
2022-07-06 23:00 | 23 | 4 | 1 | 2022-07-06 23:00 | 23 | 4
2022-07-07 | 0 | 5 | 1 | 2022-07-07 | 0 | 5
2022-07-07 01:00 | 1 | 5 | 1 | 2022-07-07 01:00 | 1 | 5
2022-07-07 02:00 | 2 | 5 | 1 | 2022-07-07 02:00 | 2 | 5
2022-07-07 03:00 | 3 | 5 | 1 | 2022-07-07 03:00 | 3 | 5
2022-07-07 04:00 | 4 | 5 | 1 | 2022-07-07 04:00 | 4 | 5
2022-07-07 05:00 | 5 | 5 | 1 | 2022-07-07 05:00 | 5 | 5
2022-07-07 06:00 | 6 | 5 | 1 | 2022-07-07 06:00 | 6 | 5
2022-07-07 07:00 | 7 | 5 | 1 | 2022-07-07 07:00 | 7 | 5
2022-07-07 08:00 | 8 | 5 | 1 | 2022-07-07 08:00 | 8 | 5
2022-07-07 09:00 | 9 | 5 | 1 | 2022-07-07 09:00 | 9 | 5
2022-07-07 10:00 | 10 | 5 | 1 | 2022-07-07 10:00 | 10 | 5
2022-07-07 11:00 | 11 | 5 | 1 | 2022-07-07 11:00 | 11 | 5
2022-07-07 12:00 | 12 | 5 | 1 | 2022-07-07 12:00 | 12 | 5
2022-07-07 13:00 | 13 | 5 | 1 | 2022-07-07 13:00 | 13 | 5
2022-07-07 14:00 | 14 | 5 | 1 | 2022-07-07 14:00 | 14 | 5
2022-07-07 15:00 | 15 | 5 | 1 | 2022-07-07 15:00 | 15 | 5
2022-07-07 16:00 | 16 | 5 | 1 | 2022-07-07 16:00 | 16 | 5
2022-07-07 17:00 | 17 | 5 | 1 | 2022-07-07 17:00 | 17 | 5
2022-07-07 18:00 | 18 | 5 | 1 | 2022-07-07 18:00 | 18 | 5
2022-07-07 19:00 | 19 | 5 | 1 | 2022-07-07 19:00 | 19 | 5
2022-07-07 20:00 | 20 | 5 | 1 | 2022-07-07 20:00 | 20 | 5
2022-07-07 21:00 | 21 | 5 | 1 | 2022-07-07 21:00 | 21 | 5
2022-07-07 22:00 | 22 | 5 | 1 | 2022-07-07 22:00 | 22 | 5
2022-07-07 23:00 | 23 | 5 | 1 | 2022-07-07 23:00 | 23 | 5
2022-07-08 | 0 | 6 | 1 | 2022-07-08 | 0 | 6
2022-07-08 01:00 | 1 | 6 | 1 | 2022-07-08 01:00 | 1 | 6
2022-07-08 02:00 | 2 | 6 | 1 | 2022-07-08 02:00 | 2 | 6
2022-07-08 03:00 | 3 | 6 | 1 | 2022-07-08 03:00 | 3 | 6
2022-07-08 04:00 | 4 | 6 | 1 | 2022-07-08 04:00 | 4 | 6
2022-07-08 05:00 | 5 | 6 | 1 | 2022-07-08 05:00 | 5 | 6
2022-07-08 06:00 | 6 | 6 | 1 | 2022-07-08 06:00 | 6 | 6
2022-07-08 07:00 | 7 | 6 | 1 | 2022-07-08 07:00 | 7 | 6
2022-07-08 08:00 | 8 | 6 | 1 | 2022-07-08 08:00 | 8 | 6
2022-07-08 09:00 | 9 | 6 | 1 | 2022-07-08 09:00 | 9 | 6
2022-07-08 10:00 | 10 | 6 | 1 | 2022-07-08 10:00 | 10 | 6
2022-07-08 11:00 | 11 | 6 | 1 | 2022-07-08 11:00 | 11 | 6
2022-07-08 12:00 | 12 | 6 | 1 | 2022-07-08 12:00 | 12 | 6
2022-07-08 13:00 | 13 | 6 | 1 | 2022-07-08 13:00 | 13 | 6
2022-07-08 14:00 | 14 | 6 | 1 | 2022-07-08 14:00 | 14 | 6
2022-07-08 15:00 | 15 | 6 | 1 | 2022-07-08 15:00 | 15 | 6
2022-07-08 16:00 | 16 | 6 | 1 | 2022-07-08 16:00 | 16 | 6
2022-07-08 17:00 | 17 | 6 | 1 | 2022-07-08 17:00 | 17 | 6
2022-07-08 18:00 | 18 | 6 | 1 | 2022-07-08 18:00 | 18 | 6
2022-07-08 19:00 | 19 | 6 | 1 | 2022-07-08 19:00 | 19 | 6
2022-07-08 20:00 | 20 | 6 | 1 | 2022-07-08 20:00 | 20 | 6
2022-07-08 21:00 | 21 | 6 | 1 | 2022-07-08 21:00 | 21 | 6
2022-07-08 22:00 | 22 | 6 | 1 | 2022-07-08 22:00 | 22 | 6
2022-07-08 23:00 | 23 | 6 | 1 | 2022-07-08 23:00 | 23 | 6
2022-07-09 | 0 | 7 | 1 | 2022-07-09 | 0 | 7
2022-07-09 01:00 | 1 | 7 | 1 | 2022-07-09 01:00 | 1 | 7
2022-07-09 02:00 | 2 | 7 | 1 | 2022-07-09 02:00 | 2 | 7
2022-07-09 03:00 | 3 | 7 | 1 | 2022-07-09 03:00 | 3 | 7
2022-07-09 04:00 | 4 | 7 | 1 | 2022-07-09 04:00 | 4 | 7
2022-07-09 05:00 | 5 | 7 | 1 | 2022-07-09 05:00 | 5 | 7
2022-07-09 06:00 | 6 | 7 | 1 | 2022-07-09 06:00 | 6 | 7
2022-07-09 07:00 | 7 | 7 | 1 | 2022-07-09 07:00 | 7 | 7
2022-07-09 08:00 | 8 | 7 | 1 | 2022-07-09 08:00 | 8 | 7
2022-07-09 09:00 | 9 | 7 | 1 | 2022-07-09 09:00 | 9 | 7
2022-07-09 10:00 | 10 | 7 | 1 | 2022-07-09 10:00 | 10 | 7
2022-07-09 11:00 | 11 | 7 | 1 | 2022-07-09 11:00 | 11 | 7
2022-07-09 12:00 | 12 | 7 | 1 | 2022-07-09 12:00 | 12 | 7
2022-07-09 13:00 | 13 | 7 | 1 | 2022-07-09 13:00 | 13 | 7
2022-07-09 14:00 | 14 | 7 | 1 | 2022-07-09 14:00 | 14 | 7
2022-07-09 15:00 | 15 | 7 | 1 | 2022-07-09 15:00 | 15 | 7
2022-07-09 16:00 | 16 | 7 | 1 | 2022-07-09 16:00 | 16 | 7
2022-07-09 17:00 | 17 | 7 | 1 | 2022-07-09 17:00 | 17 | 7
2022-07-09 18:00 | 18 | 7 | 1 | 2022-07-09 18:00 | 18 | 7
2022-07-09 19:00 | 19 | 7 | 1 | 2022-07-09 19:00 | 19 | 7
2022-07-09 20:00 | 20 | 7 | 1 | 2022-07-09 20:00 | 20 | 7
2022-07-09 21:00 | 21 | 7 | 1 | 2022-07-09 21:00 | 21 | 7
2022-07-09 22:00 | 22 | 7 | 1 | 2022-07-09 22:00 | 22 | 7
2022-07-09 23:00 | 23 | 7 | 1 | 2022-07-09 23:00 | 23 | 7
2022-07-10 | 0 | 1 | 1 | 2022-07-10 | 0 | 1
2022-07-10 01:00 | 1 | 1 | 1 | 2022-07-10 01:00 | 1 | 1
2022-07-10 02:00 | 2 | 1 | 1 | 2022-07-10 02:00 | 2 | 1
2022-07-10 03:00 | 3 | 1 | 1 | 2022-07-10 03:00 | 3 | 1
2022-07-10 04:00 | 4 | 1 | 1 | 2022-07-10 04:00 | 4 | 1
2022-07-10 05:00 | 5 | 1 | 1 | 2022-07-10 05:00 | 5 | 1
2022-07-10 06:00 | 6 | 1 | 1 | 2022-07-10 06:00 | 6 | 1
2022-07-10 07:00 | 7 | 1 | 1 | 2022-07-10 07:00 | 7 | 1
2022-07-10 08:00 | 8 | 1 | 1 | 2022-07-10 08:00 | 8 | 1
2022-07-10 09:00 | 9 | 1 | 1 | 2022-07-10 09:00 | 9 | 1
2022-07-10 10:00 | 10 | 1 | 1 | 2022-07-10 10:00 | 10 | 1
2022-07-10 11:00 | 11 | 1 | 1 | 2022-07-10 11:00 | 11 | 1
2022-07-10 12:00 | 12 | 1 | 1 | 2022-07-10 12:00 | 12 | 1
2022-07-10 13:00 | 13 | 1 | 1 | 2022-07-10 13:00 | 13 | 1
2022-07-10 14:00 | 14 | 1 | 1 | 2022-07-10 14:00 | 14 | 1
2022-07-10 15:00 | 15 | 1 | 1 | 2022-07-10 15:00 | 15 | 1
2022-07-10 16:00 | 16 | 1 | 1 | 2022-07-10 16:00 | 16 | 1
2022-07-10 17:00 | 17 | 1 | 1 | 2022-07-10 17:00 | 17 | 1
2022-07-10 18:00 | 18 | 1 | 1 | 2022-07-10 18:00 | 18 | 1
2022-07-10 19:00 | 19 | 1 | 1 | 2022-07-10 19:00 | 19 | 1
2022-07-10 20:00 | 20 | 1 | 1 | 2022-07-10 20:00 | 20 | 1
2022-07-10 21:00 | 21 | 1 | 1 | 2022-07-10 21:00 | 21 | 1
2022-07-10 22:00 | 22 | 1 | 1 | 2022-07-10 22:00 | 22 | 1
2022-07-10 23:00 | 23 | 1 | 1 | 2022-07-10 23:00 | 23 | 1
2022-07-11 | 0 | 2 | 1 | 2022-07-11 | 0 | 2
2022-07-11 01:00 | 1 | 2 | 1 | 2022-07-11 01:00 | 1 | 2
2022-07-11 02:00 | 2 | 2 | 1 | 2022-07-11 02:00 | 2 | 2
2022-07-11 03:00 | 3 | 2 | 1 | 2022-07-11 03:00 | 3 | 2
2022-07-11 04:00 | 4 | 2 | 1 | 2022-07-11 04:00 | 4 | 2
2022-07-11 05:00 | 5 | 2 | 1 | 2022-07-11 05:00 | 5 | 2
2022-07-11 06:00 | 6 | 2 | 1 | 2022-07-11 06:00 | 6 | 2
2022-07-11 07:00 | 7 | 2 | 1 | 2022-07-11 07:00 | 7 | 2
2022-07-11 08:00 | 8 | 2 | 1 | 2022-07-11 08:00 | 8 | 2
2022-07-11 09:00 | 9 | 2 | 1 | 2022-07-11 09:00 | 9 | 2
2022-07-11 10:00 | 10 | 2 | 1 | 2022-07-11 10:00 | 10 | 2
2022-07-11 11:00 | 11 | 2 | 1 | 2022-07-11 11:00 | 11 | 2
2022-07-11 12:00 | 12 | 2 | 1 | 2022-07-11 12:00 | 12 | 2
2022-07-11 13:00 | 13 | 2 | 1 | 2022-07-11 13:00 | 13 | 2
2022-07-11 14:00 | 14 | 2 | 1 | 2022-07-11 14:00 | 14 | 2
2022-07-11 15:00 | 15 | 2 | 1 | 2022-07-11 15:00 | 15 | 2
2022-07-11 16:00 | 16 | 2 | 1 | 2022-07-11 16:00 | 16 | 2
2022-07-11 17:00 | 17 | 2 | 1 | 2022-07-11 17:00 | 17 | 2
2022-07-11 18:00 | 18 | 2 | 1 | 2022-07-11 18:00 | 18 | 2
2022-07-11 19:00 | 19 | 2 | 1 | 2022-07-11 19:00 | 19 | 2
2022-07-11 20:00 | 20 | 2 | 1 | 2022-07-11 20:00 | 20 | 2
2022-07-11 21:00 | 21 | 2 | 1 | 2022-07-11 21:00 | 21 | 2
2022-07-11 22:00 | 22 | 2 | 1 | 2022-07-11 22:00 | 22 | 2
2022-07-11 23:00 | 23 | 2 | 1 | 2022-07-11 23:00 | 23 | 2
2022-07-12 | 0 | 3 | 1 | 2022-07-12 | 0 | 3
2022-07-12 01:00 | 1 | 3 | 1 | 2022-07-12 01:00 | 1 | 3
2022-07-12 02:00 | 2 | 3 | 1 | 2022-07-12 02:00 | 2 | 3
2022-07-12 03:00 | 3 | 3 | 1 | 2022-07-12 03:00 | 3 | 3
2022-07-12 04:00 | 4 | 3 | 1 | 2022-07-12 04:00 | 4 | 3
2022-07-12 05:00 | 5 | 3 | 1 | 2022-07-12 05:00 | 5 | 3
2022-07-12 06:00 | 6 | 3 | 1 | 2022-07-12 06:00 | 6 | 3
2022-07-12 07:00 | 7 | 3 | 1 | 2022-07-12 07:00 | 7 | 3
2022-07-12 08:00 | 8 | 3 | 1 | 2022-07-12 08:00 | 8 | 3
2022-07-12 09:00 | 9 | 3 | 1 | 2022-07-12 09:00 | 9 | 3
2022-07-12 10:00 | 10 | 3 | 1 | 2022-07-12 10:00 | 10 | 3
2022-07-12 11:00 | 11 | 3 | 1 | 2022-07-12 11:00 | 11 | 3
2022-07-12 12:00 | 12 | 3 | 1 | 2022-07-12 12:00 | 12 | 3
2022-07-12 13:00 | 13 | 3 | 1 | 2022-07-12 13:00 | 13 | 3
2022-07-12 14:00 | 14 | 3 | 1 | 2022-07-12 14:00 | 14 | 3
2022-07-12 15:00 | 15 | 3 | 1 | 2022-07-12 15:00 | 15 | 3
2022-07-12 16:00 | 16 | 3 | 1 | 2022-07-12 16:00 | 16 | 3
2022-07-12 17:00 | 17 | 3 | 1 | 2022-07-12 17:00 | 17 | 3
2022-07-12 18:00 | 18 | 3 | 1 | 2022-07-12 18:00 | 18 | 3
2022-07-12 19:00 | 19 | 3 | 1 | 2022-07-12 19:00 | 19 | 3
2022-07-12 20:00 | 20 | 3 | 1 | 2022-07-12 20:00 | 20 | 3
2022-07-12 21:00 | 21 | 3 | 1 | 2022-07-12 21:00 | 21 | 3
2022-07-12 22:00 | 22 | 3 | 1 | 2022-07-12 22:00 | 22 | 3
2022-07-12 23:00 | 23 | 3 | 1 | 2022-07-12 23:00 | 23 | 3
2022-07-13 | 0 | 4 | 1 | 2022-07-13 | 0 | 4
2022-07-13 01:00 | 1 | 4 | 1 | 2022-07-13 01:00 | 1 | 4
2022-07-13 02:00 | 2 | 4 | 1 | 2022-07-13 02:00 | 2 | 4
2022-07-13 03:00 | 3 | 4 | 1 | 2022-07-13 03:00 | 3 | 4
2022-07-13 04:00 | 4 | 4 | 1 | 2022-07-13 04:00 | 4 | 4
2022-07-13 05:00 | 5 | 4 | 1 | 2022-07-13 05:00 | 5 | 4
2022-07-13 06:00 | 6 | 4 | 1 | 2022-07-13 06:00 | 6 | 4
2022-07-13 07:00 | 7 | 4 | 1 | 2022-07-13 07:00 | 7 | 4
2022-07-13 08:00 | 8 | 4 | 1 | 2022-07-13 08:00 | 8 | 4
2022-07-13 09:00 | 9 | 4 | 1 | 2022-07-13 09:00 | 9 | 4
2022-07-13 10:00 | 10 | 4 | 1 | 2022-07-13 10:00 | 10 | 4
2022-07-13 11:00 | 11 | 4 | 1 | 2022-07-13 11:00 | 11 | 4
2022-07-13 12:00 | 12 | 4 | 1 | 2022-07-13 12:00 | 12 | 4
2022-07-13 13:00 | 13 | 4 | 1 | 2022-07-13 13:00 | 13 | 4
2022-07-13 14:00 | 14 | 4 | 1 | 2022-07-13 14:00 | 14 | 4
2022-07-13 15:00 | 15 | 4 | 1 | 2022-07-13 15:00 | 15 | 4
2022-07-13 16:00 | 16 | 4 | 1 | 2022-07-13 16:00 | 16 | 4
2022-07-13 17:00 | 17 | 4 | 1 | 2022-07-13 17:00 | 17 | 4
2022-07-13 18:00 | 18 | 4 | 1 | 2022-07-13 18:00 | 18 | 4
2022-07-13 19:00 | 19 | 4 | 1 | 2022-07-13 19:00 | 19 | 4
2022-07-13 20:00 | 20 | 4 | 1 | 2022-07-13 20:00 | 20 | 4
2022-07-13 21:00 | 21 | 4 | 1 | 2022-07-13 21:00 | 21 | 4
2022-07-13 22:00 | 22 | 4 | 1 | 2022-07-13 22:00 | 22 | 4
2022-07-13 23:00 | 23 | 4 | 1 | 2022-07-13 23:00 | 23 | 4
2022-07-14 | 0 | 5 | 1 | 2022-07-14 | 0 | 5
2022-07-14 01:00 | 1 | 5 | 1 | 2022-07-14 01:00 | 1 | 5
2022-07-14 02:00 | 2 | 5 | 1 | 2022-07-14 02:00 | 2 | 5
2022-07-14 03:00 | 3 | 5 | 1 | 2022-07-14 03:00 | 3 | 5
2022-07-14 04:00 | 4 | 5 | 1 | 2022-07-14 04:00 | 4 | 5
2022-07-14 05:00 | 5 | 5 | 1 | 2022-07-14 05:00 | 5 | 5
2022-07-14 06:00 | 6 | 5 | 1 | 2022-07-14 06:00 | 6 | 5
2022-07-14 07:00 | 7 | 5 | 1 | 2022-07-14 07:00 | 7 | 5
2022-07-14 08:00 | 8 | 5 | 1 | 2022-07-14 08:00 | 8 | 5

## Step 5. Daily Avg Schedule Calc
Day of Week | Hour of Day | Supply Fan Average On/Off | Return Fan Average On/Off
1 | 0 | 1 | 1
1 | 1 | 1 | 1
1 | 2 | 1 | 1
1 | 3 | 1 | 1
1 | 4 | 1 | 1
1 | 5 | 1 | 1
1 | 6 | 1 | 1
1 | 7 | 1 | 1
1 | 8 | 1 | 1
1 | 9 | 1 | 1
1 | 10 | 1 | 1
1 | 11 | 1 | 1
1 | 12 | 1 | 1
1 | 13 | 1 | 1
1 | 14 | 1 | 1
1 | 15 | 1 | 1
1 | 16 | 1 | 1
1 | 17 | 1 | 1
1 | 18 | 1 | 1
1 | 19 | 1 | 1
1 | 20 | 1 | 1
1 | 21 | 1 | 1
1 | 22 | 1 | 1
1 | 23 | 1 | 1
2 | 0 | 1 | 1
2 | 1 | 1 | 1
2 | 2 | 1 | 1
2 | 3 | 1 | 1
2 | 4 | 1 | 1
2 | 5 | 1 | 1
2 | 6 | 1 | 1
2 | 7 | 1 | 1
2 | 8 | 1 | 1
2 | 9 | 1 | 1
2 | 10 | 1 | 1
2 | 11 | 1 | 1
2 | 12 | 1 | 1
2 | 13 | 1 | 1
2 | 14 | 1 | 1
2 | 15 | 1 | 1
2 | 16 | 1 | 1
2 | 17 | 1 | 1
2 | 18 | 1 | 1
2 | 19 | 1 | 1
2 | 20 | 1 | 1
2 | 21 | 1 | 1
2 | 22 | 1 | 1
2 | 23 | 1 | 1
3 | 0 | 1 | 1
3 | 1 | 1 | 1
3 | 2 | 1 | 1
3 | 3 | 1 | 1
3 | 4 | 1 | 1
3 | 5 | 1 | 1
3 | 6 | 1 | 1
3 | 7 | 1 | 1
3 | 8 | 1 | 1
3 | 9 | 1 | 1
3 | 10 | 1 | 1
3 | 11 | 1 | 1
3 | 12 | 1 | 1
3 | 13 | 1 | 1
3 | 14 | 1 | 1
3 | 15 | 1 | 1
3 | 16 | 1 | 1
3 | 17 | 1 | 1
3 | 18 | 1 | 1
3 | 19 | 1 | 1
3 | 20 | 1 | 1
3 | 21 | 1 | 1
3 | 22 | 1 | 1
3 | 23 | 1 | 1
4 | 0 | 1 | 1
4 | 1 | 1 | 1
4 | 2 | 1 | 1
4 | 3 | 1 | 1
4 | 4 | 1 | 1
4 | 5 | 1 | 1
4 | 6 | 1 | 1
4 | 7 | 1 | 1
4 | 8 | 1 | 1
4 | 9 | 1 | 1
4 | 10 | 1 | 1
4 | 11 | 1 | 1
4 | 12 | 1 | 1
4 | 13 | 1 | 1
4 | 14 | 1 | 1
4 | 15 | 1 | 1
4 | 16 | 1 | 1
4 | 17 | 1 | 1
4 | 18 | 1 | 1
4 | 19 | 1 | 1
4 | 20 | 1 | 1
4 | 21 | 1 | 1
4 | 22 | 1 | 1
4 | 23 | 1 | 1
5 | 0 | 1 | 1
5 | 1 | 1 | 1
5 | 2 | 1 | 1
5 | 3 | 1 | 1
5 | 4 | 1 | 1
5 | 5 | 1 | 1
5 | 6 | 1 | 1
5 | 7 | 1 | 1
5 | 8 | 1 | 1
5 | 9 | 1 | 1
5 | 10 | 1 | 1
5 | 11 | 1 | 1
5 | 12 | 1 | 1
5 | 13 | 1 | 1
5 | 14 | 1 | 1
5 | 15 | 1 | 1
5 | 16 | 1 | 1
5 | 17 | 1 | 1
5 | 18 | 1 | 1
5 | 19 | 1 | 1
5 | 20 | 1 | 1
5 | 21 | 1 | 1
5 | 22 | 1 | 1
5 | 23 | 1 | 1
6 | 0 | 1 | 1
6 | 1 | 1 | 1
6 | 2 | 1 | 1
6 | 3 | 1 | 1
6 | 4 | 1 | 1
6 | 5 | 1 | 1
6 | 6 | 1 | 1
6 | 7 | 1 | 1
6 | 8 | 1 | 1
6 | 9 | 1 | 1
6 | 10 | 1 | 1
6 | 11 | 1 | 1
6 | 12 | 1 | 1
6 | 13 | 1 | 1
6 | 14 | 1 | 1
6 | 15 | 1 | 1
6 | 16 | 1 | 1
6 | 17 | 1 | 1
6 | 18 | 1 | 1
6 | 19 | 1 | 1
6 | 20 | 1 | 1
6 | 21 | 1 | 1
6 | 22 | 1 | 1
6 | 23 | 1 | 1
7 | 0 | 1 | 1
7 | 1 | 1 | 1
7 | 2 | 1 | 1
7 | 3 | 1 | 1
7 | 4 | 1 | 1
7 | 5 | 1 | 1
7 | 6 | 1 | 1
7 | 7 | 1 | 1
7 | 8 | 1 | 1
7 | 9 | 1 | 1
7 | 10 | 1 | 1
7 | 11 | 1 | 1
7 | 12 | 1 | 1
7 | 13 | 1 | 1
7 | 14 | 1 | 1
7 | 15 | 1 | 1
7 | 16 | 1 | 1
7 | 17 | 1 | 1
7 | 18 | 1 | 1
7 | 19 | 1 | 1
7 | 20 | 1 | 1
7 | 21 | 1 | 1
7 | 22 | 1 | 1
7 | 23 | 1 | 1

## Step 6. Energy Calcs
Datetime | Day of Year | Supply Fan Avg On/Off | Return Fan Avg On/Off | Normalized OAT | Supply Fan Energy (kWh) | Return Fan Energy (kWh) | Date | Supply Fan Daily Energy | Return Fan Daily Energy
2018-01-01 | 0 | 1 | 1 | 10 | 10.8423 | 4.353 | 2018-01-01 | 240.9785 | 99.0852
2018-01-01 01:00 | 0 | 1 | 1 | 10 | 10.8423 | 4.353 | 2018-01-02 | 214.1585 | 91.5408
2018-01-01 02:00 | 0 | 1 | 1 | 10 | 10.8423 | 4.353 | 2018-01-03 | 195.8985 | 86.3427
2018-01-01 03:00 | 0 | 1 | 1 | 9 | 11.0769 | 4.4181 | 2018-01-04 | 189.0285 | 84.3973
2018-01-01 04:00 | 0 | 1 | 1 | 9 | 11.0769 | 4.4181 | 2018-01-05 | 236.7532 | 97.9165
2018-01-01 05:00 | 0 | 1 | 1 | 9 | 11.0769 | 4.4181 | 2018-01-06 | 255.5458 | 103.1695
2018-01-01 06:00 | 0 | 1 | 1 | 8 | 11.3163 | 4.4845 | 2018-01-07 | 246.9125 | 100.7368
2018-01-01 07:00 | 0 | 1 | 1 | 8 | 11.3163 | 4.4845 | 2018-01-08 | 191.6093 | 85.0972
2018-01-01 08:00 | 0 | 1 | 1 | 9 | 11.0769 | 4.4181 | 2018-01-09 | 154.0574 | 74.0856
2018-01-01 09:00 | 0 | 1 | 1 | 10 | 10.8423 | 4.353 | 2018-01-10 | 159.3644 | 75.6918
2018-01-01 10:00 | 0 | 1 | 1 | 12 | 10.3877 | 4.2264 | 2018-01-11 | 144.7504 | 71.2286
2018-01-01 11:00 | 0 | 1 | 1 | 13 | 10.1677 | 4.165 | 2018-01-12 | 132.7055 | 67.0109
2018-01-01 12:00 | 0 | 1 | 1 | 15 | 9.7422 | 4.0459 | 2018-01-13 | 162.3058 | 76.3083
2018-01-01 13:00 | 0 | 1 | 1 | 16 | 9.5367 | 3.9883 | 2018-01-14 | 214.5134 | 91.6611
2018-01-01 14:00 | 0 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-01-15 | 198.0652 | 86.9627
2018-01-01 15:00 | 0 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-01-16 | 174.306 | 80.1138
2018-01-01 16:00 | 0 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-01-17 | 165.1806 | 77.429
2018-01-01 17:00 | 0 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-01-18 | 185.9579 | 83.4869
2018-01-01 18:00 | 0 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-01-19 | 162.7278 | 76.6823
2018-01-01 19:00 | 0 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-01-20 | 138.2277 | 69.049
2018-01-01 20:00 | 0 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-01-21 | 135.1986 | 68.13
2018-01-01 21:00 | 0 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-01-22 | 146.0674 | 71.6542
2018-01-01 22:00 | 0 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-01-23 | 137.1007 | 68.4888
2018-01-01 23:00 | 0 | 1 | 1 | 17 | 9.3361 | 3.9318 | 2018-01-24 | 148.4153 | 72.3256
2018-01-02 | 1 | 1 | 1 | 16 | 9.5367 | 3.9883 | 2018-01-25 | 174.5763 | 80.193
2018-01-02 01:00 | 1 | 1 | 1 | 16 | 9.5367 | 3.9883 | 2018-01-26 | 164.3001 | 77.1688
2018-01-02 02:00 | 1 | 1 | 1 | 16 | 9.5367 | 3.9883 | 2018-01-27 | 139.5809 | 69.3439
2018-01-02 03:00 | 1 | 1 | 1 | 15 | 9.7422 | 4.0459 | 2018-01-28 | 131.6522 | 66.8703
2018-01-02 04:00 | 1 | 1 | 1 | 15 | 9.7422 | 4.0459 | 2018-01-29 | 143.0197 | 70.7063
2018-01-02 05:00 | 1 | 1 | 1 | 14 | 9.9525 | 4.1048 | 2018-01-30 | 166.6701 | 77.8797
2018-01-02 06:00 | 1 | 1 | 1 | 14 | 9.9525 | 4.1048 | 2018-01-31 | 183.6305 | 82.7991
2018-01-02 07:00 | 1 | 1 | 1 | 14 | 9.9525 | 4.1048 | 2018-02-01 | 148.5683 | 72.3988
2018-01-02 08:00 | 1 | 1 | 1 | 14 | 9.9525 | 4.1048 | 2018-02-02 | 178.8101 | 81.3735
2018-01-02 09:00 | 1 | 1 | 1 | 16 | 9.5367 | 3.9883 | 2018-02-03 | 193.1665 | 85.5436
2018-01-02 10:00 | 1 | 1 | 1 | 17 | 9.3361 | 3.9318 | 2018-02-04 | 151.7981 | 73.3742
2018-01-02 11:00 | 1 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-02-05 | 160.9389 | 76.145
2018-01-02 12:00 | 1 | 1 | 1 | 21 | 8.5821 | 3.7186 | 2018-02-06 | 164.6705 | 77.2689
2018-01-02 13:00 | 1 | 1 | 1 | 23 | 8.2342 | 3.6195 | 2018-02-07 | 161.2595 | 76.242
2018-01-02 14:00 | 1 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-02-08 | 170.6472 | 79.0618
2018-01-02 15:00 | 1 | 1 | 1 | 27 | 7.5966 | 3.4362 | 2018-02-09 | 165.5951 | 77.5549
2018-01-02 16:00 | 1 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-02-10 | 140.1727 | 69.7616
2018-01-02 17:00 | 1 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-02-11 | 134.5918 | 67.8533
2018-01-02 18:00 | 1 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-02-12 | 139.1126 | 69.2428
2018-01-02 19:00 | 1 | 1 | 1 | 24 | 8.0675 | 3.5718 | 2018-02-13 | 165.5193 | 77.5402
2018-01-02 20:00 | 1 | 1 | 1 | 21 | 8.5821 | 3.7186 | 2018-02-14 | 140.7979 | 69.8548
2018-01-02 21:00 | 1 | 1 | 1 | 21 | 8.5821 | 3.7186 | 2018-02-15 | 129.6838 | 65.9151
2018-01-02 22:00 | 1 | 1 | 1 | 21 | 8.5821 | 3.7186 | 2018-02-16 | 131.2579 | 66.4068
2018-01-02 23:00 | 1 | 1 | 1 | 21 | 8.5821 | 3.7186 | 2018-02-17 | 159.4751 | 75.7444
2018-01-03 | 2 | 1 | 1 | 20 | 8.7633 | 3.7701 | 2018-02-18 | 148.2835 | 72.3159
2018-01-03 01:00 | 2 | 1 | 1 | 20 | 8.7633 | 3.7701 | 2018-02-19 | 141.2851 | 70.0526
2018-01-03 02:00 | 2 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-02-20 | 129.3222 | 65.4697
2018-01-03 03:00 | 2 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-02-21 | 133.942 | 65.8418
2018-01-03 04:00 | 2 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-02-22 | 138.4596 | 69.0797
2018-01-03 05:00 | 2 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-02-23 | 149.661 | 72.7763
2018-01-03 06:00 | 2 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-02-24 | 133.6593 | 67.57
2018-01-03 07:00 | 2 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-02-25 | 141.8583 | 70.3352
2018-01-03 08:00 | 2 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-02-26 | 134.1478 | 67.7584
2018-01-03 09:00 | 2 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-02-27 | 134.8894 | 67.9346
2018-01-03 10:00 | 2 | 1 | 1 | 22 | 8.4057 | 3.6684 | 2018-02-28 | 131.7235 | 66.6859
2018-01-03 11:00 | 2 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-03-01 | 128.6794 | 65.5892
2018-01-03 12:00 | 2 | 1 | 1 | 27 | 7.5966 | 3.4362 | 2018-03-02 | 148.2244 | 72.3248
2018-01-03 13:00 | 2 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-03-03 | 142.5801 | 70.5449
2018-01-03 14:00 | 2 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-03-04 | 143.8196 | 70.9506
2018-01-03 15:00 | 2 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-03-05 | 150.5596 | 73.0509
2018-01-03 16:00 | 2 | 1 | 1 | 30 | 7.1694 | 3.3119 | 2018-03-06 | 146.4409 | 71.7503
2018-01-03 17:00 | 2 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-03-07 | 155.8961 | 74.6792
2018-01-03 18:00 | 2 | 1 | 1 | 27 | 7.5966 | 3.4362 | 2018-03-08 | 151.0146 | 73.192
2018-01-03 19:00 | 2 | 1 | 1 | 27 | 7.5966 | 3.4362 | 2018-03-09 | 152.8237 | 73.7104
2018-01-03 20:00 | 2 | 1 | 1 | 27 | 7.5966 | 3.4362 | 2018-03-10 | 151.6006 | 73.3669
2018-01-03 21:00 | 2 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-03-11 | 141.0052 | 68.9567
2018-01-03 22:00 | 2 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-03-12 | 150.5397 | 73.0313
2018-01-03 23:00 | 2 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-03-13 | 152.4264 | 73.6227
2018-01-04 | 3 | 1 | 1 | 29 | 7.307 | 3.3521 | 2018-03-14 | 154.2572 | 74.166
2018-01-04 01:00 | 3 | 1 | 1 | 29 | 7.307 | 3.3521 | 2018-03-15 | 147.8664 | 72.1555
2018-01-04 02:00 | 3 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-03-16 | 153.6474 | 73.9995
2018-01-04 03:00 | 3 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-03-17 | 153.4 | 73.7765
2018-01-04 04:00 | 3 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-03-18 | 153.3475 | 73.8451
2018-01-04 05:00 | 3 | 1 | 1 | 27 | 7.5966 | 3.4362 | 2018-03-19 | 146.7239 | 71.8279
2018-01-04 06:00 | 3 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-03-20 | 156.4852 | 74.85
2018-01-04 07:00 | 3 | 1 | 1 | 24 | 8.0675 | 3.5718 | 2018-03-21 | 157.4259 | 75.133
2018-01-04 08:00 | 3 | 1 | 1 | 24 | 8.0675 | 3.5718 | 2018-03-22 | 144.9382 | 71.1803
2018-01-04 09:00 | 3 | 1 | 1 | 22 | 8.4057 | 3.6684 | 2018-03-23 | 141.8372 | 70.2718
2018-01-04 10:00 | 3 | 1 | 1 | 22 | 8.4057 | 3.6684 | 2018-03-24 | 140.0113 | 69.6767
2018-01-04 11:00 | 3 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-03-25 | 146.4268 | 71.7611
2018-01-04 12:00 | 3 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-03-26 | 146.2136 | 71.6556
2018-01-04 13:00 | 3 | 1 | 1 | 24 | 8.0675 | 3.5718 | 2018-03-27 | 146.4947 | 71.7786
2018-01-04 14:00 | 3 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-03-28 | 137.953 | 68.9832
2018-01-04 15:00 | 3 | 1 | 1 | 24 | 8.0675 | 3.5718 | 2018-03-29 | 131.0088 | 66.6566
2018-01-04 16:00 | 3 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-03-30 | 131.4537 | 66.7276
2018-01-04 17:00 | 3 | 1 | 1 | 26 | 7.7488 | 3.4802 | 2018-03-31 | 135.3502 | 68.1062
2018-01-04 18:00 | 3 | 1 | 1 | 26 | 7.7488 | 3.4802 | 2018-04-01 | 131.2385 | 66.6143
2018-01-04 19:00 | 3 | 1 | 1 | 26 | 7.7488 | 3.4802 | 2018-04-02 | 148.6235 | 72.4178
2018-01-04 20:00 | 3 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-04-03 | 143.9673 | 71.0079
2018-01-04 21:00 | 3 | 1 | 1 | 24 | 8.0675 | 3.5718 | 2018-04-04 | 135.4428 | 68.0914
2018-01-04 22:00 | 3 | 1 | 1 | 23 | 8.2342 | 3.6195 | 2018-04-05 | 144.227 | 71.0554
2018-01-04 23:00 | 3 | 1 | 1 | 22 | 8.4057 | 3.6684 | 2018-04-06 | 138.953 | 69.0569
2018-01-05 | 4 | 1 | 1 | 20 | 8.7633 | 3.7701 | 2018-04-07 | 138.4557 | 69.2139
2018-01-05 01:00 | 4 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-04-08 | 149.84 | 72.8079
2018-01-05 02:00 | 4 | 1 | 1 | 17 | 9.3361 | 3.9318 | 2018-04-09 | 148.0044 | 72.2103
2018-01-05 03:00 | 4 | 1 | 1 | 15 | 9.7422 | 4.0459 | 2018-04-10 | 139.7251 | 69.6031
2018-01-05 04:00 | 4 | 1 | 1 | 14 | 9.9525 | 4.1048 | 2018-04-11 | 138.4134 | 69.162
2018-01-05 05:00 | 4 | 1 | 1 | 13 | 10.1677 | 4.165 | 2018-04-12 | 130.2522 | 66.1965
2018-01-05 06:00 | 4 | 1 | 1 | 12 | 10.3877 | 4.2264 | 2018-04-13 | 134.766 | 65.6144
2018-01-05 07:00 | 4 | 1 | 1 | 11 | 10.6126 | 4.2891 | 2018-04-14 | 128.558 | 64.8676
2018-01-05 08:00 | 4 | 1 | 1 | 10 | 10.8423 | 4.353 | 2018-04-15 | 141.1665 | 70.109
2018-01-05 09:00 | 4 | 1 | 1 | 10 | 10.8423 | 4.353 | 2018-04-16 | 134.2977 | 67.57
2018-01-05 10:00 | 4 | 1 | 1 | 12 | 10.3877 | 4.2264 | 2018-04-17 | 137.0125 | 68.7558
2018-01-05 11:00 | 4 | 1 | 1 | 12 | 10.3877 | 4.2264 | 2018-04-18 | 136.5769 | 68.4603
2018-01-05 12:00 | 4 | 1 | 1 | 16 | 9.5367 | 3.9883 | 2018-04-19 | 136.938 | 68.7318
2018-01-05 13:00 | 4 | 1 | 1 | 16 | 9.5367 | 3.9883 | 2018-04-20 | 140.3045 | 69.7714
2018-01-05 14:00 | 4 | 1 | 1 | 16 | 9.5367 | 3.9883 | 2018-04-21 | 132.963 | 66.9853
2018-01-05 15:00 | 4 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-04-22 | 129.1758 | 65.6155
2018-01-05 16:00 | 4 | 1 | 1 | 17 | 9.3361 | 3.9318 | 2018-04-23 | 129.7393 | 65.8956
2018-01-05 17:00 | 4 | 1 | 1 | 16 | 9.5367 | 3.9883 | 2018-04-24 | 129.6784 | 65.6337
2018-01-05 18:00 | 4 | 1 | 1 | 16 | 9.5367 | 3.9883 | 2018-04-25 | 127.8345 | 65.1305
2018-01-05 19:00 | 4 | 1 | 1 | 15 | 9.7422 | 4.0459 | 2018-04-26 | 128.9363 | 64.8055
2018-01-05 20:00 | 4 | 1 | 1 | 16 | 9.5367 | 3.9883 | 2018-04-27 | 128.697 | 65.6951
2018-01-05 21:00 | 4 | 1 | 1 | 12 | 10.3877 | 4.2264 | 2018-04-28 | 128.1096 | 64.9985
2018-01-05 22:00 | 4 | 1 | 1 | 13 | 10.1677 | 4.165 | 2018-04-29 | 128.6754 | 65.6703
2018-01-05 23:00 | 4 | 1 | 1 | 12 | 10.3877 | 4.2264 | 2018-04-30 | 131.5133 | 66.8394
2018-01-06 | 5 | 1 | 1 | 11 | 10.6126 | 4.2891 | 2018-05-01 | 135.7303 | 66.2052
2018-01-06 01:00 | 5 | 1 | 1 | 11 | 10.6126 | 4.2891 | 2018-05-02 | 156.9855 | 69.9381
2018-01-06 02:00 | 5 | 1 | 1 | 10 | 10.8423 | 4.353 | 2018-05-03 | 161.1544 | 70.7785
2018-01-06 03:00 | 5 | 1 | 1 | 10 | 10.8423 | 4.353 | 2018-05-04 | 148.0243 | 67.9039
2018-01-06 04:00 | 5 | 1 | 1 | 10 | 10.8423 | 4.353 | 2018-05-05 | 134.6028 | 65.4179
2018-01-06 05:00 | 5 | 1 | 1 | 10 | 10.8423 | 4.353 | 2018-05-06 | 128.0394 | 64.5894
2018-01-06 06:00 | 5 | 1 | 1 | 9 | 11.0769 | 4.4181 | 2018-05-07 | 130.4957 | 64.9748
2018-01-06 07:00 | 5 | 1 | 1 | 8 | 11.3163 | 4.4845 | 2018-05-08 | 129.5615 | 64.8987
2018-01-06 08:00 | 5 | 1 | 1 | 9 | 11.0769 | 4.4181 | 2018-05-09 | 131.3379 | 65.1335
2018-01-06 09:00 | 5 | 1 | 1 | 10 | 10.8423 | 4.353 | 2018-05-10 | 127.6664 | 64.6141
2018-01-06 10:00 | 5 | 1 | 1 | 11 | 10.6126 | 4.2891 | 2018-05-11 | 131.2184 | 64.842
2018-01-06 11:00 | 5 | 1 | 1 | 12 | 10.3877 | 4.2264 | 2018-05-12 | 127.4765 | 64.9081
2018-01-06 12:00 | 5 | 1 | 1 | 12 | 10.3877 | 4.2264 | 2018-05-13 | 127.7922 | 65.3224
2018-01-06 13:00 | 5 | 1 | 1 | 13 | 10.1677 | 4.165 | 2018-05-14 | 128.8653 | 64.9514
2018-01-06 14:00 | 5 | 1 | 1 | 14 | 9.9525 | 4.1048 | 2018-05-15 | 142.0151 | 67.0489
2018-01-06 15:00 | 5 | 1 | 1 | 14 | 9.9525 | 4.1048 | 2018-05-16 | 127.975 | 64.5825
2018-01-06 16:00 | 5 | 1 | 1 | 14 | 9.9525 | 4.1048 | 2018-05-17 | 131.031 | 65.1704
2018-01-06 17:00 | 5 | 1 | 1 | 12 | 10.3877 | 4.2264 | 2018-05-18 | 128.8476 | 64.5268
2018-01-06 18:00 | 5 | 1 | 1 | 12 | 10.3877 | 4.2264 | 2018-05-19 | 127.9545 | 65.3835
2018-01-06 19:00 | 5 | 1 | 1 | 11 | 10.6126 | 4.2891 | 2018-05-20 | 140.221 | 66.7083
2018-01-06 20:00 | 5 | 1 | 1 | 10 | 10.8423 | 4.353 | 2018-05-21 | 134.2527 | 65.352
2018-01-06 21:00 | 5 | 1 | 1 | 10 | 10.8423 | 4.353 | 2018-05-22 | 129.2995 | 64.672
2018-01-06 22:00 | 5 | 1 | 1 | 9 | 11.0769 | 4.4181 | 2018-05-23 | 139.2294 | 66.4339
2018-01-06 23:00 | 5 | 1 | 1 | 9 | 11.0769 | 4.4181 | 2018-05-24 | 144.3841 | 67.2526
2018-01-07 | 6 | 1 | 1 | 8 | 11.3163 | 4.4845 | 2018-05-25 | 156.6239 | 69.8114
2018-01-07 01:00 | 6 | 1 | 1 | 8 | 11.3163 | 4.4845 | 2018-05-26 | 162.239 | 70.9464
2018-01-07 02:00 | 6 | 1 | 1 | 9 | 11.0769 | 4.4181 | 2018-05-27 | 132.9794 | 65.3625
2018-01-07 03:00 | 6 | 1 | 1 | 9 | 11.0769 | 4.4181 | 2018-05-28 | 128.4878 | 64.724
2018-01-07 04:00 | 6 | 1 | 1 | 7 | 11.5605 | 4.5522 | 2018-05-29 | 147.176 | 67.9127
2018-01-07 05:00 | 6 | 1 | 1 | 7 | 11.5605 | 4.5522 | 2018-05-30 | 132.516 | 65.0502
2018-01-07 06:00 | 6 | 1 | 1 | 7 | 11.5605 | 4.5522 | 2018-05-31 | 129.8462 | 64.6098
2018-01-07 07:00 | 6 | 1 | 1 | 6 | 11.8097 | 4.6211 | 2018-06-01 | 137.3656 | 65.9111
2018-01-07 08:00 | 6 | 1 | 1 | 7 | 11.5605 | 4.5522 | 2018-06-02 | 151.6226 | 68.7086
2018-01-07 09:00 | 6 | 1 | 1 | 9 | 11.0769 | 4.4181 | 2018-06-03 | 128.8992 | 64.5884
2018-01-07 10:00 | 6 | 1 | 1 | 9 | 11.0769 | 4.4181 | 2018-06-04 | 129.6382 | 65.0488
2018-01-07 11:00 | 6 | 1 | 1 | 12 | 10.3877 | 4.2264 | 2018-06-05 | 134.7329 | 65.4755
2018-01-07 12:00 | 6 | 1 | 1 | 12 | 10.3877 | 4.2264 | 2018-06-06 | 129.5821 | 64.6288
2018-01-07 13:00 | 6 | 1 | 1 | 15 | 9.7422 | 4.0459 | 2018-06-07 | 130.1619 | 64.7055
2018-01-07 14:00 | 6 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-06-08 | 142.5697 | 66.984
2018-01-07 15:00 | 6 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-06-09 | 144.6314 | 67.21
2018-01-07 16:00 | 6 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-06-10 | 134.3625 | 65.2692
2018-01-07 17:00 | 6 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-06-11 | 130.594 | 64.778
2018-01-07 18:00 | 6 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-06-12 | 132.7589 | 65.1272
2018-01-07 19:00 | 6 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-06-13 | 139.1746 | 66.2171
2018-01-07 20:00 | 6 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-06-14 | 150.015 | 68.329
2018-01-07 21:00 | 6 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-06-15 | 137.4079 | 65.8255
2018-01-07 22:00 | 6 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-06-16 | 148.041 | 67.9807
2018-01-07 23:00 | 6 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-06-17 | 157.6208 | 69.9953
2018-01-08 | 7 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-06-18 | 166.3298 | 71.8585
2018-01-08 01:00 | 7 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-06-19 | 163.4969 | 71.1685
2018-01-08 02:00 | 7 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-06-20 | 145.3519 | 67.376
2018-01-08 03:00 | 7 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-06-21 | 147.2236 | 67.8429
2018-01-08 04:00 | 7 | 1 | 1 | 20 | 8.7633 | 3.7701 | 2018-06-22 | 136.7298 | 65.68
2018-01-08 05:00 | 7 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-06-23 | 129.5442 | 64.5418
2018-01-08 06:00 | 7 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-06-24 | 146.0283 | 67.6224
2018-01-08 07:00 | 7 | 1 | 1 | 20 | 8.7633 | 3.7701 | 2018-06-25 | 145.1292 | 67.3332
2018-01-08 08:00 | 7 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-06-26 | 137.194 | 65.8091
2018-01-08 09:00 | 7 | 1 | 1 | 21 | 8.5821 | 3.7186 | 2018-06-27 | 137.7862 | 65.8696
2018-01-08 10:00 | 7 | 1 | 1 | 23 | 8.2342 | 3.6195 | 2018-06-28 | 148.4978 | 68.0209
2018-01-08 11:00 | 7 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-06-29 | 162.0459 | 70.9257
2018-01-08 12:00 | 7 | 1 | 1 | 27 | 7.5966 | 3.4362 | 2018-06-30 | 172.6297 | 73.2517
2018-01-08 13:00 | 7 | 1 | 1 | 27 | 7.5966 | 3.4362 | 2018-07-01 | 183.0146 | 75.5265
2018-01-08 14:00 | 7 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-07-02 | 174.1381 | 73.5334
2018-01-08 15:00 | 7 | 1 | 1 | 30 | 7.1694 | 3.3119 | 2018-07-03 | 164.2399 | 71.3355
2018-01-08 16:00 | 7 | 1 | 1 | 31 | 7.0367 | 3.2729 | 2018-07-04 | 162.9286 | 71.0465
2018-01-08 17:00 | 7 | 1 | 1 | 30.5 | 7.1024 | 3.2922 | 2018-07-05 | 165.2315 | 71.5567
2018-01-08 18:00 | 7 | 1 | 1 | 30 | 7.1694 | 3.3119 | 2018-07-06 | 155.6349 | 69.4653
2018-01-08 19:00 | 7 | 1 | 1 | 30 | 7.1694 | 3.3119 | 2018-07-07 | 136.452 | 65.6714
2018-01-08 20:00 | 7 | 1 | 1 | 30 | 7.1694 | 3.3119 | 2018-07-08 | 143.5538 | 67.0632
2018-01-08 21:00 | 7 | 1 | 1 | 30 | 7.1694 | 3.3119 | 2018-07-09 | 154.1301 | 69.2473
2018-01-08 22:00 | 7 | 1 | 1 | 31 | 7.0367 | 3.2729 | 2018-07-10 | 169.5265 | 72.5888
2018-01-08 23:00 | 7 | 1 | 1 | 34 | 6.6676 | 3.1635 | 2018-07-11 | 157.2725 | 69.8285
2018-01-09 | 8 | 1 | 1 | 32 | 6.9088 | 3.2352 | 2018-07-12 | 148.6865 | 68.0549
2018-01-09 01:00 | 8 | 1 | 1 | 32 | 6.9088 | 3.2352 | 2018-07-13 | 151.0432 | 68.5403
2018-01-09 02:00 | 8 | 1 | 1 | 30 | 7.1694 | 3.3119 | 2018-07-14 | 163.9802 | 71.3411
2018-01-09 03:00 | 8 | 1 | 1 | 30 | 7.1694 | 3.3119 | 2018-07-15 | 151.7879 | 68.7125
2018-01-09 04:00 | 8 | 1 | 1 | 32 | 6.9088 | 3.2352 | 2018-07-16 | 167.9947 | 72.1708
2018-01-09 05:00 | 8 | 1 | 1 | 34 | 6.6676 | 3.1635 | 2018-07-17 | 157.6381 | 69.9491
2018-01-09 06:00 | 8 | 1 | 1 | 34 | 6.6676 | 3.1635 | 2018-07-18 | 151.9281 | 68.7341
2018-01-09 07:00 | 8 | 1 | 1 | 34 | 6.6676 | 3.1635 | 2018-07-19 | 145.5763 | 67.424
2018-01-09 08:00 | 8 | 1 | 1 | 34 | 6.6676 | 3.1635 | 2018-07-20 | 147.3545 | 67.7703
2018-01-09 09:00 | 8 | 1 | 1 | 36 | 6.4458 | 3.0968 | 2018-07-21 | 140.2694 | 66.3489
2018-01-09 10:00 | 8 | 1 | 1 | 38 | 6.2434 | 3.0351 | 2018-07-22 | 148.7117 | 68.0373
2018-01-09 11:00 | 8 | 1 | 1 | 39 | 6.1495 | 3.0061 | 2018-07-23 | 155.5481 | 69.4574
2018-01-09 12:00 | 8 | 1 | 1 | 43 | 5.8224 | 2.9027 | 2018-07-24 | 158.6931 | 70.1262
2018-01-09 13:00 | 8 | 1 | 1 | 42 | 5.8969 | 2.9267 | 2018-07-25 | 150.1508 | 68.3108
2018-01-09 14:00 | 8 | 1 | 1 | 43 | 5.8224 | 2.9027 | 2018-07-26 | 157.3364 | 69.8739
2018-01-09 15:00 | 8 | 1 | 1 | 43 | 5.8224 | 2.9027 | 2018-07-27 | 159.403 | 70.3136
2018-01-09 16:00 | 8 | 1 | 1 | 42 | 5.8969 | 2.9267 | 2018-07-28 | 156.4343 | 69.695
2018-01-09 17:00 | 8 | 1 | 1 | 39 | 6.1495 | 3.0061 | 2018-07-29 | 152.6133 | 68.8475
2018-01-09 18:00 | 8 | 1 | 1 | 39 | 6.1495 | 3.0061 | 2018-07-30 | 148.4643 | 67.9736
2018-01-09 19:00 | 8 | 1 | 1 | 38 | 6.2434 | 3.0351 | 2018-07-31 | 147.892 | 67.8796
2018-01-09 20:00 | 8 | 1 | 1 | 37 | 6.3422 | 3.0653 | 2018-08-01 | 161.7963 | 70.8422
2018-01-09 21:00 | 8 | 1 | 1 | 36 | 6.4458 | 3.0968 | 2018-08-02 | 166.8656 | 71.9093
2018-01-09 22:00 | 8 | 1 | 1 | 36 | 6.4458 | 3.0968 | 2018-08-03 | 158.3281 | 70.042
2018-01-09 23:00 | 8 | 1 | 1 | 36 | 6.4458 | 3.0968 | 2018-08-04 | 159.0767 | 70.2394
2018-01-10 | 9 | 1 | 1 | 34 | 6.6676 | 3.1635 | 2018-08-05 | 172.743 | 73.2326
2018-01-10 01:00 | 9 | 1 | 1 | 33 | 6.7858 | 3.1987 | 2018-08-06 | 178.4449 | 74.4817
2018-01-10 02:00 | 9 | 1 | 1 | 34 | 6.6676 | 3.1635 | 2018-08-07 | 167.8656 | 72.1424
2018-01-10 03:00 | 9 | 1 | 1 | 30 | 7.1694 | 3.3119 | 2018-08-08 | 168.6407 | 72.3127
2018-01-10 04:00 | 9 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-08-09 | 166.157 | 71.7657
2018-01-10 05:00 | 9 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-08-10 | 162.6499 | 71.0086
2018-01-10 06:00 | 9 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-08-11 | 146.5661 | 67.5869
2018-01-10 07:00 | 9 | 1 | 1 | 30 | 7.1694 | 3.3119 | 2018-08-12 | 148.5309 | 68.0004
2018-01-10 08:00 | 9 | 1 | 1 | 30 | 7.1694 | 3.3119 | 2018-08-13 | 142.1147 | 66.6835
2018-01-10 09:00 | 9 | 1 | 1 | 32 | 6.9088 | 3.2352 | 2018-08-14 | 147.2707 | 67.7584
2018-01-10 10:00 | 9 | 1 | 1 | 33 | 6.7858 | 3.1987 | 2018-08-15 | 161.5265 | 70.8308
2018-01-10 11:00 | 9 | 1 | 1 | 36 | 6.4458 | 3.0968 | 2018-08-16 | 172.8863 | 73.2501
2018-01-10 12:00 | 9 | 1 | 1 | 37 | 6.3422 | 3.0653 | 2018-08-17 | 168.6319 | 72.2863
2018-01-10 13:00 | 9 | 1 | 1 | 39 | 6.1495 | 3.0061 | 2018-08-18 | 156.1998 | 69.6299
2018-01-10 14:00 | 9 | 1 | 1 | 37 | 6.3422 | 3.0653 | 2018-08-19 | 138.9731 | 66.0783
2018-01-10 15:00 | 9 | 1 | 1 | 37 | 6.3422 | 3.0653 | 2018-08-20 | 138.4912 | 66.0027
2018-01-10 16:00 | 9 | 1 | 1 | 37 | 6.3422 | 3.0653 | 2018-08-21 | 142.1976 | 66.741
2018-01-10 17:00 | 9 | 1 | 1 | 37 | 6.3422 | 3.0653 | 2018-08-22 | 152.8611 | 68.9258
2018-01-10 18:00 | 9 | 1 | 1 | 37 | 6.3422 | 3.0653 | 2018-08-23 | 143.2663 | 66.9459
2018-01-10 19:00 | 9 | 1 | 1 | 37 | 6.3422 | 3.0653 | 2018-08-24 | 147.9167 | 67.9004
2018-01-10 20:00 | 9 | 1 | 1 | 37 | 6.3422 | 3.0653 | 2018-08-25 | 146.0516 | 67.4932
2018-01-10 21:00 | 9 | 1 | 1 | 39 | 6.1495 | 3.0061 | 2018-08-26 | 152.0944 | 68.7672
2018-01-10 22:00 | 9 | 1 | 1 | 40 | 6.0605 | 2.9784 | 2018-08-27 | 166.422 | 71.829
2018-01-10 23:00 | 9 | 1 | 1 | 39 | 6.1495 | 3.0061 | 2018-08-28 | 186.195 | 76.2479
2018-01-11 | 10 | 1 | 1 | 40 | 6.0605 | 2.9784 | 2018-08-29 | 192.1624 | 77.5749
2018-01-11 01:00 | 10 | 1 | 1 | 41 | 5.9762 | 2.9519 | 2018-08-30 | 174.5023 | 73.5884
2018-01-11 02:00 | 10 | 1 | 1 | 41 | 5.9762 | 2.9519 | 2018-08-31 | 145.3457 | 67.3309
2018-01-11 03:00 | 10 | 1 | 1 | 37 | 6.3422 | 3.0653 | 2018-09-01 | 141.5229 | 66.5844
2018-01-11 04:00 | 10 | 1 | 1 | 37 | 6.3422 | 3.0653 | 2018-09-02 | 148.2456 | 67.956
2018-01-11 05:00 | 10 | 1 | 1 | 36 | 6.4458 | 3.0968 | 2018-09-03 | 166.3607 | 71.8181
2018-01-11 06:00 | 10 | 1 | 1 | 36 | 6.4458 | 3.0968 | 2018-09-04 | 175.0759 | 73.7263
2018-01-11 07:00 | 10 | 1 | 1 | 37 | 6.3422 | 3.0653 | 2018-09-05 | 166.5362 | 71.8391
2018-01-11 08:00 | 10 | 1 | 1 | 37 | 6.3422 | 3.0653 | 2018-09-06 | 168.2478 | 72.2648
2018-01-11 09:00 | 10 | 1 | 1 | 39 | 6.1495 | 3.0061 | 2018-09-07 | 143.5591 | 66.9729
2018-01-11 10:00 | 10 | 1 | 1 | 40 | 6.0605 | 2.9784 | 2018-09-08 | 135.0807 | 65.4153
2018-01-11 11:00 | 10 | 1 | 1 | 41 | 5.9762 | 2.9519 | 2018-09-09 | 128.1893 | 64.4541
2018-01-11 12:00 | 10 | 1 | 1 | 45 | 5.6879 | 2.8584 | 2018-09-10 | 128.3397 | 64.4928
2018-01-11 13:00 | 10 | 1 | 1 | 43 | 5.8224 | 2.9027 | 2018-09-11 | 134.8224 | 65.4116
2018-01-11 14:00 | 10 | 1 | 1 | 45 | 5.6879 | 2.8584 | 2018-09-12 | 141.6129 | 66.5882
2018-01-11 15:00 | 10 | 1 | 1 | 45 | 5.6879 | 2.8584 | 2018-09-13 | 140.5657 | 66.3865
2018-01-11 16:00 | 10 | 1 | 1 | 47 | 5.5728 | 2.8192 | 2018-09-14 | 140.1477 | 66.3032
2018-01-11 17:00 | 10 | 1 | 1 | 45 | 5.6879 | 2.8584 | 2018-09-15 | 143.2522 | 66.9567
2018-01-11 18:00 | 10 | 1 | 1 | 41 | 5.9762 | 2.9519 | 2018-09-16 | 147.7121 | 67.8719
2018-01-11 19:00 | 10 | 1 | 1 | 42 | 5.8969 | 2.9267 | 2018-09-17 | 145.0507 | 67.2841
2018-01-11 20:00 | 10 | 1 | 1 | 43 | 5.8224 | 2.9027 | 2018-09-18 | 146.9343 | 67.6671
2018-01-11 21:00 | 10 | 1 | 1 | 39 | 6.1495 | 3.0061 | 2018-09-19 | 145.6336 | 67.4098
2018-01-11 22:00 | 10 | 1 | 1 | 39 | 6.1495 | 3.0061 | 2018-09-20 | 134.0609 | 65.2158
2018-01-11 23:00 | 10 | 1 | 1 | 39 | 6.1495 | 3.0061 | 2018-09-21 | 137.8056 | 65.8746
2018-01-12 | 11 | 1 | 1 | 39 | 6.1495 | 3.0061 | 2018-09-22 | 138.2015 | 65.9716
2018-01-12 01:00 | 11 | 1 | 1 | 40 | 6.0605 | 2.9784 | 2018-09-23 | 129.6866 | 64.5833
2018-01-12 02:00 | 11 | 1 | 1 | 39 | 6.1495 | 3.0061 | 2018-09-24 | 129.8476 | 64.6536
2018-01-12 03:00 | 11 | 1 | 1 | 37 | 6.3422 | 3.0653 | 2018-09-25 | 135.1156 | 65.5594
2018-01-12 04:00 | 11 | 1 | 1 | 39 | 6.1495 | 3.0061 | 2018-09-26 | 147.5238 | 67.7994
2018-01-12 05:00 | 11 | 1 | 1 | 45 | 5.6879 | 2.8584 | 2018-09-27 | 134.478 | 65.323
2018-01-12 06:00 | 11 | 1 | 1 | 54 | 5.3228 | 2.7211 | 2018-09-28 | 128.5248 | 64.5163
2018-01-12 07:00 | 11 | 1 | 1 | 53 | 5.3439 | 2.7314 | 2018-09-29 | 132.8105 | 65.1356
2018-01-12 08:00 | 11 | 1 | 1 | 52 | 5.37 | 2.7429 | 2018-09-30 | 130.8524 | 64.8348
2018-01-12 09:00 | 11 | 1 | 1 | 52 | 5.37 | 2.7429 | 2018-10-01 | 137.6712 | 65.9052
2018-01-12 10:00 | 11 | 1 | 1 | 54 | 5.3228 | 2.7211 | 2018-10-02 | 141.0662 | 66.5442
2018-01-12 11:00 | 11 | 1 | 1 | 55 | 5.3065 | 2.7121 | 2018-10-03 | 136.7968 | 65.7214
2018-01-12 12:00 | 11 | 1 | 1 | 57 | 5.2884 | 2.6978 | 2018-10-04 | 138.8281 | 66.1617
2018-01-12 13:00 | 11 | 1 | 1 | 60 | 5.2976 | 2.6856 | 2018-10-05 | 132.1407 | 64.9489
2018-01-12 14:00 | 11 | 1 | 1 | 57 | 5.2884 | 2.6978 | 2018-10-06 | 130.9339 | 64.7206
2018-01-12 15:00 | 11 | 1 | 1 | 54 | 5.3228 | 2.7211 | 2018-10-07 | 144.3805 | 67.1889
2018-01-12 16:00 | 11 | 1 | 1 | 55 | 5.3065 | 2.7121 | 2018-10-08 | 132.8863 | 65.0441
2018-01-12 17:00 | 11 | 1 | 1 | 55 | 5.3065 | 2.7121 | 2018-10-09 | 139.9842 | 66.3045
2018-01-12 18:00 | 11 | 1 | 1 | 54 | 5.3228 | 2.7211 | 2018-10-10 | 144.1407 | 67.108
2018-01-12 19:00 | 11 | 1 | 1 | 51 | 5.4008 | 2.7556 | 2018-10-11 | 141.4615 | 66.5614
2018-01-12 20:00 | 11 | 1 | 1 | 50 | 5.4365 | 2.7696 | 2018-10-12 | 129.2599 | 64.7391
2018-01-12 21:00 | 11 | 1 | 1 | 50 | 5.4365 | 2.7696 | 2018-10-13 | 128.1106 | 65.3995
2018-01-12 22:00 | 11 | 1 | 1 | 51 | 5.4008 | 2.7556 | 2018-10-14 | 127.5969 | 65.0694
2018-01-12 23:00 | 11 | 1 | 1 | 54 | 5.3228 | 2.7211 | 2018-10-15 | 129.5099 | 64.7841
2018-01-13 | 12 | 1 | 1 | 53 | 5.3439 | 2.7314 | 2018-10-16 | 128.3588 | 65.3329
2018-01-13 01:00 | 12 | 1 | 1 | 51 | 5.4008 | 2.7556 | 2018-10-17 | 128.1185 | 65.1842
2018-01-13 02:00 | 12 | 1 | 1 | 50 | 5.4365 | 2.7696 | 2018-10-18 | 132.4291 | 67.1522
2018-01-13 03:00 | 12 | 1 | 1 | 52 | 5.37 | 2.7429 | 2018-10-19 | 129.8928 | 65.8771
2018-01-13 04:00 | 12 | 1 | 1 | 52 | 5.37 | 2.7429 | 2018-10-20 | 127.5536 | 64.6479
2018-01-13 05:00 | 12 | 1 | 1 | 52 | 5.37 | 2.7429 | 2018-10-21 | 132.4498 | 67.1479
2018-01-13 06:00 | 12 | 1 | 1 | 48 | 5.5225 | 2.8014 | 2018-10-22 | 133.1659 | 67.3803
2018-01-13 07:00 | 12 | 1 | 1 | 43 | 5.8224 | 2.9027 | 2018-10-23 | 129.9196 | 65.7054
2018-01-13 08:00 | 12 | 1 | 1 | 37 | 6.3422 | 3.0653 | 2018-10-24 | 129.9268 | 66.2045
2018-01-13 09:00 | 12 | 1 | 1 | 30 | 7.1694 | 3.3119 | 2018-10-25 | 134.0054 | 67.7169
2018-01-13 10:00 | 12 | 1 | 1 | 29 | 7.307 | 3.3521 | 2018-10-26 | 135.923 | 68.3742
2018-01-13 11:00 | 12 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-10-27 | 131.4365 | 66.7956
2018-01-13 12:00 | 12 | 1 | 1 | 30 | 7.1694 | 3.3119 | 2018-10-28 | 130.4656 | 66.4107
2018-01-13 13:00 | 12 | 1 | 1 | 32 | 6.9088 | 3.2352 | 2018-10-29 | 128.3831 | 65.5516
2018-01-13 14:00 | 12 | 1 | 1 | 34 | 6.6676 | 3.1635 | 2018-10-30 | 130.8422 | 66.5027
2018-01-13 15:00 | 12 | 1 | 1 | 34 | 6.6676 | 3.1635 | 2018-10-31 | 129.4972 | 65.5292
2018-01-13 16:00 | 12 | 1 | 1 | 32 | 6.9088 | 3.2352 | 2018-11-01 | 128.9173 | 64.6027
2018-01-13 17:00 | 12 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-11-02 | 130.3061 | 64.646
2018-01-13 18:00 | 12 | 1 | 1 | 27 | 7.5966 | 3.4362 | 2018-11-03 | 127.707 | 64.8419
2018-01-13 19:00 | 12 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-11-04 | 135.9731 | 69.1938
2018-01-13 20:00 | 12 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-11-05 | 129.2923 | 65.9641
2018-01-13 21:00 | 12 | 1 | 1 | 23 | 8.2342 | 3.6195 | 2018-11-06 | 128.1515 | 65.27
2018-01-13 22:00 | 12 | 1 | 1 | 22 | 8.4057 | 3.6684 | 2018-11-07 | 127.5681 | 64.6516
2018-01-13 23:00 | 12 | 1 | 1 | 21 | 8.5821 | 3.7186 | 2018-11-08 | 129.8033 | 66.1003
2018-01-14 | 13 | 1 | 1 | 20 | 8.7633 | 3.7701 | 2018-11-09 | 132.126 | 66.9898
2018-01-14 01:00 | 13 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-11-10 | 137.6885 | 68.9345
2018-01-14 02:00 | 13 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-11-11 | 143.1657 | 70.7052
2018-01-14 03:00 | 13 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-11-12 | 137.7696 | 68.965
2018-01-14 04:00 | 13 | 1 | 1 | 17 | 9.3361 | 3.9318 | 2018-11-13 | 133.1024 | 67.4026
2018-01-14 05:00 | 13 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-11-14 | 150.0834 | 72.8994
2018-01-14 06:00 | 13 | 1 | 1 | 16 | 9.5367 | 3.9883 | 2018-11-15 | 162.1008 | 76.5307
2018-01-14 07:00 | 13 | 1 | 1 | 16 | 9.5367 | 3.9883 | 2018-11-16 | 142.3001 | 70.4633
2018-01-14 08:00 | 13 | 1 | 1 | 16 | 9.5367 | 3.9883 | 2018-11-17 | 137.9129 | 69.0357
2018-01-14 09:00 | 13 | 1 | 1 | 16 | 9.5367 | 3.9883 | 2018-11-18 | 140.3698 | 69.8606
2018-01-14 10:00 | 13 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-11-19 | 134.8269 | 67.9861
2018-01-14 11:00 | 13 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-11-20 | 136.371 | 68.5474
2018-01-14 12:00 | 13 | 1 | 1 | 21 | 8.5821 | 3.7186 | 2018-11-21 | 146.3355 | 71.7135
2018-01-14 13:00 | 13 | 1 | 1 | 22 | 8.4057 | 3.6684 | 2018-11-22 | 192.6546 | 85.4312
2018-01-14 14:00 | 13 | 1 | 1 | 23 | 8.2342 | 3.6195 | 2018-11-23 | 190.0267 | 84.6251
2018-01-14 15:00 | 13 | 1 | 1 | 23 | 8.2342 | 3.6195 | 2018-11-24 | 148.231 | 72.2251
2018-01-14 16:00 | 13 | 1 | 1 | 23 | 8.2342 | 3.6195 | 2018-11-25 | 130.5723 | 66.4381
2018-01-14 17:00 | 13 | 1 | 1 | 21 | 8.5821 | 3.7186 | 2018-11-26 | 132.3136 | 67.0984
2018-01-14 18:00 | 13 | 1 | 1 | 21 | 8.5821 | 3.7186 | 2018-11-27 | 139.7004 | 69.6354
2018-01-14 19:00 | 13 | 1 | 1 | 21 | 8.5821 | 3.7186 | 2018-11-28 | 145.4391 | 71.4588
2018-01-14 20:00 | 13 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-11-29 | 140.5624 | 69.9198
2018-01-14 21:00 | 13 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-11-30 | 145.0573 | 71.351
2018-01-14 22:00 | 13 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-12-01 | 141.85 | 70.3234
2018-01-14 23:00 | 13 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-12-02 | 132.8687 | 67.2604
2018-01-15 | 14 | 1 | 1 | 17 | 9.3361 | 3.9318 | 2018-12-03 | 128.5806 | 65.6121
2018-01-15 01:00 | 14 | 1 | 1 | 17 | 9.3361 | 3.9318 | 2018-12-04 | 148.3439 | 72.3507
2018-01-15 02:00 | 14 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-12-05 | 162.3627 | 76.5981
2018-01-15 03:00 | 14 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-12-06 | 154.0808 | 74.1158
2018-01-15 04:00 | 14 | 1 | 1 | 17 | 9.3361 | 3.9318 | 2018-12-07 | 155.0116 | 74.3938
2018-01-15 05:00 | 14 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-12-08 | 168.4827 | 78.4086
2018-01-15 06:00 | 14 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-12-09 | 161.7511 | 76.4263
2018-01-15 07:00 | 14 | 1 | 1 | 19 | 8.9494 | 3.8227 | 2018-12-10 | 158.6135 | 75.4746
2018-01-15 08:00 | 14 | 1 | 1 | 18 | 9.1403 | 3.8767 | 2018-12-11 | 158.3512 | 75.3926
2018-01-15 09:00 | 14 | 1 | 1 | 21 | 8.5821 | 3.7186 | 2018-12-12 | 152.4216 | 73.6215
2018-01-15 10:00 | 14 | 1 | 1 | 24 | 8.0675 | 3.5718 | 2018-12-13 | 152.7695 | 73.7206
2018-01-15 11:00 | 14 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-12-14 | 136.6607 | 68.5784
2018-01-15 12:00 | 14 | 1 | 1 | 27 | 7.5966 | 3.4362 | 2018-12-15 | 134.0257 | 67.7511
2018-01-15 13:00 | 14 | 1 | 1 | 27 | 7.5966 | 3.4362 | 2018-12-16 | 144.7248 | 71.2317
2018-01-15 14:00 | 14 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-12-17 | 142.5576 | 70.544
2018-01-15 15:00 | 14 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-12-18 | 159.9702 | 75.8863
2018-01-15 16:00 | 14 | 1 | 1 | 29 | 7.307 | 3.3521 | 2018-12-19 | 160.6933 | 76.0336
2018-01-15 17:00 | 14 | 1 | 1 | 28 | 7.4494 | 3.3935 | 2018-12-20 | 144.2455 | 71.0843
2018-01-15 18:00 | 14 | 1 | 1 | 27 | 7.5966 | 3.4362 | 2018-12-21 | 127.465 | 64.9534
2018-01-15 19:00 | 14 | 1 | 1 | 26 | 7.7488 | 3.4802 | 2018-12-22 | 136.6298 | 68.5657
2018-01-15 20:00 | 14 | 1 | 1 | 27 | 7.5966 | 3.4362 | 2018-12-23 | 145.7535 | 71.5638
2018-01-15 21:00 | 14 | 1 | 1 | 27 | 7.5966 | 3.4362 | 2018-12-24 | 148.0026 | 72.2581
2018-01-15 22:00 | 14 | 1 | 1 | 26 | 7.7488 | 3.4802 | 2018-12-25 | 152.59 | 73.6744
2018-01-15 23:00 | 14 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-12-26 | 150.0745 | 72.873
2018-01-16 | 15 | 1 | 1 | 24 | 8.0675 | 3.5718 | 2018-12-27 | 144.2054 | 71.0836
2018-01-16 01:00 | 15 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-12-28 | 131.3426 | 66.6072
2018-01-16 02:00 | 15 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-12-29 | 132.9948 | 67.2398
2018-01-16 03:00 | 15 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-12-30 | 152.7325 | 73.7159
2018-01-16 04:00 | 15 | 1 | 1 | 25 | 7.9057 | 3.5254 | 2018-12-31 | 142.4209 | 70.4799
2018-01-16 05:00 | 15 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-01-16 06:00 | 15 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-01-16 07:00 | 15 | 1 | 1 | 26 | 7.7488 | 3.4802
2018-01-16 08:00 | 15 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-01-16 09:00 | 15 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-01-16 10:00 | 15 | 1 | 1 | 29 | 7.307 | 3.3521
2018-01-16 11:00 | 15 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-16 12:00 | 15 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-16 13:00 | 15 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-01-16 14:00 | 15 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-16 15:00 | 15 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-16 16:00 | 15 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-16 17:00 | 15 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-16 18:00 | 15 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-16 19:00 | 15 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-16 20:00 | 15 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-16 21:00 | 15 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-16 22:00 | 15 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-01-16 23:00 | 15 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-17 | 16 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-17 01:00 | 16 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-01-17 02:00 | 16 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-17 03:00 | 16 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-17 04:00 | 16 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-01-17 05:00 | 16 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-17 06:00 | 16 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-17 07:00 | 16 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-01-17 08:00 | 16 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-17 09:00 | 16 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-17 10:00 | 16 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-17 11:00 | 16 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-17 12:00 | 16 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-17 13:00 | 16 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-17 14:00 | 16 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-17 15:00 | 16 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-17 16:00 | 16 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-01-17 17:00 | 16 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-01-17 18:00 | 16 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-17 19:00 | 16 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-17 20:00 | 16 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-01-17 21:00 | 16 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-01-17 22:00 | 16 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-01-17 23:00 | 16 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-01-18 | 17 | 1 | 1 | 23 | 8.2342 | 3.6195
2018-01-18 01:00 | 17 | 1 | 1 | 23 | 8.2342 | 3.6195
2018-01-18 02:00 | 17 | 1 | 1 | 21 | 8.5821 | 3.7186
2018-01-18 03:00 | 17 | 1 | 1 | 21 | 8.5821 | 3.7186
2018-01-18 04:00 | 17 | 1 | 1 | 21 | 8.5821 | 3.7186
2018-01-18 05:00 | 17 | 1 | 1 | 21 | 8.5821 | 3.7186
2018-01-18 06:00 | 17 | 1 | 1 | 21 | 8.5821 | 3.7186
2018-01-18 07:00 | 17 | 1 | 1 | 22 | 8.4057 | 3.6684
2018-01-18 08:00 | 17 | 1 | 1 | 21 | 8.5821 | 3.7186
2018-01-18 09:00 | 17 | 1 | 1 | 23 | 8.2342 | 3.6195
2018-01-18 10:00 | 17 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-01-18 11:00 | 17 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-18 12:00 | 17 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-18 13:00 | 17 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-01-18 14:00 | 17 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-18 15:00 | 17 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-18 16:00 | 17 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-01-18 17:00 | 17 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-18 18:00 | 17 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-18 19:00 | 17 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-18 20:00 | 17 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-18 21:00 | 17 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-18 22:00 | 17 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-18 23:00 | 17 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-01-19 | 18 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-01-19 01:00 | 18 | 1 | 1 | 26 | 7.7488 | 3.4802
2018-01-19 02:00 | 18 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-01-19 03:00 | 18 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-01-19 04:00 | 18 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-01-19 05:00 | 18 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-19 06:00 | 18 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-19 07:00 | 18 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-19 08:00 | 18 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-19 09:00 | 18 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-19 10:00 | 18 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-19 11:00 | 18 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-19 12:00 | 18 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-19 13:00 | 18 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-19 14:00 | 18 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-19 15:00 | 18 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-19 16:00 | 18 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-01-19 17:00 | 18 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-19 18:00 | 18 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-19 19:00 | 18 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-01-19 20:00 | 18 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-19 21:00 | 18 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-19 22:00 | 18 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-19 23:00 | 18 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-20 | 19 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-20 01:00 | 19 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-20 02:00 | 19 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-20 03:00 | 19 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-20 04:00 | 19 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-01-20 05:00 | 19 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-20 06:00 | 19 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-20 07:00 | 19 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-01-20 08:00 | 19 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-20 09:00 | 19 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-20 10:00 | 19 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-01-20 11:00 | 19 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-20 12:00 | 19 | 1 | 1 | 52 | 5.37 | 2.7429
2018-01-20 13:00 | 19 | 1 | 1 | 52 | 5.37 | 2.7429
2018-01-20 14:00 | 19 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-01-20 15:00 | 19 | 1 | 1 | 52 | 5.37 | 2.7429
2018-01-20 16:00 | 19 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-01-20 17:00 | 19 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-01-20 18:00 | 19 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-20 19:00 | 19 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-20 20:00 | 19 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-20 21:00 | 19 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-01-20 22:00 | 19 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-01-20 23:00 | 19 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-01-21 | 20 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-01-21 01:00 | 20 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-21 02:00 | 20 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-21 03:00 | 20 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-21 04:00 | 20 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-21 05:00 | 20 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-21 06:00 | 20 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-01-21 07:00 | 20 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-01-21 08:00 | 20 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-01-21 09:00 | 20 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-01-21 10:00 | 20 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-01-21 11:00 | 20 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-01-21 12:00 | 20 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-01-21 13:00 | 20 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-21 14:00 | 20 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-01-21 15:00 | 20 | 1 | 1 | 52 | 5.37 | 2.7429
2018-01-21 16:00 | 20 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-21 17:00 | 20 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-21 18:00 | 20 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-01-21 19:00 | 20 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-01-21 20:00 | 20 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-01-21 21:00 | 20 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-21 22:00 | 20 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-01-21 23:00 | 20 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-01-22 | 21 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-01-22 01:00 | 21 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-01-22 02:00 | 21 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-22 03:00 | 21 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-22 04:00 | 21 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-01-22 05:00 | 21 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-22 06:00 | 21 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-22 07:00 | 21 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-22 08:00 | 21 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-22 09:00 | 21 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-22 10:00 | 21 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-01-22 11:00 | 21 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-22 12:00 | 21 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-22 13:00 | 21 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-22 14:00 | 21 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-22 15:00 | 21 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-22 16:00 | 21 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-01-22 17:00 | 21 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-22 18:00 | 21 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-22 19:00 | 21 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-01-22 20:00 | 21 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-22 21:00 | 21 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-22 22:00 | 21 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-22 23:00 | 21 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-23 | 22 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-23 01:00 | 22 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-23 02:00 | 22 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-23 03:00 | 22 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-23 04:00 | 22 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-23 05:00 | 22 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-23 06:00 | 22 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-23 07:00 | 22 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-23 08:00 | 22 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-01-23 09:00 | 22 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-01-23 10:00 | 22 | 1 | 1 | 52 | 5.37 | 2.7429
2018-01-23 11:00 | 22 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-01-23 12:00 | 22 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-01-23 13:00 | 22 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-01-23 14:00 | 22 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-01-23 15:00 | 22 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-01-23 16:00 | 22 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-01-23 17:00 | 22 | 1 | 1 | 56 | 5.295 | 2.7043
2018-01-23 18:00 | 22 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-01-23 19:00 | 22 | 1 | 1 | 52 | 5.37 | 2.7429
2018-01-23 20:00 | 22 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-01-23 21:00 | 22 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-23 22:00 | 22 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-01-23 23:00 | 22 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-01-24 | 23 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-01-24 01:00 | 23 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-01-24 02:00 | 23 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-01-24 03:00 | 23 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-01-24 04:00 | 23 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-01-24 05:00 | 23 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-01-24 06:00 | 23 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-01-24 07:00 | 23 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-01-24 08:00 | 23 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-01-24 09:00 | 23 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-01-24 10:00 | 23 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-01-24 11:00 | 23 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-24 12:00 | 23 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-01-24 13:00 | 23 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-01-24 14:00 | 23 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-24 15:00 | 23 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-24 16:00 | 23 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-24 17:00 | 23 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-24 18:00 | 23 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-24 19:00 | 23 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-24 20:00 | 23 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-24 21:00 | 23 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-24 22:00 | 23 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-24 23:00 | 23 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-25 | 24 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-25 01:00 | 24 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-01-25 02:00 | 24 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-01-25 03:00 | 24 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-01-25 04:00 | 24 | 1 | 1 | 24 | 8.0675 | 3.5718
2018-01-25 05:00 | 24 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-01-25 06:00 | 24 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-01-25 07:00 | 24 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-01-25 08:00 | 24 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-01-25 09:00 | 24 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-01-25 10:00 | 24 | 1 | 1 | 29 | 7.307 | 3.3521
2018-01-25 11:00 | 24 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-25 12:00 | 24 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-25 13:00 | 24 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-01-25 14:00 | 24 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-25 15:00 | 24 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-25 16:00 | 24 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-25 17:00 | 24 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-25 18:00 | 24 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-25 19:00 | 24 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-25 20:00 | 24 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-25 21:00 | 24 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-25 22:00 | 24 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-01-25 23:00 | 24 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-26 | 25 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-26 01:00 | 25 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-26 02:00 | 25 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-26 03:00 | 25 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-26 04:00 | 25 | 1 | 1 | 29 | 7.307 | 3.3521
2018-01-26 05:00 | 25 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-26 06:00 | 25 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-26 07:00 | 25 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-26 08:00 | 25 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-26 09:00 | 25 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-26 10:00 | 25 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-26 11:00 | 25 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-26 12:00 | 25 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-26 13:00 | 25 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-26 14:00 | 25 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-26 15:00 | 25 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-26 16:00 | 25 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-01-26 17:00 | 25 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-26 18:00 | 25 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-26 19:00 | 25 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-26 20:00 | 25 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-26 21:00 | 25 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-26 22:00 | 25 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-01-26 23:00 | 25 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-27 | 26 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-01-27 01:00 | 26 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-27 02:00 | 26 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-27 03:00 | 26 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-27 04:00 | 26 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-27 05:00 | 26 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-27 06:00 | 26 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-27 07:00 | 26 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-01-27 08:00 | 26 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-27 09:00 | 26 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-27 10:00 | 26 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-27 11:00 | 26 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-01-27 12:00 | 26 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-27 13:00 | 26 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-01-27 14:00 | 26 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-01-27 15:00 | 26 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-01-27 16:00 | 26 | 1 | 1 | 56 | 5.295 | 2.7043
2018-01-27 17:00 | 26 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-01-27 18:00 | 26 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-01-27 19:00 | 26 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-01-27 20:00 | 26 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-01-27 21:00 | 26 | 1 | 1 | 52 | 5.37 | 2.7429
2018-01-27 22:00 | 26 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-01-27 23:00 | 26 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-01-28 | 27 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-01-28 01:00 | 27 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-01-28 02:00 | 27 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-01-28 03:00 | 27 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-01-28 04:00 | 27 | 1 | 1 | 52 | 5.37 | 2.7429
2018-01-28 05:00 | 27 | 1 | 1 | 52 | 5.37 | 2.7429
2018-01-28 06:00 | 27 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-01-28 07:00 | 27 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-01-28 08:00 | 27 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-01-28 09:00 | 27 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-01-28 10:00 | 27 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-01-28 11:00 | 27 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-28 12:00 | 27 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-28 13:00 | 27 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-01-28 14:00 | 27 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-01-28 15:00 | 27 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-28 16:00 | 27 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-28 17:00 | 27 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-28 18:00 | 27 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-28 19:00 | 27 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-01-28 20:00 | 27 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-28 21:00 | 27 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-01-28 22:00 | 27 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-01-28 23:00 | 27 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-29 | 28 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-01-29 01:00 | 28 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-01-29 02:00 | 28 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-01-29 03:00 | 28 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-01-29 04:00 | 28 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-01-29 05:00 | 28 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-29 06:00 | 28 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-01-29 07:00 | 28 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-01-29 08:00 | 28 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-29 09:00 | 28 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-29 10:00 | 28 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-01-29 11:00 | 28 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-01-29 12:00 | 28 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-29 13:00 | 28 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-01-29 14:00 | 28 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-29 15:00 | 28 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-29 16:00 | 28 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-29 17:00 | 28 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-01-29 18:00 | 28 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-01-29 19:00 | 28 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-01-29 20:00 | 28 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-29 21:00 | 28 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-29 22:00 | 28 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-01-29 23:00 | 28 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-30 | 29 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-01-30 01:00 | 29 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-30 02:00 | 29 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-30 03:00 | 29 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-30 04:00 | 29 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-01-30 05:00 | 29 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-30 06:00 | 29 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-30 07:00 | 29 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-01-30 08:00 | 29 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-30 09:00 | 29 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-30 10:00 | 29 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-01-30 11:00 | 29 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-30 12:00 | 29 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-30 13:00 | 29 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-30 14:00 | 29 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-01-30 15:00 | 29 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-01-30 16:00 | 29 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-01-30 17:00 | 29 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-30 18:00 | 29 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-30 19:00 | 29 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-30 20:00 | 29 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-30 21:00 | 29 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-30 22:00 | 29 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-30 23:00 | 29 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-01-31 | 30 | 1 | 1 | 26 | 7.7488 | 3.4802
2018-01-31 01:00 | 30 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-01-31 02:00 | 30 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-01-31 03:00 | 30 | 1 | 1 | 23.5 | 8.1503 | 3.5955
2018-01-31 04:00 | 30 | 1 | 1 | 22 | 8.4057 | 3.6684
2018-01-31 05:00 | 30 | 1 | 1 | 21 | 8.5821 | 3.7186
2018-01-31 06:00 | 30 | 1 | 1 | 19 | 8.9494 | 3.8227
2018-01-31 07:00 | 30 | 1 | 1 | 19 | 8.9494 | 3.8227
2018-01-31 08:00 | 30 | 1 | 1 | 19 | 8.9494 | 3.8227
2018-01-31 09:00 | 30 | 1 | 1 | 21 | 8.5821 | 3.7186
2018-01-31 10:00 | 30 | 1 | 1 | 23 | 8.2342 | 3.6195
2018-01-31 11:00 | 30 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-01-31 12:00 | 30 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-01-31 13:00 | 30 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-31 14:00 | 30 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-01-31 15:00 | 30 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-31 16:00 | 30 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-31 17:00 | 30 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-31 18:00 | 30 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-31 19:00 | 30 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-01-31 20:00 | 30 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-01-31 21:00 | 30 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-31 22:00 | 30 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-01-31 23:00 | 30 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-01 | 31 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-01 01:00 | 31 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-01 02:00 | 31 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-01 03:00 | 31 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-01 04:00 | 31 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-01 05:00 | 31 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-01 06:00 | 31 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-01 07:00 | 31 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-01 08:00 | 31 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-01 09:00 | 31 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-01 10:00 | 31 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-01 11:00 | 31 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-01 12:00 | 31 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-01 13:00 | 31 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-01 14:00 | 31 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-01 15:00 | 31 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-01 16:00 | 31 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-01 17:00 | 31 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-01 18:00 | 31 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-01 19:00 | 31 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-01 20:00 | 31 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-01 21:00 | 31 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-01 22:00 | 31 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-01 23:00 | 31 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-02 | 32 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-02 01:00 | 32 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-02 02:00 | 32 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-02 03:00 | 32 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-02 04:00 | 32 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-02 05:00 | 32 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-02 06:00 | 32 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-02 07:00 | 32 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-02 08:00 | 32 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-02 09:00 | 32 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-02-02 10:00 | 32 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-02-02 11:00 | 32 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-02-02 12:00 | 32 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-02-02 13:00 | 32 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-02-02 14:00 | 32 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-02-02 15:00 | 32 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-02-02 16:00 | 32 | 1 | 1 | 26 | 7.7488 | 3.4802
2018-02-02 17:00 | 32 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-02-02 18:00 | 32 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-02-02 19:00 | 32 | 1 | 1 | 22 | 8.4057 | 3.6684
2018-02-02 20:00 | 32 | 1 | 1 | 21 | 8.5821 | 3.7186
2018-02-02 21:00 | 32 | 1 | 1 | 19 | 8.9494 | 3.8227
2018-02-02 22:00 | 32 | 1 | 1 | 19 | 8.9494 | 3.8227
2018-02-02 23:00 | 32 | 1 | 1 | 18 | 9.1403 | 3.8767
2018-02-03 | 33 | 1 | 1 | 18 | 9.1403 | 3.8767
2018-02-03 01:00 | 33 | 1 | 1 | 18 | 9.1403 | 3.8767
2018-02-03 02:00 | 33 | 1 | 1 | 18 | 9.1403 | 3.8767
2018-02-03 03:00 | 33 | 1 | 1 | 18 | 9.1403 | 3.8767
2018-02-03 04:00 | 33 | 1 | 1 | 18 | 9.1403 | 3.8767
2018-02-03 05:00 | 33 | 1 | 1 | 18 | 9.1403 | 3.8767
2018-02-03 06:00 | 33 | 1 | 1 | 19 | 8.9494 | 3.8227
2018-02-03 07:00 | 33 | 1 | 1 | 19 | 8.9494 | 3.8227
2018-02-03 08:00 | 33 | 1 | 1 | 19 | 8.9494 | 3.8227
2018-02-03 09:00 | 33 | 1 | 1 | 21 | 8.5821 | 3.7186
2018-02-03 10:00 | 33 | 1 | 1 | 23 | 8.2342 | 3.6195
2018-02-03 11:00 | 33 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-02-03 12:00 | 33 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-02-03 13:00 | 33 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-02-03 14:00 | 33 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-03 15:00 | 33 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-03 16:00 | 33 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-03 17:00 | 33 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-03 18:00 | 33 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-03 19:00 | 33 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-03 20:00 | 33 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-03 21:00 | 33 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-03 22:00 | 33 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-03 23:00 | 33 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-04 | 34 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-04 01:00 | 34 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-04 02:00 | 34 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-04 03:00 | 34 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-04 04:00 | 34 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-04 05:00 | 34 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-04 06:00 | 34 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-04 07:00 | 34 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-04 08:00 | 34 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-04 09:00 | 34 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-04 10:00 | 34 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-04 11:00 | 34 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-04 12:00 | 34 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-04 13:00 | 34 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-02-04 14:00 | 34 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-04 15:00 | 34 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-04 16:00 | 34 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-04 17:00 | 34 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-04 18:00 | 34 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-04 19:00 | 34 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-04 20:00 | 34 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-04 21:00 | 34 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-04 22:00 | 34 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-04 23:00 | 34 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-05 | 35 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-02-05 01:00 | 35 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-05 02:00 | 35 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-05 03:00 | 35 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-05 04:00 | 35 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-05 05:00 | 35 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-05 06:00 | 35 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-05 07:00 | 35 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-02-05 08:00 | 35 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-05 09:00 | 35 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-05 10:00 | 35 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-05 11:00 | 35 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-05 12:00 | 35 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-05 13:00 | 35 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-05 14:00 | 35 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-05 15:00 | 35 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-05 16:00 | 35 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-05 17:00 | 35 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-05 18:00 | 35 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-05 19:00 | 35 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-05 20:00 | 35 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-02-05 21:00 | 35 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-02-05 22:00 | 35 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-02-05 23:00 | 35 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-02-06 | 36 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-02-06 01:00 | 36 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-02-06 02:00 | 36 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-02-06 03:00 | 36 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-02-06 04:00 | 36 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-02-06 05:00 | 36 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-02-06 06:00 | 36 | 1 | 1 | 29 | 7.307 | 3.3521
2018-02-06 07:00 | 36 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-06 08:00 | 36 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-06 09:00 | 36 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-06 10:00 | 36 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-06 11:00 | 36 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-06 12:00 | 36 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-06 13:00 | 36 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-06 14:00 | 36 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-06 15:00 | 36 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-06 16:00 | 36 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-06 17:00 | 36 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-06 18:00 | 36 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-06 19:00 | 36 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-06 20:00 | 36 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-06 21:00 | 36 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-06 22:00 | 36 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-02-06 23:00 | 36 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-07 | 37 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-07 01:00 | 37 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-07 02:00 | 37 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-07 03:00 | 37 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-07 04:00 | 37 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-07 05:00 | 37 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-07 06:00 | 37 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-07 07:00 | 37 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-07 08:00 | 37 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-07 09:00 | 37 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-07 10:00 | 37 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-07 11:00 | 37 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-07 12:00 | 37 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-07 13:00 | 37 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-07 14:00 | 37 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-07 15:00 | 37 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-07 16:00 | 37 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-07 17:00 | 37 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-07 18:00 | 37 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-07 19:00 | 37 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-07 20:00 | 37 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-07 21:00 | 37 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-07 22:00 | 37 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-07 23:00 | 37 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-08 | 38 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-08 01:00 | 38 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-08 02:00 | 38 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-08 03:00 | 38 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-08 04:00 | 38 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-08 05:00 | 38 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-08 06:00 | 38 | 1 | 1 | 29 | 7.307 | 3.3521
2018-02-08 07:00 | 38 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-02-08 08:00 | 38 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-02-08 09:00 | 38 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-02-08 10:00 | 38 | 1 | 1 | 29 | 7.307 | 3.3521
2018-02-08 11:00 | 38 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-08 12:00 | 38 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-08 13:00 | 38 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-08 14:00 | 38 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-08 15:00 | 38 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-08 16:00 | 38 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-08 17:00 | 38 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-08 18:00 | 38 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-08 19:00 | 38 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-08 20:00 | 38 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-08 21:00 | 38 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-08 22:00 | 38 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-08 23:00 | 38 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-09 | 39 | 1 | 1 | 29 | 7.307 | 3.3521
2018-02-09 01:00 | 39 | 1 | 1 | 29 | 7.307 | 3.3521
2018-02-09 02:00 | 39 | 1 | 1 | 29 | 7.307 | 3.3521
2018-02-09 03:00 | 39 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-02-09 04:00 | 39 | 1 | 1 | 29 | 7.307 | 3.3521
2018-02-09 05:00 | 39 | 1 | 1 | 29 | 7.307 | 3.3521
2018-02-09 06:00 | 39 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-02-09 07:00 | 39 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-02-09 08:00 | 39 | 1 | 1 | 29 | 7.307 | 3.3521
2018-02-09 09:00 | 39 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-09 10:00 | 39 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-09 11:00 | 39 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-09 12:00 | 39 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-09 13:00 | 39 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-09 14:00 | 39 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-09 15:00 | 39 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-09 16:00 | 39 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-09 17:00 | 39 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-02-09 18:00 | 39 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-02-09 19:00 | 39 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-09 20:00 | 39 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-09 21:00 | 39 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-09 22:00 | 39 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-09 23:00 | 39 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-10 | 40 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-10 01:00 | 40 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-10 02:00 | 40 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-02-10 03:00 | 40 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-02-10 04:00 | 40 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-02-10 05:00 | 40 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-02-10 06:00 | 40 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-02-10 07:00 | 40 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-10 08:00 | 40 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-02-10 09:00 | 40 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-10 10:00 | 40 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-10 11:00 | 40 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-02-10 12:00 | 40 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-02-10 13:00 | 40 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-02-10 14:00 | 40 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-10 15:00 | 40 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-10 16:00 | 40 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-10 17:00 | 40 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-10 18:00 | 40 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-10 19:00 | 40 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-10 20:00 | 40 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-02-10 21:00 | 40 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-02-10 22:00 | 40 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-10 23:00 | 40 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-02-11 | 41 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-11 01:00 | 41 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-11 02:00 | 41 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-11 03:00 | 41 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-11 04:00 | 41 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-11 05:00 | 41 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-02-11 06:00 | 41 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-11 07:00 | 41 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-11 08:00 | 41 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-11 09:00 | 41 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-11 10:00 | 41 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-11 11:00 | 41 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-11 12:00 | 41 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-11 13:00 | 41 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-02-11 14:00 | 41 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-11 15:00 | 41 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-02-11 16:00 | 41 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-02-11 17:00 | 41 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-02-11 18:00 | 41 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-02-11 19:00 | 41 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-02-11 20:00 | 41 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-02-11 21:00 | 41 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-02-11 22:00 | 41 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-02-11 23:00 | 41 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-02-12 | 42 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-02-12 01:00 | 42 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-12 02:00 | 42 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-02-12 03:00 | 42 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-02-12 04:00 | 42 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-02-12 05:00 | 42 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-12 06:00 | 42 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-12 07:00 | 42 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-12 08:00 | 42 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-02-12 09:00 | 42 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-02-12 10:00 | 42 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-02-12 11:00 | 42 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-02-12 12:00 | 42 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-12 13:00 | 42 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-12 14:00 | 42 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-02-12 15:00 | 42 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-12 16:00 | 42 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-12 17:00 | 42 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-12 18:00 | 42 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-12 19:00 | 42 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-12 20:00 | 42 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-02-12 21:00 | 42 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-12 22:00 | 42 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-12 23:00 | 42 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-02-13 | 43 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-13 01:00 | 43 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-13 02:00 | 43 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-13 03:00 | 43 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-13 04:00 | 43 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-13 05:00 | 43 | 1 | 1 | 29 | 7.307 | 3.3521
2018-02-13 06:00 | 43 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-02-13 07:00 | 43 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-02-13 08:00 | 43 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-02-13 09:00 | 43 | 1 | 1 | 29 | 7.307 | 3.3521
2018-02-13 10:00 | 43 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-13 11:00 | 43 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-13 12:00 | 43 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-13 13:00 | 43 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-13 14:00 | 43 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-02-13 15:00 | 43 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-13 16:00 | 43 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-13 17:00 | 43 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-13 18:00 | 43 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-13 19:00 | 43 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-13 20:00 | 43 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-13 21:00 | 43 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-13 22:00 | 43 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-02-13 23:00 | 43 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-14 | 44 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-14 01:00 | 44 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-14 02:00 | 44 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-14 03:00 | 44 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-14 04:00 | 44 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-14 05:00 | 44 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-14 06:00 | 44 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-14 07:00 | 44 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-14 08:00 | 44 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-14 09:00 | 44 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-14 10:00 | 44 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-02-14 11:00 | 44 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-14 12:00 | 44 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-14 13:00 | 44 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-02-14 14:00 | 44 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-02-14 15:00 | 44 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-14 16:00 | 44 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-02-14 17:00 | 44 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-02-14 18:00 | 44 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-14 19:00 | 44 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-02-14 20:00 | 44 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-02-14 21:00 | 44 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-02-14 22:00 | 44 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-02-14 23:00 | 44 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-02-15 | 45 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-15 01:00 | 45 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-15 02:00 | 45 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-15 03:00 | 45 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-02-15 04:00 | 45 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-02-15 05:00 | 45 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-02-15 06:00 | 45 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-15 07:00 | 45 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-15 08:00 | 45 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-15 09:00 | 45 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-02-15 10:00 | 45 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-02-15 11:00 | 45 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-15 12:00 | 45 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-02-15 13:00 | 45 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-02-15 14:00 | 45 | 1 | 1 | 56 | 5.295 | 2.7043
2018-02-15 15:00 | 45 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-02-15 16:00 | 45 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-02-15 17:00 | 45 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-02-15 18:00 | 45 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-02-15 19:00 | 45 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-02-15 20:00 | 45 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-02-15 21:00 | 45 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-02-15 22:00 | 45 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-02-15 23:00 | 45 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-02-16 | 46 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-02-16 01:00 | 46 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-02-16 02:00 | 46 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-02-16 03:00 | 46 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-02-16 04:00 | 46 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-02-16 05:00 | 46 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-02-16 06:00 | 46 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-02-16 07:00 | 46 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-02-16 08:00 | 46 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-16 09:00 | 46 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-02-16 10:00 | 46 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-02-16 11:00 | 46 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-02-16 12:00 | 46 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-02-16 13:00 | 46 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-02-16 14:00 | 46 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-02-16 15:00 | 46 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-02-16 16:00 | 46 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-02-16 17:00 | 46 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-02-16 18:00 | 46 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-16 19:00 | 46 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-16 20:00 | 46 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-02-16 21:00 | 46 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-16 22:00 | 46 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-02-16 23:00 | 46 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-17 | 47 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-17 01:00 | 47 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-17 02:00 | 47 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-17 03:00 | 47 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-17 04:00 | 47 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-17 05:00 | 47 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-17 06:00 | 47 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-02-17 07:00 | 47 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-02-17 08:00 | 47 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-02-17 09:00 | 47 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-17 10:00 | 47 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-17 11:00 | 47 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-02-17 12:00 | 47 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-17 13:00 | 47 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-17 14:00 | 47 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-17 15:00 | 47 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-17 16:00 | 47 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-17 17:00 | 47 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-17 18:00 | 47 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-17 19:00 | 47 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-17 20:00 | 47 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-17 21:00 | 47 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-17 22:00 | 47 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-17 23:00 | 47 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-18 | 48 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-18 01:00 | 48 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-02-18 02:00 | 48 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-18 03:00 | 48 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-18 04:00 | 48 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-02-18 05:00 | 48 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-18 06:00 | 48 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-18 07:00 | 48 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-18 08:00 | 48 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-18 09:00 | 48 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-18 10:00 | 48 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-18 11:00 | 48 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-18 12:00 | 48 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-18 13:00 | 48 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-18 14:00 | 48 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-18 15:00 | 48 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-18 16:00 | 48 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-18 17:00 | 48 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-18 18:00 | 48 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-18 19:00 | 48 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-18 20:00 | 48 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-02-18 21:00 | 48 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-02-18 22:00 | 48 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-18 23:00 | 48 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-19 | 49 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-19 01:00 | 49 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-19 02:00 | 49 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-02-19 03:00 | 49 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-19 04:00 | 49 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-19 05:00 | 49 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-02-19 06:00 | 49 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-19 07:00 | 49 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-19 08:00 | 49 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-02-19 09:00 | 49 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-19 10:00 | 49 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-19 11:00 | 49 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-02-19 12:00 | 49 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-02-19 13:00 | 49 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-19 14:00 | 49 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-19 15:00 | 49 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-19 16:00 | 49 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-02-19 17:00 | 49 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-19 18:00 | 49 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-19 19:00 | 49 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-19 20:00 | 49 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-02-19 21:00 | 49 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-02-19 22:00 | 49 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-02-19 23:00 | 49 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-20 | 50 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-02-20 01:00 | 50 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-20 02:00 | 50 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-02-20 03:00 | 50 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-02-20 04:00 | 50 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-02-20 05:00 | 50 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-02-20 06:00 | 50 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-02-20 07:00 | 50 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-02-20 08:00 | 50 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-20 09:00 | 50 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-20 10:00 | 50 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-02-20 11:00 | 50 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-02-20 12:00 | 50 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-02-20 13:00 | 50 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-02-20 14:00 | 50 | 1 | 1 | 64 | 5.3779 | 2.687
2018-02-20 15:00 | 50 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-02-20 16:00 | 50 | 1 | 1 | 67 | 5.489 | 2.7011
2018-02-20 17:00 | 50 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-02-20 18:00 | 50 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-02-20 19:00 | 50 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-02-20 20:00 | 50 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-02-20 21:00 | 50 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-02-20 22:00 | 50 | 1 | 1 | 56 | 5.295 | 2.7043
2018-02-20 23:00 | 50 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-02-21 | 51 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-02-21 01:00 | 51 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-02-21 02:00 | 51 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-21 03:00 | 51 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-21 04:00 | 51 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-02-21 05:00 | 51 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-02-21 06:00 | 51 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-02-21 07:00 | 51 | 1 | 1 | 56 | 5.295 | 2.7043
2018-02-21 08:00 | 51 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-02-21 09:00 | 51 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-02-21 10:00 | 51 | 1 | 1 | 64 | 5.3779 | 2.687
2018-02-21 11:00 | 51 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-02-21 12:00 | 51 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-02-21 13:00 | 51 | 1 | 1 | 74 | 5.918 | 2.7776
2018-02-21 14:00 | 51 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-02-21 15:00 | 51 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-02-21 16:00 | 51 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-02-21 17:00 | 51 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-02-21 18:00 | 51 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-02-21 19:00 | 51 | 1 | 1 | 74 | 5.918 | 2.7776
2018-02-21 20:00 | 51 | 1 | 1 | 67 | 5.489 | 2.7011
2018-02-21 21:00 | 51 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-02-21 22:00 | 51 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-02-21 23:00 | 51 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-02-22 | 52 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-02-22 01:00 | 52 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-02-22 02:00 | 52 | 1 | 1 | 56 | 5.295 | 2.7043
2018-02-22 03:00 | 52 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-02-22 04:00 | 52 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-02-22 05:00 | 52 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-02-22 06:00 | 52 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-22 07:00 | 52 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-22 08:00 | 52 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-02-22 09:00 | 52 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-22 10:00 | 52 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-22 11:00 | 52 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-22 12:00 | 52 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-22 13:00 | 52 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-22 14:00 | 52 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-22 15:00 | 52 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-22 16:00 | 52 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-22 17:00 | 52 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-22 18:00 | 52 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-22 19:00 | 52 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-22 20:00 | 52 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-22 21:00 | 52 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-22 22:00 | 52 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-22 23:00 | 52 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-23 | 53 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-23 01:00 | 53 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-23 02:00 | 53 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-23 03:00 | 53 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-23 04:00 | 53 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-23 05:00 | 53 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-23 06:00 | 53 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-23 07:00 | 53 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-23 08:00 | 53 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-23 09:00 | 53 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-23 10:00 | 53 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-23 11:00 | 53 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-23 12:00 | 53 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-23 13:00 | 53 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-23 14:00 | 53 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-23 15:00 | 53 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-23 16:00 | 53 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-02-23 17:00 | 53 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-02-23 18:00 | 53 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-23 19:00 | 53 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-23 20:00 | 53 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-23 21:00 | 53 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-23 22:00 | 53 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-02-23 23:00 | 53 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-24 | 54 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-24 01:00 | 54 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-24 02:00 | 54 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-24 03:00 | 54 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-24 04:00 | 54 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-24 05:00 | 54 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-24 06:00 | 54 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-24 07:00 | 54 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-24 08:00 | 54 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-24 09:00 | 54 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-24 10:00 | 54 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-02-24 11:00 | 54 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-02-24 12:00 | 54 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-02-24 13:00 | 54 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-02-24 14:00 | 54 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-02-24 15:00 | 54 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-24 16:00 | 54 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-24 17:00 | 54 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-24 18:00 | 54 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-24 19:00 | 54 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-02-24 20:00 | 54 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-24 21:00 | 54 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-24 22:00 | 54 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-24 23:00 | 54 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-25 | 55 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-25 01:00 | 55 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-25 02:00 | 55 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-25 03:00 | 55 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-25 04:00 | 55 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-02-25 05:00 | 55 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-25 06:00 | 55 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-25 07:00 | 55 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-02-25 08:00 | 55 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-25 09:00 | 55 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-25 10:00 | 55 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-02-25 11:00 | 55 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-25 12:00 | 55 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-25 13:00 | 55 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-25 14:00 | 55 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-25 15:00 | 55 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-25 16:00 | 55 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-02-25 17:00 | 55 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-25 18:00 | 55 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-25 19:00 | 55 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-25 20:00 | 55 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-25 21:00 | 55 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-25 22:00 | 55 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-25 23:00 | 55 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-26 | 56 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-26 01:00 | 56 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-26 02:00 | 56 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-26 03:00 | 56 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-26 04:00 | 56 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-26 05:00 | 56 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-26 06:00 | 56 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-26 07:00 | 56 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-26 08:00 | 56 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-26 09:00 | 56 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-26 10:00 | 56 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-26 11:00 | 56 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-26 12:00 | 56 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-26 13:00 | 56 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-02-26 14:00 | 56 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-26 15:00 | 56 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-02-26 16:00 | 56 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-26 17:00 | 56 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-26 18:00 | 56 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-26 19:00 | 56 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-02-26 20:00 | 56 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-26 21:00 | 56 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-26 22:00 | 56 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-02-26 23:00 | 56 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-27 | 57 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-27 01:00 | 57 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-02-27 02:00 | 57 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-27 03:00 | 57 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-27 04:00 | 57 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-27 05:00 | 57 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-27 06:00 | 57 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-02-27 07:00 | 57 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-02-27 08:00 | 57 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-27 09:00 | 57 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-27 10:00 | 57 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-02-27 11:00 | 57 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-02-27 12:00 | 57 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-27 13:00 | 57 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-27 14:00 | 57 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-02-27 15:00 | 57 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-02-27 16:00 | 57 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-02-27 17:00 | 57 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-27 18:00 | 57 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-27 19:00 | 57 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-02-27 20:00 | 57 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-27 21:00 | 57 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-27 22:00 | 57 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-27 23:00 | 57 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-28 | 58 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-28 01:00 | 58 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-28 02:00 | 58 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-28 03:00 | 58 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-28 04:00 | 58 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-28 05:00 | 58 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-02-28 06:00 | 58 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-28 07:00 | 58 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-28 08:00 | 58 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-02-28 09:00 | 58 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-02-28 10:00 | 58 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-02-28 11:00 | 58 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-02-28 12:00 | 58 | 1 | 1 | 52 | 5.37 | 2.7429
2018-02-28 13:00 | 58 | 1 | 1 | 56 | 5.295 | 2.7043
2018-02-28 14:00 | 58 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-02-28 15:00 | 58 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-02-28 16:00 | 58 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-02-28 17:00 | 58 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-02-28 18:00 | 58 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-02-28 19:00 | 58 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-02-28 20:00 | 58 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-02-28 21:00 | 58 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-02-28 22:00 | 58 | 1 | 1 | 56 | 5.295 | 2.7043
2018-02-28 23:00 | 58 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-03-01 | 59 | 1 | 1 | 56 | 5.295 | 2.7043
2018-03-01 01:00 | 59 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-03-01 02:00 | 59 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-03-01 03:00 | 59 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-03-01 04:00 | 59 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-03-01 05:00 | 59 | 1 | 1 | 52 | 5.37 | 2.7429
2018-03-01 06:00 | 59 | 1 | 1 | 52 | 5.37 | 2.7429
2018-03-01 07:00 | 59 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-01 08:00 | 59 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-03-01 09:00 | 59 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-03-01 10:00 | 59 | 1 | 1 | 56 | 5.295 | 2.7043
2018-03-01 11:00 | 59 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-03-01 12:00 | 59 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-03-01 13:00 | 59 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-03-01 14:00 | 59 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-03-01 15:00 | 59 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-03-01 16:00 | 59 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-03-01 17:00 | 59 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-03-01 18:00 | 59 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-03-01 19:00 | 59 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-03-01 20:00 | 59 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-03-01 21:00 | 59 | 1 | 1 | 52 | 5.37 | 2.7429
2018-03-01 22:00 | 59 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-03-01 23:00 | 59 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-02 | 60 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-03-02 01:00 | 60 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-02 02:00 | 60 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-02 03:00 | 60 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-03-02 04:00 | 60 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-02 05:00 | 60 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-03-02 06:00 | 60 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-02 07:00 | 60 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-02 08:00 | 60 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-02 09:00 | 60 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-02 10:00 | 60 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-02 11:00 | 60 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-02 12:00 | 60 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-02 13:00 | 60 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-02 14:00 | 60 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-02 15:00 | 60 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-02 16:00 | 60 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-02 17:00 | 60 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-02 18:00 | 60 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-02 19:00 | 60 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-02 20:00 | 60 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-02 21:00 | 60 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-02 22:00 | 60 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-02 23:00 | 60 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-03 | 61 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-03 01:00 | 61 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-03 02:00 | 61 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-03 03:00 | 61 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-03 04:00 | 61 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-03 05:00 | 61 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-03 06:00 | 61 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-03 07:00 | 61 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-03 08:00 | 61 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-03 09:00 | 61 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-03 10:00 | 61 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-03 11:00 | 61 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-03 12:00 | 61 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-03 13:00 | 61 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-03 14:00 | 61 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-03 15:00 | 61 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-03 16:00 | 61 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-03 17:00 | 61 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-03 18:00 | 61 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-03 19:00 | 61 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-03 20:00 | 61 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-03 21:00 | 61 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-03 22:00 | 61 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-03-03 23:00 | 61 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-04 | 62 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-03-04 01:00 | 62 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-03-04 02:00 | 62 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-04 03:00 | 62 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-04 04:00 | 62 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-04 05:00 | 62 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-04 06:00 | 62 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-04 07:00 | 62 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-04 08:00 | 62 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-04 09:00 | 62 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-04 10:00 | 62 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-03-04 11:00 | 62 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-04 12:00 | 62 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-04 13:00 | 62 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-04 14:00 | 62 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-04 15:00 | 62 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-04 16:00 | 62 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-04 17:00 | 62 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-04 18:00 | 62 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-04 19:00 | 62 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-04 20:00 | 62 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-04 21:00 | 62 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-04 22:00 | 62 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-04 23:00 | 62 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-05 | 63 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-05 01:00 | 63 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-05 02:00 | 63 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-05 03:00 | 63 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-05 04:00 | 63 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-05 05:00 | 63 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-05 06:00 | 63 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-05 07:00 | 63 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-05 08:00 | 63 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-05 09:00 | 63 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-05 10:00 | 63 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-05 11:00 | 63 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-05 12:00 | 63 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-05 13:00 | 63 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-05 14:00 | 63 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-05 15:00 | 63 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-05 16:00 | 63 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-05 17:00 | 63 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-05 18:00 | 63 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-05 19:00 | 63 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-05 20:00 | 63 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-05 21:00 | 63 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-05 22:00 | 63 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-05 23:00 | 63 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-06 | 64 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-06 01:00 | 64 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-06 02:00 | 64 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-06 03:00 | 64 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-06 04:00 | 64 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-06 05:00 | 64 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-06 06:00 | 64 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-06 07:00 | 64 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-06 08:00 | 64 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-06 09:00 | 64 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-06 10:00 | 64 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-06 11:00 | 64 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-06 12:00 | 64 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-06 13:00 | 64 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-06 14:00 | 64 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-06 15:00 | 64 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-06 16:00 | 64 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-06 17:00 | 64 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-06 18:00 | 64 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-06 19:00 | 64 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-06 20:00 | 64 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-06 21:00 | 64 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-06 22:00 | 64 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-06 23:00 | 64 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-07 | 65 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-07 01:00 | 65 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-07 02:00 | 65 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-07 03:00 | 65 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-07 04:00 | 65 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-07 05:00 | 65 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-07 06:00 | 65 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-07 07:00 | 65 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-07 08:00 | 65 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-07 09:00 | 65 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-07 10:00 | 65 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-07 11:00 | 65 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-07 12:00 | 65 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-07 13:00 | 65 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-07 14:00 | 65 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-07 15:00 | 65 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-07 16:00 | 65 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-07 17:00 | 65 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-07 18:00 | 65 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-07 19:00 | 65 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-07 20:00 | 65 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-07 21:00 | 65 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-07 22:00 | 65 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-07 23:00 | 65 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-08 | 66 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-08 01:00 | 66 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-08 02:00 | 66 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-08 03:00 | 66 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-08 04:00 | 66 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-08 05:00 | 66 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-08 06:00 | 66 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-08 07:00 | 66 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-08 08:00 | 66 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-08 09:00 | 66 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-08 10:00 | 66 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-08 11:00 | 66 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-08 12:00 | 66 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-08 13:00 | 66 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-08 14:00 | 66 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-08 15:00 | 66 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-08 16:00 | 66 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-08 17:00 | 66 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-08 18:00 | 66 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-08 19:00 | 66 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-08 20:00 | 66 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-08 21:00 | 66 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-08 22:00 | 66 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-08 23:00 | 66 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-09 | 67 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-09 01:00 | 67 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-09 02:00 | 67 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-09 03:00 | 67 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-09 04:00 | 67 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-03-09 05:00 | 67 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-03-09 06:00 | 67 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-03-09 07:00 | 67 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-03-09 08:00 | 67 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-03-09 09:00 | 67 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-09 10:00 | 67 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-09 11:00 | 67 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-09 12:00 | 67 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-09 13:00 | 67 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-09 14:00 | 67 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-09 15:00 | 67 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-09 16:00 | 67 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-03-09 17:00 | 67 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-09 18:00 | 67 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-09 19:00 | 67 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-09 20:00 | 67 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-09 21:00 | 67 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-09 22:00 | 67 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-09 23:00 | 67 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-10 | 68 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-10 01:00 | 68 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-10 02:00 | 68 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-10 03:00 | 68 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-10 04:00 | 68 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-10 05:00 | 68 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-10 06:00 | 68 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-10 07:00 | 68 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-10 08:00 | 68 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-10 09:00 | 68 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-10 10:00 | 68 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-10 11:00 | 68 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-10 12:00 | 68 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-10 13:00 | 68 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-10 14:00 | 68 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-10 15:00 | 68 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-10 16:00 | 68 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-10 17:00 | 68 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-10 18:00 | 68 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-10 19:00 | 68 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-10 20:00 | 68 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-10 21:00 | 68 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-10 22:00 | 68 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-10 23:00 | 68 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-11 | 69 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-11 01:00 | 69 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-11 03:00 | 69 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-11 04:00 | 69 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-11 05:00 | 69 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-11 06:00 | 69 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-11 07:00 | 69 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-11 08:00 | 69 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-11 09:00 | 69 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-11 10:00 | 69 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-11 11:00 | 69 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-11 12:00 | 69 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-11 13:00 | 69 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-11 14:00 | 69 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-11 15:00 | 69 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-11 16:00 | 69 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-11 17:00 | 69 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-11 18:00 | 69 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-11 19:00 | 69 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-11 20:00 | 69 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-11 21:00 | 69 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-11 22:00 | 69 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-11 23:00 | 69 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-12 | 70 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-12 01:00 | 70 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-12 02:00 | 70 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-12 03:00 | 70 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-12 04:00 | 70 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-12 05:00 | 70 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-03-12 06:00 | 70 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-12 07:00 | 70 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-12 08:00 | 70 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-12 09:00 | 70 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-12 10:00 | 70 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-12 11:00 | 70 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-12 12:00 | 70 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-12 13:00 | 70 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-12 14:00 | 70 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-12 15:00 | 70 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-12 16:00 | 70 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-12 17:00 | 70 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-12 18:00 | 70 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-12 19:00 | 70 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-12 20:00 | 70 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-12 21:00 | 70 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-12 22:00 | 70 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-12 23:00 | 70 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-13 | 71 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-13 01:00 | 71 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-13 02:00 | 71 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-13 03:00 | 71 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-13 04:00 | 71 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-13 05:00 | 71 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-13 06:00 | 71 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-13 07:00 | 71 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-13 08:00 | 71 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-13 09:00 | 71 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-13 10:00 | 71 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-13 11:00 | 71 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-13 12:00 | 71 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-13 13:00 | 71 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-13 14:00 | 71 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-13 15:00 | 71 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-13 16:00 | 71 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-13 17:00 | 71 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-13 18:00 | 71 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-13 19:00 | 71 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-13 20:00 | 71 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-13 21:00 | 71 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-13 22:00 | 71 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-13 23:00 | 71 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-14 | 72 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-14 01:00 | 72 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-14 02:00 | 72 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-14 03:00 | 72 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-14 04:00 | 72 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-14 05:00 | 72 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-03-14 06:00 | 72 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-03-14 07:00 | 72 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-03-14 08:00 | 72 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-03-14 09:00 | 72 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-14 10:00 | 72 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-14 11:00 | 72 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-14 12:00 | 72 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-14 13:00 | 72 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-14 14:00 | 72 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-14 15:00 | 72 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-14 16:00 | 72 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-14 17:00 | 72 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-14 18:00 | 72 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-14 19:00 | 72 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-14 20:00 | 72 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-14 21:00 | 72 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-14 22:00 | 72 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-14 23:00 | 72 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-15 | 73 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-15 01:00 | 73 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-15 02:00 | 73 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-15 03:00 | 73 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-15 04:00 | 73 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-15 05:00 | 73 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-15 06:00 | 73 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-15 07:00 | 73 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-15 08:00 | 73 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-15 09:00 | 73 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-15 10:00 | 73 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-15 11:00 | 73 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-15 12:00 | 73 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-15 13:00 | 73 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-15 14:00 | 73 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-15 15:00 | 73 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-15 16:00 | 73 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-15 17:00 | 73 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-15 18:00 | 73 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-15 19:00 | 73 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-03-15 20:00 | 73 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-15 21:00 | 73 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-15 22:00 | 73 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-15 23:00 | 73 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-16 | 74 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-16 01:00 | 74 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-16 02:00 | 74 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-16 03:00 | 74 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-16 04:00 | 74 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-16 05:00 | 74 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-16 06:00 | 74 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-16 07:00 | 74 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-16 08:00 | 74 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-16 09:00 | 74 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-16 10:00 | 74 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-16 11:00 | 74 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-16 12:00 | 74 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-16 13:00 | 74 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-16 14:00 | 74 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-16 15:00 | 74 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-16 16:00 | 74 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-16 17:00 | 74 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-16 18:00 | 74 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-16 19:00 | 74 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-16 20:00 | 74 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-16 21:00 | 74 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-16 22:00 | 74 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-16 23:00 | 74 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-17 | 75 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-17 01:00 | 75 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-03-17 02:00 | 75 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-03-17 03:00 | 75 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-03-17 04:00 | 75 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-03-17 05:00 | 75 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-03-17 06:00 | 75 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-03-17 07:00 | 75 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-03-17 08:00 | 75 | 1 | 1 | 29 | 7.307 | 3.3521
2018-03-17 09:00 | 75 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-03-17 10:00 | 75 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-17 11:00 | 75 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-17 12:00 | 75 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-17 13:00 | 75 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-17 14:00 | 75 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-17 15:00 | 75 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-17 16:00 | 75 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-17 17:00 | 75 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-17 18:00 | 75 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-17 19:00 | 75 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-17 20:00 | 75 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-17 21:00 | 75 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-17 22:00 | 75 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-17 23:00 | 75 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-18 | 76 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-18 01:00 | 76 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-18 02:00 | 76 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-18 03:00 | 76 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-18 04:00 | 76 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-18 05:00 | 76 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-03-18 06:00 | 76 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-03-18 07:00 | 76 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-03-18 08:00 | 76 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-03-18 09:00 | 76 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-03-18 10:00 | 76 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-03-18 11:00 | 76 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-03-18 12:00 | 76 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-18 13:00 | 76 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-18 14:00 | 76 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-18 15:00 | 76 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-18 16:00 | 76 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-18 17:00 | 76 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-18 18:00 | 76 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-18 19:00 | 76 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-18 20:00 | 76 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-03-18 21:00 | 76 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-18 22:00 | 76 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-18 23:00 | 76 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-19 | 77 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-19 01:00 | 77 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-19 02:00 | 77 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-19 03:00 | 77 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-19 04:00 | 77 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-19 05:00 | 77 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-19 06:00 | 77 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-19 07:00 | 77 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-19 08:00 | 77 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-19 09:00 | 77 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-19 10:00 | 77 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-19 11:00 | 77 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-19 12:00 | 77 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-19 13:00 | 77 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-19 14:00 | 77 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-19 15:00 | 77 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-19 16:00 | 77 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-19 17:00 | 77 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-19 18:00 | 77 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-19 19:00 | 77 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-19 20:00 | 77 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-19 21:00 | 77 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-19 22:00 | 77 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-19 23:00 | 77 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-20 | 78 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-20 01:00 | 78 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-20 02:00 | 78 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-20 03:00 | 78 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-20 04:00 | 78 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-20 05:00 | 78 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-03-20 06:00 | 78 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-03-20 07:00 | 78 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-03-20 08:00 | 78 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-03-20 09:00 | 78 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-20 10:00 | 78 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-20 11:00 | 78 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-03-20 12:00 | 78 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-20 13:00 | 78 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-20 14:00 | 78 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-20 15:00 | 78 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-20 16:00 | 78 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-20 17:00 | 78 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-20 18:00 | 78 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-20 19:00 | 78 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-20 20:00 | 78 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-20 21:00 | 78 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-20 22:00 | 78 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-20 23:00 | 78 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-21 | 79 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-21 01:00 | 79 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-21 02:00 | 79 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-21 03:00 | 79 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-21 04:00 | 79 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-21 05:00 | 79 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-21 06:00 | 79 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-21 07:00 | 79 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-21 08:00 | 79 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-21 09:00 | 79 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-21 10:00 | 79 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-03-21 11:00 | 79 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-03-21 12:00 | 79 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-21 13:00 | 79 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-21 14:00 | 79 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-03-21 15:00 | 79 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-21 16:00 | 79 | 1 | 1 | 33.5 | 6.7261 | 3.1809
2018-03-21 17:00 | 79 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-03-21 18:00 | 79 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-21 19:00 | 79 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-21 20:00 | 79 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-21 21:00 | 79 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-21 22:00 | 79 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-21 23:00 | 79 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-03-22 | 80 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-22 01:00 | 80 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-03-22 02:00 | 80 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-03-22 03:00 | 80 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-22 04:00 | 80 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-22 05:00 | 80 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-22 06:00 | 80 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-22 07:00 | 80 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-22 08:00 | 80 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-22 09:00 | 80 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-22 10:00 | 80 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-22 11:00 | 80 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-03-22 12:00 | 80 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-22 13:00 | 80 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-22 14:00 | 80 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-03-22 15:00 | 80 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-22 16:00 | 80 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-22 17:00 | 80 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-03-22 18:00 | 80 | 1 | 1 | 52 | 5.37 | 2.7429
2018-03-22 19:00 | 80 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-22 20:00 | 80 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-03-22 21:00 | 80 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-22 22:00 | 80 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-22 23:00 | 80 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-23 | 81 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-23 01:00 | 81 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-23 02:00 | 81 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-23 03:00 | 81 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-23 04:00 | 81 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-23 05:00 | 81 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-23 06:00 | 81 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-23 07:00 | 81 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-23 08:00 | 81 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-23 09:00 | 81 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-23 10:00 | 81 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-23 11:00 | 81 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-03-23 12:00 | 81 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-23 13:00 | 81 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-23 14:00 | 81 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-23 15:00 | 81 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-23 16:00 | 81 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-23 17:00 | 81 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-23 18:00 | 81 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-23 19:00 | 81 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-23 20:00 | 81 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-23 21:00 | 81 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-23 22:00 | 81 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-23 23:00 | 81 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-24 | 82 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-24 01:00 | 82 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-24 02:00 | 82 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-24 03:00 | 82 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-24 04:00 | 82 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-24 05:00 | 82 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-24 06:00 | 82 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-24 07:00 | 82 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-24 08:00 | 82 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-24 09:00 | 82 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-24 10:00 | 82 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-24 11:00 | 82 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-03-24 12:00 | 82 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-24 13:00 | 82 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-24 14:00 | 82 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-03-24 15:00 | 82 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-24 16:00 | 82 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-24 17:00 | 82 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-24 18:00 | 82 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-24 19:00 | 82 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-24 20:00 | 82 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-03-24 21:00 | 82 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-24 22:00 | 82 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-24 23:00 | 82 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-25 | 83 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-25 01:00 | 83 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-25 02:00 | 83 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-25 03:00 | 83 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-25 04:00 | 83 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-25 05:00 | 83 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-25 06:00 | 83 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-25 07:00 | 83 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-25 08:00 | 83 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-25 09:00 | 83 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-25 10:00 | 83 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-25 11:00 | 83 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-25 12:00 | 83 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-25 13:00 | 83 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-25 14:00 | 83 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-03-25 15:00 | 83 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-25 16:00 | 83 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-25 17:00 | 83 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-25 18:00 | 83 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-25 19:00 | 83 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-25 20:00 | 83 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-03-25 21:00 | 83 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-25 22:00 | 83 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-25 23:00 | 83 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-26 | 84 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-26 01:00 | 84 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-26 02:00 | 84 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-26 03:00 | 84 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-26 04:00 | 84 | 1 | 1 | 35.5 | 6.4995 | 3.113
2018-03-26 05:00 | 84 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-26 06:00 | 84 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-26 07:00 | 84 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-03-26 08:00 | 84 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-26 09:00 | 84 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-26 10:00 | 84 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-26 11:00 | 84 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-26 12:00 | 84 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-03-26 13:00 | 84 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-03-26 14:00 | 84 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-26 15:00 | 84 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-26 16:00 | 84 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-26 17:00 | 84 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-03-26 18:00 | 84 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-26 19:00 | 84 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-03-26 20:00 | 84 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-26 21:00 | 84 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-26 22:00 | 84 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-26 23:00 | 84 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-27 | 85 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-27 01:00 | 85 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-27 02:00 | 85 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-03-27 03:00 | 85 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-27 04:00 | 85 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-27 05:00 | 85 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-27 06:00 | 85 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-03-27 07:00 | 85 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-27 08:00 | 85 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-03-27 09:00 | 85 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-03-27 10:00 | 85 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-27 11:00 | 85 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-27 12:00 | 85 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-27 13:00 | 85 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-27 14:00 | 85 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-03-27 15:00 | 85 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-27 16:00 | 85 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-27 17:00 | 85 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-03-27 18:00 | 85 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-27 19:00 | 85 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-27 20:00 | 85 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-27 21:00 | 85 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-27 22:00 | 85 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-27 23:00 | 85 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-28 | 86 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-28 01:00 | 86 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-28 02:00 | 86 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-28 03:00 | 86 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-28 04:00 | 86 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-28 05:00 | 86 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-03-28 06:00 | 86 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-28 07:00 | 86 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-28 08:00 | 86 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-28 09:00 | 86 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-28 10:00 | 86 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-28 11:00 | 86 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-03-28 12:00 | 86 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-28 13:00 | 86 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-28 14:00 | 86 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-03-28 15:00 | 86 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-28 16:00 | 86 | 1 | 1 | 52 | 5.37 | 2.7429
2018-03-28 17:00 | 86 | 1 | 1 | 52 | 5.37 | 2.7429
2018-03-28 18:00 | 86 | 1 | 1 | 52 | 5.37 | 2.7429
2018-03-28 19:00 | 86 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-28 20:00 | 86 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-03-28 21:00 | 86 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-28 22:00 | 86 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-28 23:00 | 86 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-29 | 87 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-29 01:00 | 87 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-29 02:00 | 87 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-29 03:00 | 87 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-29 04:00 | 87 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-03-29 05:00 | 87 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-29 06:00 | 87 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-29 07:00 | 87 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-03-29 08:00 | 87 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-29 09:00 | 87 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-29 10:00 | 87 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-29 11:00 | 87 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-29 12:00 | 87 | 1 | 1 | 52 | 5.37 | 2.7429
2018-03-29 13:00 | 87 | 1 | 1 | 52 | 5.37 | 2.7429
2018-03-29 14:00 | 87 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-03-29 15:00 | 87 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-29 16:00 | 87 | 1 | 1 | 52 | 5.37 | 2.7429
2018-03-29 17:00 | 87 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-29 18:00 | 87 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-29 19:00 | 87 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-29 20:00 | 87 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-29 21:00 | 87 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-03-29 22:00 | 87 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-03-29 23:00 | 87 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-03-30 | 88 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-30 01:00 | 88 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-30 02:00 | 88 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-03-30 03:00 | 88 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-30 04:00 | 88 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-03-30 05:00 | 88 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-03-30 06:00 | 88 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-30 07:00 | 88 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-03-30 08:00 | 88 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-03-30 09:00 | 88 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-03-30 10:00 | 88 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-03-30 11:00 | 88 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-03-30 12:00 | 88 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-03-30 13:00 | 88 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-03-30 14:00 | 88 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-03-30 15:00 | 88 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-03-30 16:00 | 88 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-03-30 17:00 | 88 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-03-30 18:00 | 88 | 1 | 1 | 52 | 5.37 | 2.7429
2018-03-30 19:00 | 88 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-30 20:00 | 88 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-30 21:00 | 88 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-30 22:00 | 88 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-30 23:00 | 88 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-03-31 | 89 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-31 01:00 | 89 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-31 02:00 | 89 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-03-31 03:00 | 89 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-31 04:00 | 89 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-31 05:00 | 89 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-31 06:00 | 89 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-31 07:00 | 89 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-03-31 08:00 | 89 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-03-31 09:00 | 89 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-03-31 10:00 | 89 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-03-31 11:00 | 89 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-31 12:00 | 89 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-03-31 13:00 | 89 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-03-31 14:00 | 89 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-03-31 15:00 | 89 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-03-31 16:00 | 89 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-03-31 17:00 | 89 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-03-31 18:00 | 89 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-31 19:00 | 89 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-03-31 20:00 | 89 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-03-31 21:00 | 89 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-31 22:00 | 89 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-03-31 23:00 | 89 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-04-01 | 90 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-01 01:00 | 90 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-04-01 02:00 | 90 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-04-01 03:00 | 90 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-01 04:00 | 90 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-01 05:00 | 90 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-04-01 06:00 | 90 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-01 07:00 | 90 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-01 08:00 | 90 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-04-01 09:00 | 90 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-01 10:00 | 90 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-01 11:00 | 90 | 1 | 1 | 56 | 5.295 | 2.7043
2018-04-01 12:00 | 90 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-01 13:00 | 90 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-01 14:00 | 90 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-01 15:00 | 90 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-01 16:00 | 90 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-01 17:00 | 90 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-01 18:00 | 90 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-01 19:00 | 90 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-01 20:00 | 90 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-01 21:00 | 90 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-01 22:00 | 90 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-01 23:00 | 90 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-02 | 91 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-02 01:00 | 91 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-02 02:00 | 91 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-02 03:00 | 91 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-02 04:00 | 91 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-02 05:00 | 91 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-04-02 06:00 | 91 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-04-02 07:00 | 91 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-04-02 08:00 | 91 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-04-02 09:00 | 91 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-04-02 10:00 | 91 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-04-02 11:00 | 91 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-04-02 12:00 | 91 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-04-02 13:00 | 91 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-04-02 14:00 | 91 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-04-02 15:00 | 91 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-04-02 16:00 | 91 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-02 17:00 | 91 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-02 18:00 | 91 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-02 19:00 | 91 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-02 20:00 | 91 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-02 21:00 | 91 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-02 22:00 | 91 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-02 23:00 | 91 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-04-03 | 92 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-03 01:00 | 92 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-03 02:00 | 92 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-03 03:00 | 92 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-03 04:00 | 92 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-03 05:00 | 92 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-03 06:00 | 92 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-03 07:00 | 92 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-03 08:00 | 92 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-03 09:00 | 92 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-03 10:00 | 92 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-03 11:00 | 92 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-03 12:00 | 92 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-03 13:00 | 92 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-03 14:00 | 92 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-03 15:00 | 92 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-03 16:00 | 92 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-03 17:00 | 92 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-03 18:00 | 92 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-03 19:00 | 92 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-03 20:00 | 92 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-03 21:00 | 92 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-03 22:00 | 92 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-03 23:00 | 92 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-04 | 93 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-04 01:00 | 93 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-04 02:00 | 93 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-04 03:00 | 93 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-04 04:00 | 93 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-04 05:00 | 93 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-04 06:00 | 93 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-04 07:00 | 93 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-04 08:00 | 93 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-04 09:00 | 93 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-04 10:00 | 93 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-04 11:00 | 93 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-04 12:00 | 93 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-04 13:00 | 93 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-04 14:00 | 93 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-04 15:00 | 93 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-04 16:00 | 93 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-04 17:00 | 93 | 1 | 1 | 56 | 5.295 | 2.7043
2018-04-04 18:00 | 93 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-04 19:00 | 93 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-04 20:00 | 93 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-04 21:00 | 93 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-04 22:00 | 93 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-04 23:00 | 93 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-05 | 94 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-05 01:00 | 94 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-05 02:00 | 94 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-05 03:00 | 94 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-05 04:00 | 94 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-04-05 05:00 | 94 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-04-05 06:00 | 94 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-04-05 07:00 | 94 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-04-05 08:00 | 94 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-04-05 09:00 | 94 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-04-05 10:00 | 94 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-04-05 11:00 | 94 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-04-05 12:00 | 94 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-05 13:00 | 94 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-05 14:00 | 94 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-04-05 15:00 | 94 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-05 16:00 | 94 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-05 17:00 | 94 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-05 18:00 | 94 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-05 19:00 | 94 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-05 20:00 | 94 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-05 21:00 | 94 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-05 22:00 | 94 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-05 23:00 | 94 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-06 | 95 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-06 01:00 | 95 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-04-06 02:00 | 95 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-06 03:00 | 95 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-04-06 04:00 | 95 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-04-06 05:00 | 95 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-04-06 06:00 | 95 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-04-06 07:00 | 95 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-04-06 08:00 | 95 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-04-06 09:00 | 95 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-06 10:00 | 95 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-06 11:00 | 95 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-06 12:00 | 95 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-06 13:00 | 95 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-06 14:00 | 95 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-06 15:00 | 95 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-06 16:00 | 95 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-06 17:00 | 95 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-06 18:00 | 95 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-04-06 19:00 | 95 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-06 20:00 | 95 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-06 21:00 | 95 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-06 22:00 | 95 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-06 23:00 | 95 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-04-07 | 96 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-07 01:00 | 96 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-04-07 02:00 | 96 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-04-07 03:00 | 96 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-07 04:00 | 96 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-07 05:00 | 96 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-04-07 06:00 | 96 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-07 07:00 | 96 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-07 08:00 | 96 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-07 09:00 | 96 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-07 10:00 | 96 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-07 11:00 | 96 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-04-07 12:00 | 96 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-07 13:00 | 96 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-07 14:00 | 96 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-07 15:00 | 96 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-07 16:00 | 96 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-07 17:00 | 96 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-04-07 18:00 | 96 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-07 19:00 | 96 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-07 20:00 | 96 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-07 21:00 | 96 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-07 22:00 | 96 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-07 23:00 | 96 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-08 | 97 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-08 01:00 | 97 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-04-08 02:00 | 97 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-04-08 03:00 | 97 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-04-08 04:00 | 97 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-04-08 05:00 | 97 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-04-08 06:00 | 97 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-04-08 07:00 | 97 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-04-08 08:00 | 97 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-04-08 09:00 | 97 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-04-08 10:00 | 97 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-04-08 11:00 | 97 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-04-08 12:00 | 97 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-08 13:00 | 97 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-08 14:00 | 97 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-08 15:00 | 97 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-08 16:00 | 97 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-08 17:00 | 97 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-08 18:00 | 97 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-08 19:00 | 97 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-08 20:00 | 97 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-08 21:00 | 97 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-08 22:00 | 97 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-04-08 23:00 | 97 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-04-09 | 98 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-04-09 01:00 | 98 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-04-09 02:00 | 98 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-04-09 03:00 | 98 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-04-09 04:00 | 98 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-04-09 05:00 | 98 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-04-09 06:00 | 98 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-04-09 07:00 | 98 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-04-09 08:00 | 98 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-04-09 09:00 | 98 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-04-09 10:00 | 98 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-04-09 11:00 | 98 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-09 12:00 | 98 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-09 13:00 | 98 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-09 14:00 | 98 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-09 15:00 | 98 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-09 16:00 | 98 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-09 17:00 | 98 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-09 18:00 | 98 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-09 19:00 | 98 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-09 20:00 | 98 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-09 21:00 | 98 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-09 22:00 | 98 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-09 23:00 | 98 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-10 | 99 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-10 01:00 | 99 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-10 02:00 | 99 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-10 03:00 | 99 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-10 04:00 | 99 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-10 05:00 | 99 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-04-10 06:00 | 99 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-10 07:00 | 99 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-10 08:00 | 99 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-04-10 09:00 | 99 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-10 10:00 | 99 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-10 11:00 | 99 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-10 12:00 | 99 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-10 13:00 | 99 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-10 14:00 | 99 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-04-10 15:00 | 99 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-10 16:00 | 99 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-10 17:00 | 99 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-04-10 18:00 | 99 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-10 19:00 | 99 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-10 20:00 | 99 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-04-10 21:00 | 99 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-10 22:00 | 99 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-10 23:00 | 99 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-11 | 100 | 1 | 1 | 42.5 | 5.859 | 2.9145
2018-04-11 01:00 | 100 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-11 02:00 | 100 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-11 03:00 | 100 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-04-11 04:00 | 100 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-04-11 05:00 | 100 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-11 06:00 | 100 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-11 07:00 | 100 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-11 08:00 | 100 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-04-11 09:00 | 100 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-11 10:00 | 100 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-11 11:00 | 100 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-11 12:00 | 100 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-11 13:00 | 100 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-11 14:00 | 100 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-04-11 15:00 | 100 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-11 16:00 | 100 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-11 17:00 | 100 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-04-11 18:00 | 100 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-11 19:00 | 100 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-11 20:00 | 100 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-11 21:00 | 100 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-11 22:00 | 100 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-11 23:00 | 100 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-12 | 101 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-12 01:00 | 101 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-12 02:00 | 101 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-12 03:00 | 101 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-12 04:00 | 101 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-12 05:00 | 101 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-04-12 06:00 | 101 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-12 07:00 | 101 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-12 08:00 | 101 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-12 09:00 | 101 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-12 10:00 | 101 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-12 11:00 | 101 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-12 12:00 | 101 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-12 13:00 | 101 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-12 14:00 | 101 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-04-12 15:00 | 101 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-04-12 16:00 | 101 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-12 17:00 | 101 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-12 18:00 | 101 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-12 19:00 | 101 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-12 20:00 | 101 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-12 21:00 | 101 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-12 22:00 | 101 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-12 23:00 | 101 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-13 | 102 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-13 01:00 | 102 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-04-13 02:00 | 102 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-04-13 03:00 | 102 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-13 04:00 | 102 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-13 05:00 | 102 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-13 06:00 | 102 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-04-13 07:00 | 102 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-04-13 08:00 | 102 | 1 | 1 | 64 | 5.3779 | 2.687
2018-04-13 09:00 | 102 | 1 | 1 | 64 | 5.3779 | 2.687
2018-04-13 10:00 | 102 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-04-13 11:00 | 102 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-04-13 12:00 | 102 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-04-13 13:00 | 102 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-04-13 14:00 | 102 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-04-13 15:00 | 102 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-04-13 16:00 | 102 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-04-13 17:00 | 102 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-04-13 18:00 | 102 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-04-13 19:00 | 102 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-04-13 20:00 | 102 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-04-13 21:00 | 102 | 1 | 1 | 64 | 5.3779 | 2.687
2018-04-13 22:00 | 102 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-04-13 23:00 | 102 | 1 | 1 | 64 | 5.3779 | 2.687
2018-04-14 | 103 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-14 01:00 | 103 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-14 02:00 | 103 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-14 03:00 | 103 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-04-14 04:00 | 103 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-04-14 05:00 | 103 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-04-14 06:00 | 103 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-14 07:00 | 103 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-14 08:00 | 103 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-14 09:00 | 103 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-04-14 10:00 | 103 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-14 11:00 | 103 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-04-14 12:00 | 103 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-04-14 13:00 | 103 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-04-14 14:00 | 103 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-04-14 15:00 | 103 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-04-14 16:00 | 103 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-14 17:00 | 103 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-14 18:00 | 103 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-14 19:00 | 103 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-14 20:00 | 103 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-14 21:00 | 103 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-14 22:00 | 103 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-14 23:00 | 103 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-15 | 104 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-15 01:00 | 104 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-15 02:00 | 104 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-15 03:00 | 104 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-15 04:00 | 104 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-15 05:00 | 104 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-15 06:00 | 104 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-15 07:00 | 104 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-15 08:00 | 104 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-15 09:00 | 104 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-15 10:00 | 104 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-15 11:00 | 104 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-15 12:00 | 104 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-15 13:00 | 104 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-15 14:00 | 104 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-04-15 15:00 | 104 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-15 16:00 | 104 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-15 17:00 | 104 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-15 18:00 | 104 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-15 19:00 | 104 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-15 20:00 | 104 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-15 21:00 | 104 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-15 22:00 | 104 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-15 23:00 | 104 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-04-16 | 105 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-16 01:00 | 105 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-04-16 02:00 | 105 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-16 03:00 | 105 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-16 04:00 | 105 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-16 05:00 | 105 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-16 06:00 | 105 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-16 07:00 | 105 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-16 08:00 | 105 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-04-16 09:00 | 105 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-16 10:00 | 105 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-16 11:00 | 105 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-04-16 12:00 | 105 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-16 13:00 | 105 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-16 14:00 | 105 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-16 15:00 | 105 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-16 16:00 | 105 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-16 17:00 | 105 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-16 18:00 | 105 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-16 19:00 | 105 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-16 20:00 | 105 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-04-16 21:00 | 105 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-16 22:00 | 105 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-16 23:00 | 105 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-04-17 | 106 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-17 01:00 | 106 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-04-17 02:00 | 106 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-04-17 03:00 | 106 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-17 04:00 | 106 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-17 05:00 | 106 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-17 06:00 | 106 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-17 07:00 | 106 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-17 08:00 | 106 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-17 09:00 | 106 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-17 10:00 | 106 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-17 11:00 | 106 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-17 12:00 | 106 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-17 13:00 | 106 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-17 14:00 | 106 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-04-17 15:00 | 106 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-17 16:00 | 106 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-17 17:00 | 106 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-17 18:00 | 106 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-17 19:00 | 106 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-17 20:00 | 106 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-17 21:00 | 106 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-17 22:00 | 106 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-17 23:00 | 106 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-18 | 107 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-18 01:00 | 107 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-18 02:00 | 107 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-04-18 03:00 | 107 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-18 04:00 | 107 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-18 05:00 | 107 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-18 06:00 | 107 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-18 07:00 | 107 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-18 08:00 | 107 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-04-18 09:00 | 107 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-18 10:00 | 107 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-18 11:00 | 107 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-18 12:00 | 107 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-18 13:00 | 107 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-18 14:00 | 107 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-18 15:00 | 107 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-18 16:00 | 107 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-18 17:00 | 107 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-18 18:00 | 107 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-18 19:00 | 107 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-18 20:00 | 107 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-04-18 21:00 | 107 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-18 22:00 | 107 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-18 23:00 | 107 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-19 | 108 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-19 01:00 | 108 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-19 02:00 | 108 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-04-19 03:00 | 108 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-19 04:00 | 108 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-19 05:00 | 108 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-04-19 06:00 | 108 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-19 07:00 | 108 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-19 08:00 | 108 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-19 09:00 | 108 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-19 10:00 | 108 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-19 11:00 | 108 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-04-19 12:00 | 108 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-19 13:00 | 108 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-19 14:00 | 108 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-04-19 15:00 | 108 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-19 16:00 | 108 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-19 17:00 | 108 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-04-19 18:00 | 108 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-19 19:00 | 108 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-19 20:00 | 108 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-19 21:00 | 108 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-19 22:00 | 108 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-19 23:00 | 108 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-20 | 109 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-20 01:00 | 109 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-04-20 02:00 | 109 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-20 03:00 | 109 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-20 04:00 | 109 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-20 05:00 | 109 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-04-20 06:00 | 109 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-04-20 07:00 | 109 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-04-20 08:00 | 109 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-04-20 09:00 | 109 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-04-20 10:00 | 109 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-20 11:00 | 109 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-04-20 12:00 | 109 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-20 13:00 | 109 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-20 14:00 | 109 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-20 15:00 | 109 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-20 16:00 | 109 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-20 17:00 | 109 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-20 18:00 | 109 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-20 19:00 | 109 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-20 20:00 | 109 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-20 21:00 | 109 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-20 22:00 | 109 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-20 23:00 | 109 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-21 | 110 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-21 01:00 | 110 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-21 02:00 | 110 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-04-21 03:00 | 110 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-21 04:00 | 110 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-21 05:00 | 110 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-04-21 06:00 | 110 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-21 07:00 | 110 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-21 08:00 | 110 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-04-21 09:00 | 110 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-21 10:00 | 110 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-21 11:00 | 110 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-21 12:00 | 110 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-21 13:00 | 110 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-21 14:00 | 110 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-21 15:00 | 110 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-21 16:00 | 110 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-21 17:00 | 110 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-04-21 18:00 | 110 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-21 19:00 | 110 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-21 20:00 | 110 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-04-21 21:00 | 110 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-21 22:00 | 110 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-21 23:00 | 110 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-22 | 111 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-22 01:00 | 111 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-04-22 02:00 | 111 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-04-22 03:00 | 111 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-22 04:00 | 111 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-22 05:00 | 111 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-22 06:00 | 111 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-22 07:00 | 111 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-22 08:00 | 111 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-22 09:00 | 111 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-22 10:00 | 111 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-22 11:00 | 111 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-22 12:00 | 111 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-04-22 13:00 | 111 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-22 14:00 | 111 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-04-22 15:00 | 111 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-04-22 16:00 | 111 | 1 | 1 | 64 | 5.3779 | 2.687
2018-04-22 17:00 | 111 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-22 18:00 | 111 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-04-22 19:00 | 111 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-22 20:00 | 111 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-22 21:00 | 111 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-22 22:00 | 111 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-22 23:00 | 111 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-23 | 112 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-23 01:00 | 112 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-23 02:00 | 112 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-04-23 03:00 | 112 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-23 04:00 | 112 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-23 05:00 | 112 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-23 06:00 | 112 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-23 07:00 | 112 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-23 08:00 | 112 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-04-23 09:00 | 112 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-23 10:00 | 112 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-23 11:00 | 112 | 1 | 1 | 56 | 5.295 | 2.7043
2018-04-23 12:00 | 112 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-23 13:00 | 112 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-23 14:00 | 112 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-04-23 15:00 | 112 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-04-23 16:00 | 112 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-04-23 17:00 | 112 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-04-23 18:00 | 112 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-23 19:00 | 112 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-23 20:00 | 112 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-23 21:00 | 112 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-23 22:00 | 112 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-23 23:00 | 112 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-04-24 | 113 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-24 01:00 | 113 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-24 02:00 | 113 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-24 03:00 | 113 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-24 04:00 | 113 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-24 05:00 | 113 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-04-24 06:00 | 113 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-24 07:00 | 113 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-24 08:00 | 113 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-24 09:00 | 113 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-24 10:00 | 113 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-24 11:00 | 113 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-24 12:00 | 113 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-04-24 13:00 | 113 | 1 | 1 | 64 | 5.3779 | 2.687
2018-04-24 14:00 | 113 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-04-24 15:00 | 113 | 1 | 1 | 64 | 5.3779 | 2.687
2018-04-24 16:00 | 113 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-04-24 17:00 | 113 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-04-24 18:00 | 113 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-24 19:00 | 113 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-24 20:00 | 113 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-04-24 21:00 | 113 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-24 22:00 | 113 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-24 23:00 | 113 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-25 | 114 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-25 01:00 | 114 | 1 | 1 | 56 | 5.295 | 2.7043
2018-04-25 02:00 | 114 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-25 03:00 | 114 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-25 04:00 | 114 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-25 05:00 | 114 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-25 06:00 | 114 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-25 07:00 | 114 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-25 08:00 | 114 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-25 09:00 | 114 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-25 10:00 | 114 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-25 11:00 | 114 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-25 12:00 | 114 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-25 13:00 | 114 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-25 14:00 | 114 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-04-25 15:00 | 114 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-25 16:00 | 114 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-04-25 17:00 | 114 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-25 18:00 | 114 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-25 19:00 | 114 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-25 20:00 | 114 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-25 21:00 | 114 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-25 22:00 | 114 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-25 23:00 | 114 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-26 | 115 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-26 01:00 | 115 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-26 02:00 | 115 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-26 03:00 | 115 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-26 04:00 | 115 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-26 05:00 | 115 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-04-26 06:00 | 115 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-26 07:00 | 115 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-26 08:00 | 115 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-04-26 09:00 | 115 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-26 10:00 | 115 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-26 11:00 | 115 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-04-26 12:00 | 115 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-04-26 13:00 | 115 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-04-26 14:00 | 115 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-04-26 15:00 | 115 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-04-26 16:00 | 115 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-04-26 17:00 | 115 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-04-26 18:00 | 115 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-04-26 19:00 | 115 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-04-26 20:00 | 115 | 1 | 1 | 64 | 5.3779 | 2.687
2018-04-26 21:00 | 115 | 1 | 1 | 64 | 5.3779 | 2.687
2018-04-26 22:00 | 115 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-04-26 23:00 | 115 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-04-27 | 116 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-27 01:00 | 116 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-27 02:00 | 116 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-27 03:00 | 116 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-27 04:00 | 116 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-27 05:00 | 116 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-04-27 06:00 | 116 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-27 07:00 | 116 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-27 08:00 | 116 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-04-27 09:00 | 116 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-27 10:00 | 116 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-27 11:00 | 116 | 1 | 1 | 56 | 5.295 | 2.7043
2018-04-27 12:00 | 116 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-27 13:00 | 116 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-27 14:00 | 116 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-04-27 15:00 | 116 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-27 16:00 | 116 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-27 17:00 | 116 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-27 18:00 | 116 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-27 19:00 | 116 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-27 20:00 | 116 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-27 21:00 | 116 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-27 22:00 | 116 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-27 23:00 | 116 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-04-28 | 117 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-28 01:00 | 117 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-04-28 02:00 | 117 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-04-28 03:00 | 117 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-28 04:00 | 117 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-28 05:00 | 117 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-28 06:00 | 117 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-28 07:00 | 117 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-28 08:00 | 117 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-28 09:00 | 117 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-28 10:00 | 117 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-28 11:00 | 117 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-28 12:00 | 117 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-28 13:00 | 117 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-04-28 14:00 | 117 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-04-28 15:00 | 117 | 1 | 1 | 64 | 5.3779 | 2.687
2018-04-28 16:00 | 117 | 1 | 1 | 64 | 5.3779 | 2.687
2018-04-28 17:00 | 117 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-04-28 18:00 | 117 | 1 | 1 | 64 | 5.3779 | 2.687
2018-04-28 19:00 | 117 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-04-28 20:00 | 117 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-04-28 21:00 | 117 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-28 22:00 | 117 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-28 23:00 | 117 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-29 | 118 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-29 01:00 | 118 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-29 02:00 | 118 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-29 03:00 | 118 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-29 04:00 | 118 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-29 05:00 | 118 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-04-29 06:00 | 118 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-29 07:00 | 118 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-29 08:00 | 118 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-29 09:00 | 118 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-29 10:00 | 118 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-29 11:00 | 118 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-04-29 12:00 | 118 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-29 13:00 | 118 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-29 14:00 | 118 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-29 15:00 | 118 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-04-29 16:00 | 118 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-04-29 17:00 | 118 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-29 18:00 | 118 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-04-29 19:00 | 118 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-29 20:00 | 118 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-29 21:00 | 118 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-29 22:00 | 118 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-29 23:00 | 118 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-04-30 | 119 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-30 01:00 | 119 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-30 02:00 | 119 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-30 03:00 | 119 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-30 04:00 | 119 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-30 05:00 | 119 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-04-30 06:00 | 119 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-30 07:00 | 119 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-30 08:00 | 119 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-04-30 09:00 | 119 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-30 10:00 | 119 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-30 11:00 | 119 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-30 12:00 | 119 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-04-30 13:00 | 119 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-04-30 14:00 | 119 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-04-30 15:00 | 119 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-30 16:00 | 119 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-04-30 17:00 | 119 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-30 18:00 | 119 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-30 19:00 | 119 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-30 20:00 | 119 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-30 21:00 | 119 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-04-30 22:00 | 119 | 1 | 1 | 52 | 5.37 | 2.7429
2018-04-30 23:00 | 119 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-05-01 | 120 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-05-01 01:00 | 120 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-05-01 02:00 | 120 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-05-01 03:00 | 120 | 1 | 1 | 52 | 5.37 | 2.7429
2018-05-01 04:00 | 120 | 1 | 1 | 52 | 5.37 | 2.7429
2018-05-01 05:00 | 120 | 1 | 1 | 52 | 5.37 | 2.7429
2018-05-01 06:00 | 120 | 1 | 1 | 52 | 5.37 | 2.7429
2018-05-01 07:00 | 120 | 1 | 1 | 52 | 5.37 | 2.7429
2018-05-01 08:00 | 120 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-01 09:00 | 120 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-01 10:00 | 120 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-01 11:00 | 120 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-01 12:00 | 120 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-01 13:00 | 120 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-01 14:00 | 120 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-01 15:00 | 120 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-01 16:00 | 120 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-01 17:00 | 120 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-05-01 18:00 | 120 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-01 19:00 | 120 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-01 20:00 | 120 | 1 | 1 | 74 | 5.918 | 2.7776
2018-05-01 21:00 | 120 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-01 22:00 | 120 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-01 23:00 | 120 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-02 | 121 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-02 01:00 | 121 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-02 02:00 | 121 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-02 03:00 | 121 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-02 04:00 | 121 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-02 05:00 | 121 | 1 | 1 | 67 | 5.489 | 2.7011
2018-05-02 06:00 | 121 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-02 07:00 | 121 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-02 08:00 | 121 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-02 09:00 | 121 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-02 10:00 | 121 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-05-02 11:00 | 121 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-05-02 12:00 | 121 | 1 | 1 | 84 | 6.9431 | 2.993
2018-05-02 13:00 | 121 | 1 | 1 | 86 | 7.2064 | 3.051
2018-05-02 14:00 | 121 | 1 | 1 | 88 | 7.489 | 3.114
2018-05-02 15:00 | 121 | 1 | 1 | 90 | 7.791 | 3.182
2018-05-02 16:00 | 121 | 1 | 1 | 90 | 7.791 | 3.182
2018-05-02 17:00 | 121 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-05-02 18:00 | 121 | 1 | 1 | 90 | 7.791 | 3.182
2018-05-02 19:00 | 121 | 1 | 1 | 88 | 7.489 | 3.114
2018-05-02 20:00 | 121 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-05-02 21:00 | 121 | 1 | 1 | 84 | 6.9431 | 2.993
2018-05-02 22:00 | 121 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-05-02 23:00 | 121 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-05-03 | 122 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-03 01:00 | 122 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-05-03 02:00 | 122 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-05-03 03:00 | 122 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-03 04:00 | 122 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-03 05:00 | 122 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-03 06:00 | 122 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-03 07:00 | 122 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-03 08:00 | 122 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-03 09:00 | 122 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-03 10:00 | 122 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-05-03 11:00 | 122 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-05-03 12:00 | 122 | 1 | 1 | 88 | 7.489 | 3.114
2018-05-03 13:00 | 122 | 1 | 1 | 90 | 7.791 | 3.182
2018-05-03 14:00 | 122 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-05-03 15:00 | 122 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-05-03 16:00 | 122 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-05-03 17:00 | 122 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-05-03 18:00 | 122 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-05-03 19:00 | 122 | 1 | 1 | 90 | 7.791 | 3.182
2018-05-03 20:00 | 122 | 1 | 1 | 71 | 5.705 | 2.7373
2018-05-03 21:00 | 122 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-03 22:00 | 122 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-03 23:00 | 122 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-04 | 123 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-04 01:00 | 123 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-04 02:00 | 123 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-04 03:00 | 123 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-04 04:00 | 123 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-04 05:00 | 123 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-04 06:00 | 123 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-04 07:00 | 123 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-04 08:00 | 123 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-05-04 09:00 | 123 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-04 10:00 | 123 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-04 11:00 | 123 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-05-04 12:00 | 123 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-04 13:00 | 123 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-04 14:00 | 123 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-05-04 15:00 | 123 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-05-04 16:00 | 123 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-05-04 17:00 | 123 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-05-04 18:00 | 123 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-04 19:00 | 123 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-04 20:00 | 123 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-05-04 21:00 | 123 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-04 22:00 | 123 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-05-04 23:00 | 123 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-05-05 | 124 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-05 01:00 | 124 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-05-05 02:00 | 124 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-05 03:00 | 124 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-05 04:00 | 124 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-05 05:00 | 124 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-05 06:00 | 124 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-05 07:00 | 124 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-05 08:00 | 124 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-05 09:00 | 124 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-05 10:00 | 124 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-05 11:00 | 124 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-05 12:00 | 124 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-05 13:00 | 124 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-05 14:00 | 124 | 1 | 1 | 74 | 5.918 | 2.7776
2018-05-05 15:00 | 124 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-05 16:00 | 124 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-05 17:00 | 124 | 1 | 1 | 71 | 5.705 | 2.7373
2018-05-05 18:00 | 124 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-05 19:00 | 124 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-05 20:00 | 124 | 1 | 1 | 67 | 5.489 | 2.7011
2018-05-05 21:00 | 124 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-05 22:00 | 124 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-05 23:00 | 124 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-06 | 125 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-06 01:00 | 125 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-06 02:00 | 125 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-06 03:00 | 125 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-06 04:00 | 125 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-06 05:00 | 125 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-06 06:00 | 125 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-06 07:00 | 125 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-06 08:00 | 125 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-05-06 09:00 | 125 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-06 10:00 | 125 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-06 11:00 | 125 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-06 12:00 | 125 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-06 13:00 | 125 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-06 14:00 | 125 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-05-06 15:00 | 125 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-06 16:00 | 125 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-06 17:00 | 125 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-06 18:00 | 125 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-06 19:00 | 125 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-06 20:00 | 125 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-06 21:00 | 125 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-06 22:00 | 125 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-06 23:00 | 125 | 1 | 1 | 56 | 5.295 | 2.7043
2018-05-07 | 126 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-07 01:00 | 126 | 1 | 1 | 56 | 5.295 | 2.7043
2018-05-07 02:00 | 126 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-05-07 03:00 | 126 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-07 04:00 | 126 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-07 05:00 | 126 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-07 06:00 | 126 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-07 07:00 | 126 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-07 08:00 | 126 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-07 09:00 | 126 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-07 10:00 | 126 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-07 11:00 | 126 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-07 12:00 | 126 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-07 13:00 | 126 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-07 14:00 | 126 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-07 15:00 | 126 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-07 16:00 | 126 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-07 17:00 | 126 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-05-07 18:00 | 126 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-07 19:00 | 126 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-07 20:00 | 126 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-07 21:00 | 126 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-07 22:00 | 126 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-07 23:00 | 126 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-08 | 127 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-08 01:00 | 127 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-08 02:00 | 127 | 1 | 1 | 56 | 5.295 | 2.7043
2018-05-08 03:00 | 127 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-08 04:00 | 127 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-08 05:00 | 127 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-08 06:00 | 127 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-08 07:00 | 127 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-08 08:00 | 127 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-08 09:00 | 127 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-08 10:00 | 127 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-08 11:00 | 127 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-08 12:00 | 127 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-08 13:00 | 127 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-05-08 14:00 | 127 | 1 | 1 | 71 | 5.705 | 2.7373
2018-05-08 15:00 | 127 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-08 16:00 | 127 | 1 | 1 | 71 | 5.705 | 2.7373
2018-05-08 17:00 | 127 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-08 18:00 | 127 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-08 19:00 | 127 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-08 20:00 | 127 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-08 21:00 | 127 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-08 22:00 | 127 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-05-08 23:00 | 127 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-09 | 128 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-09 01:00 | 128 | 1 | 1 | 56 | 5.295 | 2.7043
2018-05-09 02:00 | 128 | 1 | 1 | 56 | 5.295 | 2.7043
2018-05-09 03:00 | 128 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-09 04:00 | 128 | 1 | 1 | 56 | 5.295 | 2.7043
2018-05-09 05:00 | 128 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-09 06:00 | 128 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-09 07:00 | 128 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-09 08:00 | 128 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-05-09 09:00 | 128 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-09 10:00 | 128 | 1 | 1 | 67 | 5.489 | 2.7011
2018-05-09 11:00 | 128 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-09 12:00 | 128 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-09 13:00 | 128 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-09 14:00 | 128 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-09 15:00 | 128 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-09 16:00 | 128 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-09 17:00 | 128 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-09 18:00 | 128 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-09 19:00 | 128 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-09 20:00 | 128 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-09 21:00 | 128 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-09 22:00 | 128 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-09 23:00 | 128 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-05-10 | 129 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-10 01:00 | 129 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-10 02:00 | 129 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-10 03:00 | 129 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-10 04:00 | 129 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-10 05:00 | 129 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-10 06:00 | 129 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-10 07:00 | 129 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-10 08:00 | 129 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-05-10 09:00 | 129 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-10 10:00 | 129 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-10 11:00 | 129 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-05-10 12:00 | 129 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-10 13:00 | 129 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-10 14:00 | 129 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-10 15:00 | 129 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-10 16:00 | 129 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-10 17:00 | 129 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-10 18:00 | 129 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-10 19:00 | 129 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-10 20:00 | 129 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-10 21:00 | 129 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-10 22:00 | 129 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-10 23:00 | 129 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-11 | 130 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-11 01:00 | 130 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-11 02:00 | 130 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-11 03:00 | 130 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-11 04:00 | 130 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-11 05:00 | 130 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-11 06:00 | 130 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-11 07:00 | 130 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-11 08:00 | 130 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-11 09:00 | 130 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-11 10:00 | 130 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-11 11:00 | 130 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-11 12:00 | 130 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-11 13:00 | 130 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-11 14:00 | 130 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-05-11 15:00 | 130 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-11 16:00 | 130 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-11 17:00 | 130 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-11 18:00 | 130 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-11 19:00 | 130 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-11 20:00 | 130 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-11 21:00 | 130 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-11 22:00 | 130 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-11 23:00 | 130 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-12 | 131 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-12 01:00 | 131 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-12 02:00 | 131 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-12 03:00 | 131 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-12 04:00 | 131 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-12 05:00 | 131 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-05-12 06:00 | 131 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-12 07:00 | 131 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-12 08:00 | 131 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-12 09:00 | 131 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-12 10:00 | 131 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-12 11:00 | 131 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-12 12:00 | 131 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-12 13:00 | 131 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-12 14:00 | 131 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-05-12 15:00 | 131 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-12 16:00 | 131 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-12 17:00 | 131 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-12 18:00 | 131 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-12 19:00 | 131 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-12 20:00 | 131 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-12 21:00 | 131 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-12 22:00 | 131 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-12 23:00 | 131 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-05-13 | 132 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-13 01:00 | 132 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-05-13 02:00 | 132 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-05-13 03:00 | 132 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-13 04:00 | 132 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-13 05:00 | 132 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-05-13 06:00 | 132 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-13 07:00 | 132 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-13 08:00 | 132 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-05-13 09:00 | 132 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-13 10:00 | 132 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-13 11:00 | 132 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-13 12:00 | 132 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-13 13:00 | 132 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-13 14:00 | 132 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-05-13 15:00 | 132 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-13 16:00 | 132 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-13 17:00 | 132 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-13 18:00 | 132 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-13 19:00 | 132 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-13 20:00 | 132 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-13 21:00 | 132 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-13 22:00 | 132 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-13 23:00 | 132 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-05-14 | 133 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-14 01:00 | 133 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-14 02:00 | 133 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-05-14 03:00 | 133 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-14 04:00 | 133 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-14 05:00 | 133 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-05-14 06:00 | 133 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-14 07:00 | 133 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-14 08:00 | 133 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-14 09:00 | 133 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-14 10:00 | 133 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-14 11:00 | 133 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-14 12:00 | 133 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-14 13:00 | 133 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-14 14:00 | 133 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-14 15:00 | 133 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-14 16:00 | 133 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-14 17:00 | 133 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-05-14 18:00 | 133 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-14 19:00 | 133 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-14 20:00 | 133 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-14 21:00 | 133 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-14 22:00 | 133 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-14 23:00 | 133 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-15 | 134 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-15 01:00 | 134 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-05-15 02:00 | 134 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-05-15 03:00 | 134 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-15 04:00 | 134 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-15 05:00 | 134 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-15 06:00 | 134 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-15 07:00 | 134 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-15 08:00 | 134 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-15 09:00 | 134 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-15 10:00 | 134 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-15 11:00 | 134 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-15 12:00 | 134 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-05-15 13:00 | 134 | 1 | 1 | 84 | 6.9431 | 2.993
2018-05-15 14:00 | 134 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-05-15 15:00 | 134 | 1 | 1 | 88 | 7.489 | 3.114
2018-05-15 16:00 | 134 | 1 | 1 | 88 | 7.489 | 3.114
2018-05-15 17:00 | 134 | 1 | 1 | 90 | 7.791 | 3.182
2018-05-15 18:00 | 134 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-15 19:00 | 134 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-15 20:00 | 134 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-15 21:00 | 134 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-15 22:00 | 134 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-15 23:00 | 134 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-16 | 135 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-16 01:00 | 135 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-16 02:00 | 135 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-16 03:00 | 135 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-16 04:00 | 135 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-16 05:00 | 135 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-16 06:00 | 135 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-16 07:00 | 135 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-16 08:00 | 135 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-16 09:00 | 135 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-16 10:00 | 135 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-16 11:00 | 135 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-05-16 12:00 | 135 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-16 13:00 | 135 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-16 14:00 | 135 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-16 15:00 | 135 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-16 16:00 | 135 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-16 17:00 | 135 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-16 18:00 | 135 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-16 19:00 | 135 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-16 20:00 | 135 | 1 | 1 | 56 | 5.295 | 2.7043
2018-05-16 21:00 | 135 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-16 22:00 | 135 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-16 23:00 | 135 | 1 | 1 | 56 | 5.295 | 2.7043
2018-05-17 | 136 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-17 01:00 | 136 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-17 02:00 | 136 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-17 03:00 | 136 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-17 04:00 | 136 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-17 05:00 | 136 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-17 06:00 | 136 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-17 07:00 | 136 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-17 08:00 | 136 | 1 | 1 | 56 | 5.295 | 2.7043
2018-05-17 09:00 | 136 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-17 10:00 | 136 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-17 11:00 | 136 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-05-17 12:00 | 136 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-17 13:00 | 136 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-17 14:00 | 136 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-17 15:00 | 136 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-17 16:00 | 136 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-17 17:00 | 136 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-17 18:00 | 136 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-17 19:00 | 136 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-17 20:00 | 136 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-17 21:00 | 136 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-17 22:00 | 136 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-17 23:00 | 136 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-18 | 137 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-18 01:00 | 137 | 1 | 1 | 67 | 5.489 | 2.7011
2018-05-18 02:00 | 137 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-18 03:00 | 137 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-18 04:00 | 137 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-18 05:00 | 137 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-18 06:00 | 137 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-18 07:00 | 137 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-18 08:00 | 137 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-18 09:00 | 137 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-18 10:00 | 137 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-18 11:00 | 137 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-18 12:00 | 137 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-18 13:00 | 137 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-18 14:00 | 137 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-18 15:00 | 137 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-18 16:00 | 137 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-18 17:00 | 137 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-18 18:00 | 137 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-18 19:00 | 137 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-18 20:00 | 137 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-18 21:00 | 137 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-05-18 22:00 | 137 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-18 23:00 | 137 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-19 | 138 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-19 01:00 | 138 | 1 | 1 | 56 | 5.295 | 2.7043
2018-05-19 02:00 | 138 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-19 03:00 | 138 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-19 04:00 | 138 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-19 05:00 | 138 | 1 | 1 | 52 | 5.37 | 2.7429
2018-05-19 06:00 | 138 | 1 | 1 | 52 | 5.37 | 2.7429
2018-05-19 07:00 | 138 | 1 | 1 | 52 | 5.37 | 2.7429
2018-05-19 08:00 | 138 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-05-19 09:00 | 138 | 1 | 1 | 52 | 5.37 | 2.7429
2018-05-19 10:00 | 138 | 1 | 1 | 52 | 5.37 | 2.7429
2018-05-19 11:00 | 138 | 1 | 1 | 52 | 5.37 | 2.7429
2018-05-19 12:00 | 138 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-19 13:00 | 138 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-19 14:00 | 138 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-19 15:00 | 138 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-19 16:00 | 138 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-19 17:00 | 138 | 1 | 1 | 56 | 5.295 | 2.7043
2018-05-19 18:00 | 138 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-19 19:00 | 138 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-19 20:00 | 138 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-19 21:00 | 138 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-19 22:00 | 138 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-19 23:00 | 138 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-05-20 | 139 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-20 01:00 | 139 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-20 02:00 | 139 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-20 03:00 | 139 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-05-20 04:00 | 139 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-05-20 05:00 | 139 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-05-20 06:00 | 139 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-20 07:00 | 139 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-20 08:00 | 139 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-20 09:00 | 139 | 1 | 1 | 71 | 5.705 | 2.7373
2018-05-20 10:00 | 139 | 1 | 1 | 74 | 5.918 | 2.7776
2018-05-20 11:00 | 139 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-05-20 12:00 | 139 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-05-20 13:00 | 139 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-05-20 14:00 | 139 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-05-20 15:00 | 139 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-05-20 16:00 | 139 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-05-20 17:00 | 139 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-05-20 18:00 | 139 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-05-20 19:00 | 139 | 1 | 1 | 74 | 5.918 | 2.7776
2018-05-20 20:00 | 139 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-20 21:00 | 139 | 1 | 1 | 71 | 5.705 | 2.7373
2018-05-20 22:00 | 139 | 1 | 1 | 71 | 5.705 | 2.7373
2018-05-20 23:00 | 139 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-21 | 140 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-21 01:00 | 140 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-21 02:00 | 140 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-21 03:00 | 140 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-21 04:00 | 140 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-21 05:00 | 140 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-21 06:00 | 140 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-21 07:00 | 140 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-21 08:00 | 140 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-21 09:00 | 140 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-21 10:00 | 140 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-21 11:00 | 140 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-05-21 12:00 | 140 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-21 13:00 | 140 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-21 14:00 | 140 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-05-21 15:00 | 140 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-05-21 16:00 | 140 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-21 17:00 | 140 | 1 | 1 | 74 | 5.918 | 2.7776
2018-05-21 18:00 | 140 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-21 19:00 | 140 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-21 20:00 | 140 | 1 | 1 | 67 | 5.489 | 2.7011
2018-05-21 21:00 | 140 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-21 22:00 | 140 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-21 23:00 | 140 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-22 | 141 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-22 01:00 | 141 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-22 02:00 | 141 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-22 03:00 | 141 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-22 04:00 | 141 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-22 05:00 | 141 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-22 06:00 | 141 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-22 07:00 | 141 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-22 08:00 | 141 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-22 09:00 | 141 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-22 10:00 | 141 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-22 11:00 | 141 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-22 12:00 | 141 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-22 13:00 | 141 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-22 14:00 | 141 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-22 15:00 | 141 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-22 16:00 | 141 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-22 17:00 | 141 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-05-22 18:00 | 141 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-22 19:00 | 141 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-22 20:00 | 141 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-22 21:00 | 141 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-22 22:00 | 141 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-22 23:00 | 141 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-05-23 | 142 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-05-23 01:00 | 142 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-05-23 02:00 | 142 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-05-23 03:00 | 142 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-23 04:00 | 142 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-05-23 05:00 | 142 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-05-23 06:00 | 142 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-23 07:00 | 142 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-05-23 08:00 | 142 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-23 09:00 | 142 | 1 | 1 | 67 | 5.489 | 2.7011
2018-05-23 10:00 | 142 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-23 11:00 | 142 | 1 | 1 | 71 | 5.705 | 2.7373
2018-05-23 12:00 | 142 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-23 13:00 | 142 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-23 14:00 | 142 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-23 15:00 | 142 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-23 16:00 | 142 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-23 17:00 | 142 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-05-23 18:00 | 142 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-05-23 19:00 | 142 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-23 20:00 | 142 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-05-23 21:00 | 142 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-05-23 22:00 | 142 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-23 23:00 | 142 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-05-24 | 143 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-24 01:00 | 143 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-24 02:00 | 143 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-05-24 03:00 | 143 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-24 04:00 | 143 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-24 05:00 | 143 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-24 06:00 | 143 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-24 07:00 | 143 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-24 08:00 | 143 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-24 09:00 | 143 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-24 10:00 | 143 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-24 11:00 | 143 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-24 12:00 | 143 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-24 13:00 | 143 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-24 14:00 | 143 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-05-24 15:00 | 143 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-05-24 16:00 | 143 | 1 | 1 | 84 | 6.9431 | 2.993
2018-05-24 17:00 | 143 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-05-24 18:00 | 143 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-05-24 19:00 | 143 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-24 20:00 | 143 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-05-24 21:00 | 143 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-24 22:00 | 143 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-24 23:00 | 143 | 1 | 1 | 74 | 5.918 | 2.7776
2018-05-25 | 144 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-25 01:00 | 144 | 1 | 1 | 71 | 5.705 | 2.7373
2018-05-25 02:00 | 144 | 1 | 1 | 71 | 5.705 | 2.7373
2018-05-25 03:00 | 144 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-25 04:00 | 144 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-25 05:00 | 144 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-05-25 06:00 | 144 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-25 07:00 | 144 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-25 08:00 | 144 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-25 09:00 | 144 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-25 10:00 | 144 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-05-25 11:00 | 144 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-05-25 12:00 | 144 | 1 | 1 | 84 | 6.9431 | 2.993
2018-05-25 13:00 | 144 | 1 | 1 | 86 | 7.2064 | 3.051
2018-05-25 14:00 | 144 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-05-25 15:00 | 144 | 1 | 1 | 88 | 7.489 | 3.114
2018-05-25 16:00 | 144 | 1 | 1 | 88 | 7.489 | 3.114
2018-05-25 17:00 | 144 | 1 | 1 | 88 | 7.489 | 3.114
2018-05-25 18:00 | 144 | 1 | 1 | 88 | 7.489 | 3.114
2018-05-25 19:00 | 144 | 1 | 1 | 88 | 7.489 | 3.114
2018-05-25 20:00 | 144 | 1 | 1 | 86 | 7.2064 | 3.051
2018-05-25 21:00 | 144 | 1 | 1 | 84 | 6.9431 | 2.993
2018-05-25 22:00 | 144 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-05-25 23:00 | 144 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-05-26 | 145 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-26 01:00 | 145 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-05-26 02:00 | 145 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-05-26 03:00 | 145 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-26 04:00 | 145 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-26 05:00 | 145 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-26 06:00 | 145 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-26 07:00 | 145 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-26 08:00 | 145 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-05-26 09:00 | 145 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-05-26 10:00 | 145 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-05-26 11:00 | 145 | 1 | 1 | 84 | 6.9431 | 2.993
2018-05-26 12:00 | 145 | 1 | 1 | 90 | 7.791 | 3.182
2018-05-26 13:00 | 145 | 1 | 1 | 90 | 7.791 | 3.182
2018-05-26 14:00 | 145 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-05-26 15:00 | 145 | 1 | 1 | 90 | 7.791 | 3.182
2018-05-26 16:00 | 145 | 1 | 1 | 90 | 7.791 | 3.182
2018-05-26 17:00 | 145 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-05-26 18:00 | 145 | 1 | 1 | 88 | 7.489 | 3.114
2018-05-26 19:00 | 145 | 1 | 1 | 84 | 6.9431 | 2.993
2018-05-26 20:00 | 145 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-05-26 21:00 | 145 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-05-26 22:00 | 145 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-05-26 23:00 | 145 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-05-27 | 146 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-05-27 01:00 | 146 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-05-27 02:00 | 146 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-05-27 03:00 | 146 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-27 04:00 | 146 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-27 05:00 | 146 | 1 | 1 | 71 | 5.705 | 2.7373
2018-05-27 06:00 | 146 | 1 | 1 | 67 | 5.489 | 2.7011
2018-05-27 07:00 | 146 | 1 | 1 | 67 | 5.489 | 2.7011
2018-05-27 08:00 | 146 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-27 09:00 | 146 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-27 10:00 | 146 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-27 11:00 | 146 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-05-27 12:00 | 146 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-27 13:00 | 146 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-27 14:00 | 146 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-05-27 15:00 | 146 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-27 16:00 | 146 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-27 17:00 | 146 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-27 18:00 | 146 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-27 19:00 | 146 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-05-27 20:00 | 146 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-27 21:00 | 146 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-05-27 22:00 | 146 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-05-27 23:00 | 146 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-28 | 147 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-28 01:00 | 147 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-28 02:00 | 147 | 1 | 1 | 56 | 5.295 | 2.7043
2018-05-28 03:00 | 147 | 1 | 1 | 56 | 5.295 | 2.7043
2018-05-28 04:00 | 147 | 1 | 1 | 56 | 5.295 | 2.7043
2018-05-28 05:00 | 147 | 1 | 1 | 56 | 5.295 | 2.7043
2018-05-28 06:00 | 147 | 1 | 1 | 56 | 5.295 | 2.7043
2018-05-28 07:00 | 147 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-28 08:00 | 147 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-05-28 09:00 | 147 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-05-28 10:00 | 147 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-05-28 11:00 | 147 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-05-28 12:00 | 147 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-28 13:00 | 147 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-28 14:00 | 147 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-28 15:00 | 147 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-05-28 16:00 | 147 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-05-28 17:00 | 147 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-05-28 18:00 | 147 | 1 | 1 | 67 | 5.489 | 2.7011
2018-05-28 19:00 | 147 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-28 20:00 | 147 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-28 21:00 | 147 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-28 22:00 | 147 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-05-28 23:00 | 147 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-05-29 | 148 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-05-29 01:00 | 148 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-05-29 02:00 | 148 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-29 03:00 | 148 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-29 04:00 | 148 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-29 05:00 | 148 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-29 06:00 | 148 | 1 | 1 | 67 | 5.489 | 2.7011
2018-05-29 07:00 | 148 | 1 | 1 | 67 | 5.489 | 2.7011
2018-05-29 08:00 | 148 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-05-29 09:00 | 148 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-29 10:00 | 148 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-29 11:00 | 148 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-05-29 12:00 | 148 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-05-29 13:00 | 148 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-05-29 14:00 | 148 | 1 | 1 | 86 | 7.2064 | 3.051
2018-05-29 15:00 | 148 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-05-29 16:00 | 148 | 1 | 1 | 86 | 7.2064 | 3.051
2018-05-29 17:00 | 148 | 1 | 1 | 84 | 6.9431 | 2.993
2018-05-29 18:00 | 148 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-05-29 19:00 | 148 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-05-29 20:00 | 148 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-05-29 21:00 | 148 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-05-29 22:00 | 148 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-29 23:00 | 148 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-30 | 149 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-30 01:00 | 149 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-30 02:00 | 149 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-30 03:00 | 149 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-30 04:00 | 149 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-30 05:00 | 149 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-30 06:00 | 149 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-30 07:00 | 149 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-30 08:00 | 149 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-30 09:00 | 149 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-30 10:00 | 149 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-30 11:00 | 149 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-30 12:00 | 149 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-30 13:00 | 149 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-30 14:00 | 149 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-30 15:00 | 149 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-30 16:00 | 149 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-05-30 17:00 | 149 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-05-30 18:00 | 149 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-05-30 19:00 | 149 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-30 20:00 | 149 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-30 21:00 | 149 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-30 22:00 | 149 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-30 23:00 | 149 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-05-31 | 150 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-31 01:00 | 150 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-05-31 02:00 | 150 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-05-31 03:00 | 150 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-31 04:00 | 150 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-31 05:00 | 150 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-05-31 06:00 | 150 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-31 07:00 | 150 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-31 08:00 | 150 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-05-31 09:00 | 150 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-31 10:00 | 150 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-31 11:00 | 150 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-05-31 12:00 | 150 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-31 13:00 | 150 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-31 14:00 | 150 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-31 15:00 | 150 | 1 | 1 | 64 | 5.3779 | 2.687
2018-05-31 16:00 | 150 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-31 17:00 | 150 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-31 18:00 | 150 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-05-31 19:00 | 150 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-05-31 20:00 | 150 | 1 | 1 | 67 | 5.489 | 2.7011
2018-05-31 21:00 | 150 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-31 22:00 | 150 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-05-31 23:00 | 150 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-01 | 151 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-01 01:00 | 151 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-01 02:00 | 151 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-01 03:00 | 151 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-01 04:00 | 151 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-01 05:00 | 151 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-01 06:00 | 151 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-01 07:00 | 151 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-01 08:00 | 151 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-01 09:00 | 151 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-01 10:00 | 151 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-01 11:00 | 151 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-01 12:00 | 151 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-01 13:00 | 151 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-01 14:00 | 151 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-01 15:00 | 151 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-01 16:00 | 151 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-01 17:00 | 151 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-01 18:00 | 151 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-01 19:00 | 151 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-01 20:00 | 151 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-01 21:00 | 151 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-01 22:00 | 151 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-01 23:00 | 151 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-02 | 152 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-02 01:00 | 152 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-02 02:00 | 152 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-06-02 03:00 | 152 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-02 04:00 | 152 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-02 05:00 | 152 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-02 06:00 | 152 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-02 07:00 | 152 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-02 08:00 | 152 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-06-02 09:00 | 152 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-02 10:00 | 152 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-06-02 11:00 | 152 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-06-02 12:00 | 152 | 1 | 1 | 86 | 7.2064 | 3.051
2018-06-02 13:00 | 152 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-02 14:00 | 152 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-02 15:00 | 152 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-06-02 16:00 | 152 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-06-02 17:00 | 152 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-06-02 18:00 | 152 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-06-02 19:00 | 152 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-02 20:00 | 152 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-06-02 21:00 | 152 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-02 22:00 | 152 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-02 23:00 | 152 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-03 | 153 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-03 01:00 | 153 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-03 02:00 | 153 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-06-03 03:00 | 153 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-03 04:00 | 153 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-03 05:00 | 153 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-03 06:00 | 153 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-03 07:00 | 153 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-03 08:00 | 153 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-03 09:00 | 153 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-03 10:00 | 153 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-03 11:00 | 153 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-03 12:00 | 153 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-03 13:00 | 153 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-03 14:00 | 153 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-03 15:00 | 153 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-03 16:00 | 153 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-03 17:00 | 153 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-03 18:00 | 153 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-03 19:00 | 153 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-03 20:00 | 153 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-06-03 21:00 | 153 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-06-03 22:00 | 153 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-06-03 23:00 | 153 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-06-04 | 154 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-06-04 01:00 | 154 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-06-04 02:00 | 154 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-06-04 03:00 | 154 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-06-04 04:00 | 154 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-06-04 05:00 | 154 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-06-04 06:00 | 154 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-06-04 07:00 | 154 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-06-04 08:00 | 154 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-06-04 09:00 | 154 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-06-04 10:00 | 154 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-06-04 11:00 | 154 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-06-04 12:00 | 154 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-04 13:00 | 154 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-04 14:00 | 154 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-06-04 15:00 | 154 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-04 16:00 | 154 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-04 17:00 | 154 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-04 18:00 | 154 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-04 19:00 | 154 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-04 20:00 | 154 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-04 21:00 | 154 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-04 22:00 | 154 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-04 23:00 | 154 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-05 | 155 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-05 01:00 | 155 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-05 02:00 | 155 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-05 03:00 | 155 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-05 04:00 | 155 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-05 05:00 | 155 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-06-05 06:00 | 155 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-06-05 07:00 | 155 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-05 08:00 | 155 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-05 09:00 | 155 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-05 10:00 | 155 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-05 11:00 | 155 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-05 12:00 | 155 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-05 13:00 | 155 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-05 14:00 | 155 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-05 15:00 | 155 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-05 16:00 | 155 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-05 17:00 | 155 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-05 18:00 | 155 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-05 19:00 | 155 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-05 20:00 | 155 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-05 21:00 | 155 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-05 22:00 | 155 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-05 23:00 | 155 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-06-06 | 156 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-06 01:00 | 156 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-06 02:00 | 156 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-06 03:00 | 156 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-06 04:00 | 156 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-06 05:00 | 156 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-06 06:00 | 156 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-06 07:00 | 156 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-06 08:00 | 156 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-06 09:00 | 156 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-06 10:00 | 156 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-06 11:00 | 156 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-06 12:00 | 156 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-06 13:00 | 156 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-06 14:00 | 156 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-06-06 15:00 | 156 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-06 16:00 | 156 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-06 17:00 | 156 | 1 | 1 | 67 | 5.489 | 2.7011
2018-06-06 18:00 | 156 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-06 19:00 | 156 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-06 20:00 | 156 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-06 21:00 | 156 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-06 22:00 | 156 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-06 23:00 | 156 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-06-07 | 157 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-07 01:00 | 157 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-07 02:00 | 157 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-07 03:00 | 157 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-07 04:00 | 157 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-07 05:00 | 157 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-07 06:00 | 157 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-07 07:00 | 157 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-07 08:00 | 157 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-07 09:00 | 157 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-07 10:00 | 157 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-07 11:00 | 157 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-06-07 12:00 | 157 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-07 13:00 | 157 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-07 14:00 | 157 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-07 15:00 | 157 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-07 16:00 | 157 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-07 17:00 | 157 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-06-07 18:00 | 157 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-07 19:00 | 157 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-07 20:00 | 157 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-07 21:00 | 157 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-07 22:00 | 157 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-07 23:00 | 157 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-08 | 158 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-08 01:00 | 158 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-08 02:00 | 158 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-08 03:00 | 158 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-08 04:00 | 158 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-08 05:00 | 158 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-08 06:00 | 158 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-08 07:00 | 158 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-08 08:00 | 158 | 1 | 1 | 67 | 5.489 | 2.7011
2018-06-08 09:00 | 158 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-08 10:00 | 158 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-08 11:00 | 158 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-06-08 12:00 | 158 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-08 13:00 | 158 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-08 14:00 | 158 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-08 15:00 | 158 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-08 16:00 | 158 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-08 17:00 | 158 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-08 18:00 | 158 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-08 19:00 | 158 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-08 20:00 | 158 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-08 21:00 | 158 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-08 22:00 | 158 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-08 23:00 | 158 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-06-09 | 159 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-09 01:00 | 159 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-09 02:00 | 159 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-09 03:00 | 159 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-09 04:00 | 159 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-09 05:00 | 159 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-09 06:00 | 159 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-09 07:00 | 159 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-09 08:00 | 159 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-09 09:00 | 159 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-09 10:00 | 159 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-09 11:00 | 159 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-09 12:00 | 159 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-09 13:00 | 159 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-09 14:00 | 159 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-06-09 15:00 | 159 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-09 16:00 | 159 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-09 17:00 | 159 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-09 18:00 | 159 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-09 19:00 | 159 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-09 20:00 | 159 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-09 21:00 | 159 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-09 22:00 | 159 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-09 23:00 | 159 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-10 | 160 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-10 01:00 | 160 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-10 02:00 | 160 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-10 03:00 | 160 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-10 04:00 | 160 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-10 05:00 | 160 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-10 06:00 | 160 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-10 07:00 | 160 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-10 08:00 | 160 | 1 | 1 | 67 | 5.489 | 2.7011
2018-06-10 09:00 | 160 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-10 10:00 | 160 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-10 11:00 | 160 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-10 12:00 | 160 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-10 13:00 | 160 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-10 14:00 | 160 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-10 15:00 | 160 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-10 16:00 | 160 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-10 17:00 | 160 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-06-10 18:00 | 160 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-10 19:00 | 160 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-10 20:00 | 160 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-10 21:00 | 160 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-10 22:00 | 160 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-10 23:00 | 160 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-06-11 | 161 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-11 01:00 | 161 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-11 02:00 | 161 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-06-11 03:00 | 161 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-11 04:00 | 161 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-11 05:00 | 161 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-06-11 06:00 | 161 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-11 07:00 | 161 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-11 08:00 | 161 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-11 09:00 | 161 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-11 10:00 | 161 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-06-11 11:00 | 161 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-11 12:00 | 161 | 1 | 1 | 67 | 5.489 | 2.7011
2018-06-11 13:00 | 161 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-06-11 14:00 | 161 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-06-11 15:00 | 161 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-11 16:00 | 161 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-06-11 17:00 | 161 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-11 18:00 | 161 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-11 19:00 | 161 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-06-11 20:00 | 161 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-11 21:00 | 161 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-11 22:00 | 161 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-11 23:00 | 161 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-12 | 162 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-12 01:00 | 162 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-12 02:00 | 162 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-12 03:00 | 162 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-12 04:00 | 162 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-06-12 05:00 | 162 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-06-12 06:00 | 162 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-06-12 07:00 | 162 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-06-12 08:00 | 162 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-06-12 09:00 | 162 | 1 | 1 | 67 | 5.489 | 2.7011
2018-06-12 10:00 | 162 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-12 11:00 | 162 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-12 12:00 | 162 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-12 13:00 | 162 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-12 14:00 | 162 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-12 15:00 | 162 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-12 16:00 | 162 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-12 17:00 | 162 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-12 18:00 | 162 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-12 19:00 | 162 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-12 20:00 | 162 | 1 | 1 | 67 | 5.489 | 2.7011
2018-06-12 21:00 | 162 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-12 22:00 | 162 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-12 23:00 | 162 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-06-13 | 163 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-13 01:00 | 163 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-13 02:00 | 163 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-06-13 03:00 | 163 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-13 04:00 | 163 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-13 05:00 | 163 | 1 | 1 | 67 | 5.489 | 2.7011
2018-06-13 06:00 | 163 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-13 07:00 | 163 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-13 08:00 | 163 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-13 09:00 | 163 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-13 10:00 | 163 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-13 11:00 | 163 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-13 12:00 | 163 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-13 13:00 | 163 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-13 14:00 | 163 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-13 15:00 | 163 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-13 16:00 | 163 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-13 17:00 | 163 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-13 18:00 | 163 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-13 19:00 | 163 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-13 20:00 | 163 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-06-13 21:00 | 163 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-13 22:00 | 163 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-13 23:00 | 163 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-14 | 164 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-14 01:00 | 164 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-14 02:00 | 164 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-06-14 03:00 | 164 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-14 04:00 | 164 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-14 05:00 | 164 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-14 06:00 | 164 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-14 07:00 | 164 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-14 08:00 | 164 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-14 09:00 | 164 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-14 10:00 | 164 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-14 11:00 | 164 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-14 12:00 | 164 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-14 13:00 | 164 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-14 14:00 | 164 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-14 15:00 | 164 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-14 16:00 | 164 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-14 17:00 | 164 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-14 18:00 | 164 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-14 19:00 | 164 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-14 20:00 | 164 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-14 21:00 | 164 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-14 22:00 | 164 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-14 23:00 | 164 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-15 | 165 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-15 01:00 | 165 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-15 02:00 | 165 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-15 03:00 | 165 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-15 04:00 | 165 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-15 05:00 | 165 | 1 | 1 | 67 | 5.489 | 2.7011
2018-06-15 06:00 | 165 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-15 07:00 | 165 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-15 08:00 | 165 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-15 09:00 | 165 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-15 10:00 | 165 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-15 11:00 | 165 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-15 12:00 | 165 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-15 13:00 | 165 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-15 14:00 | 165 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-15 15:00 | 165 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-15 16:00 | 165 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-15 17:00 | 165 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-15 18:00 | 165 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-15 19:00 | 165 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-15 20:00 | 165 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-15 21:00 | 165 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-15 22:00 | 165 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-15 23:00 | 165 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-16 | 166 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-16 01:00 | 166 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-06-16 02:00 | 166 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-16 03:00 | 166 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-16 04:00 | 166 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-16 05:00 | 166 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-16 06:00 | 166 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-16 07:00 | 166 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-16 08:00 | 166 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-16 09:00 | 166 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-16 10:00 | 166 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-16 11:00 | 166 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-06-16 12:00 | 166 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-16 13:00 | 166 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-16 14:00 | 166 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-16 15:00 | 166 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-16 16:00 | 166 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-16 17:00 | 166 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-06-16 18:00 | 166 | 1 | 1 | 86 | 7.2064 | 3.051
2018-06-16 19:00 | 166 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-16 20:00 | 166 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-06-16 21:00 | 166 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-16 22:00 | 166 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-16 23:00 | 166 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-06-17 | 167 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-17 01:00 | 167 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-17 02:00 | 167 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-17 03:00 | 167 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-17 04:00 | 167 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-17 05:00 | 167 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-17 06:00 | 167 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-17 07:00 | 167 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-17 08:00 | 167 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-17 09:00 | 167 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-17 10:00 | 167 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-17 11:00 | 167 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-06-17 12:00 | 167 | 1 | 1 | 88 | 7.489 | 3.114
2018-06-17 13:00 | 167 | 1 | 1 | 88 | 7.489 | 3.114
2018-06-17 14:00 | 167 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-06-17 15:00 | 167 | 1 | 1 | 90 | 7.791 | 3.182
2018-06-17 16:00 | 167 | 1 | 1 | 90 | 7.791 | 3.182
2018-06-17 17:00 | 167 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-06-17 18:00 | 167 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-17 19:00 | 167 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-17 20:00 | 167 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-17 21:00 | 167 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-17 22:00 | 167 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-17 23:00 | 167 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-06-18 | 168 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-18 01:00 | 168 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-18 02:00 | 168 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-06-18 03:00 | 168 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-18 04:00 | 168 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-18 05:00 | 168 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-18 06:00 | 168 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-18 07:00 | 168 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-18 08:00 | 168 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-18 09:00 | 168 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-18 10:00 | 168 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-18 11:00 | 168 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-06-18 12:00 | 168 | 1 | 1 | 90 | 7.791 | 3.182
2018-06-18 13:00 | 168 | 1 | 1 | 90 | 7.791 | 3.182
2018-06-18 14:00 | 168 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-06-18 15:00 | 168 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-06-18 16:00 | 168 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-06-18 17:00 | 168 | 1 | 1 | 90 | 7.791 | 3.182
2018-06-18 18:00 | 168 | 1 | 1 | 90 | 7.791 | 3.182
2018-06-18 19:00 | 168 | 1 | 1 | 90 | 7.791 | 3.182
2018-06-18 20:00 | 168 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-06-18 21:00 | 168 | 1 | 1 | 86 | 7.2064 | 3.051
2018-06-18 22:00 | 168 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-18 23:00 | 168 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-19 | 169 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-19 01:00 | 169 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-19 02:00 | 169 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-19 03:00 | 169 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-19 04:00 | 169 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-19 05:00 | 169 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-19 06:00 | 169 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-19 07:00 | 169 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-19 08:00 | 169 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-06-19 09:00 | 169 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-19 10:00 | 169 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-19 11:00 | 169 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-19 12:00 | 169 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-19 13:00 | 169 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-19 14:00 | 169 | 1 | 1 | 86 | 7.2064 | 3.051
2018-06-19 15:00 | 169 | 1 | 1 | 88 | 7.489 | 3.114
2018-06-19 16:00 | 169 | 1 | 1 | 88 | 7.489 | 3.114
2018-06-19 17:00 | 169 | 1 | 1 | 88 | 7.489 | 3.114
2018-06-19 18:00 | 169 | 1 | 1 | 88 | 7.489 | 3.114
2018-06-19 19:00 | 169 | 1 | 1 | 88 | 7.489 | 3.114
2018-06-19 20:00 | 169 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-19 21:00 | 169 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-19 22:00 | 169 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-19 23:00 | 169 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-20 | 170 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-20 01:00 | 170 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-06-20 02:00 | 170 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-20 03:00 | 170 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-20 04:00 | 170 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-20 05:00 | 170 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-20 06:00 | 170 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-20 07:00 | 170 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-20 08:00 | 170 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-20 09:00 | 170 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-20 10:00 | 170 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-20 11:00 | 170 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-20 12:00 | 170 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-20 13:00 | 170 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-20 14:00 | 170 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-20 15:00 | 170 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-20 16:00 | 170 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-20 17:00 | 170 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-20 18:00 | 170 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-20 19:00 | 170 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-20 20:00 | 170 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-06-20 21:00 | 170 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-20 22:00 | 170 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-20 23:00 | 170 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-21 | 171 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-21 01:00 | 171 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-21 02:00 | 171 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-06-21 03:00 | 171 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-21 04:00 | 171 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-21 05:00 | 171 | 1 | 1 | 67 | 5.489 | 2.7011
2018-06-21 06:00 | 171 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-21 07:00 | 171 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-21 08:00 | 171 | 1 | 1 | 67 | 5.489 | 2.7011
2018-06-21 09:00 | 171 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-21 10:00 | 171 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-21 11:00 | 171 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-21 12:00 | 171 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-21 13:00 | 171 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-21 14:00 | 171 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-21 15:00 | 171 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-21 16:00 | 171 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-21 17:00 | 171 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-06-21 18:00 | 171 | 1 | 1 | 86 | 7.2064 | 3.051
2018-06-21 19:00 | 171 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-21 20:00 | 171 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-06-21 21:00 | 171 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-21 22:00 | 171 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-21 23:00 | 171 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-06-22 | 172 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-22 01:00 | 172 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-22 02:00 | 172 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-22 03:00 | 172 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-22 04:00 | 172 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-22 05:00 | 172 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-22 06:00 | 172 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-22 07:00 | 172 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-22 08:00 | 172 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-22 09:00 | 172 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-22 10:00 | 172 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-22 11:00 | 172 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-22 12:00 | 172 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-22 13:00 | 172 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-22 14:00 | 172 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-22 15:00 | 172 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-22 16:00 | 172 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-22 17:00 | 172 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-22 18:00 | 172 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-22 19:00 | 172 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-22 20:00 | 172 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-22 21:00 | 172 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-22 22:00 | 172 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-22 23:00 | 172 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-23 | 173 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-23 01:00 | 173 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-23 02:00 | 173 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-23 03:00 | 173 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-23 04:00 | 173 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-23 05:00 | 173 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-06-23 06:00 | 173 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-23 07:00 | 173 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-23 08:00 | 173 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-06-23 09:00 | 173 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-23 10:00 | 173 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-23 11:00 | 173 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-23 12:00 | 173 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-23 13:00 | 173 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-06-23 14:00 | 173 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-23 15:00 | 173 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-23 16:00 | 173 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-23 17:00 | 173 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-23 18:00 | 173 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-23 19:00 | 173 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-06-23 20:00 | 173 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-06-23 21:00 | 173 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-06-23 22:00 | 173 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-06-23 23:00 | 173 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-06-24 | 174 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-06-24 01:00 | 174 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-24 02:00 | 174 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-24 03:00 | 174 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-24 04:00 | 174 | 1 | 1 | 67 | 5.489 | 2.7011
2018-06-24 05:00 | 174 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-24 06:00 | 174 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-24 07:00 | 174 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-24 08:00 | 174 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-24 09:00 | 174 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-24 10:00 | 174 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-24 11:00 | 174 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-24 12:00 | 174 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-06-24 13:00 | 174 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-06-24 14:00 | 174 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-24 15:00 | 174 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-06-24 16:00 | 174 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-06-24 17:00 | 174 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-06-24 18:00 | 174 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-06-24 19:00 | 174 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-24 20:00 | 174 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-06-24 21:00 | 174 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-06-24 22:00 | 174 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-24 23:00 | 174 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-25 | 175 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-25 01:00 | 175 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-25 02:00 | 175 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-25 03:00 | 175 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-25 04:00 | 175 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-06-25 05:00 | 175 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-06-25 06:00 | 175 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-06-25 07:00 | 175 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-06-25 08:00 | 175 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-25 09:00 | 175 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-25 10:00 | 175 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-25 11:00 | 175 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-25 12:00 | 175 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-25 13:00 | 175 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-25 14:00 | 175 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-06-25 15:00 | 175 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-25 16:00 | 175 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-25 17:00 | 175 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-25 18:00 | 175 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-25 19:00 | 175 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-25 20:00 | 175 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-25 21:00 | 175 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-25 22:00 | 175 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-25 23:00 | 175 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-26 | 176 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-26 01:00 | 176 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-26 02:00 | 176 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-06-26 03:00 | 176 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-26 04:00 | 176 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-26 05:00 | 176 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-26 06:00 | 176 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-26 07:00 | 176 | 1 | 1 | 64 | 5.3779 | 2.687
2018-06-26 08:00 | 176 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-26 09:00 | 176 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-06-26 10:00 | 176 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-26 11:00 | 176 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-26 12:00 | 176 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-26 13:00 | 176 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-26 14:00 | 176 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-26 15:00 | 176 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-26 16:00 | 176 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-26 17:00 | 176 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-26 18:00 | 176 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-26 19:00 | 176 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-26 20:00 | 176 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-26 21:00 | 176 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-26 22:00 | 176 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-26 23:00 | 176 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-27 | 177 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-27 01:00 | 177 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-27 02:00 | 177 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-06-27 03:00 | 177 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-27 04:00 | 177 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-27 05:00 | 177 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-27 06:00 | 177 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-06-27 07:00 | 177 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-27 08:00 | 177 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-06-27 09:00 | 177 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-27 10:00 | 177 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-27 11:00 | 177 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-27 12:00 | 177 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-27 13:00 | 177 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-27 14:00 | 177 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-27 15:00 | 177 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-27 16:00 | 177 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-27 17:00 | 177 | 1 | 1 | 74 | 5.918 | 2.7776
2018-06-27 18:00 | 177 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-27 19:00 | 177 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-27 20:00 | 177 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-27 21:00 | 177 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-27 22:00 | 177 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-27 23:00 | 177 | 1 | 1 | 71 | 5.705 | 2.7373
2018-06-28 | 178 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-28 01:00 | 178 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-28 02:00 | 178 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-28 03:00 | 178 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-28 04:00 | 178 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-28 05:00 | 178 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-28 06:00 | 178 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-28 07:00 | 178 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-28 08:00 | 178 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-28 09:00 | 178 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-28 10:00 | 178 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-28 11:00 | 178 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-28 12:00 | 178 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-06-28 13:00 | 178 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-28 14:00 | 178 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-28 15:00 | 178 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-28 16:00 | 178 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-28 17:00 | 178 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-06-28 18:00 | 178 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-28 19:00 | 178 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-28 20:00 | 178 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-28 21:00 | 178 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-28 22:00 | 178 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-28 23:00 | 178 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-06-29 | 179 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-29 01:00 | 179 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-29 02:00 | 179 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-29 03:00 | 179 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-29 04:00 | 179 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-29 05:00 | 179 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-29 06:00 | 179 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-06-29 07:00 | 179 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-29 08:00 | 179 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-06-29 09:00 | 179 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-29 10:00 | 179 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-29 11:00 | 179 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-29 12:00 | 179 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-29 13:00 | 179 | 1 | 1 | 86 | 7.2064 | 3.051
2018-06-29 14:00 | 179 | 1 | 1 | 88 | 7.489 | 3.114
2018-06-29 15:00 | 179 | 1 | 1 | 90 | 7.791 | 3.182
2018-06-29 16:00 | 179 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-06-29 17:00 | 179 | 1 | 1 | 90 | 7.791 | 3.182
2018-06-29 18:00 | 179 | 1 | 1 | 90 | 7.791 | 3.182
2018-06-29 19:00 | 179 | 1 | 1 | 88 | 7.489 | 3.114
2018-06-29 20:00 | 179 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-06-29 21:00 | 179 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-29 22:00 | 179 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-29 23:00 | 179 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-06-30 | 180 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-30 01:00 | 180 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-06-30 02:00 | 180 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-30 03:00 | 180 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-30 04:00 | 180 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-06-30 05:00 | 180 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-06-30 06:00 | 180 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-06-30 07:00 | 180 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-06-30 08:00 | 180 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-06-30 09:00 | 180 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-06-30 10:00 | 180 | 1 | 1 | 84 | 6.9431 | 2.993
2018-06-30 11:00 | 180 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-06-30 12:00 | 180 | 1 | 1 | 88 | 7.489 | 3.114
2018-06-30 13:00 | 180 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-06-30 14:00 | 180 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-06-30 15:00 | 180 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-06-30 16:00 | 180 | 1 | 1 | 95 | 8.631 | 3.3739
2018-06-30 17:00 | 180 | 1 | 1 | 94 | 8.4533 | 3.333
2018-06-30 18:00 | 180 | 1 | 1 | 95 | 8.631 | 3.3739
2018-06-30 19:00 | 180 | 1 | 1 | 95 | 8.631 | 3.3739
2018-06-30 20:00 | 180 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-06-30 21:00 | 180 | 1 | 1 | 88 | 7.489 | 3.114
2018-06-30 22:00 | 180 | 1 | 1 | 86 | 7.2064 | 3.051
2018-06-30 23:00 | 180 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-01 | 181 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-01 01:00 | 181 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-01 02:00 | 181 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-01 03:00 | 181 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-01 04:00 | 181 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-01 05:00 | 181 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-01 06:00 | 181 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-01 07:00 | 181 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-01 08:00 | 181 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-01 09:00 | 181 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-01 10:00 | 181 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-01 11:00 | 181 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-07-01 12:00 | 181 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-07-01 13:00 | 181 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-07-01 14:00 | 181 | 1 | 1 | 94 | 8.4533 | 3.333
2018-07-01 15:00 | 181 | 1 | 1 | 95 | 8.631 | 3.3739
2018-07-01 16:00 | 181 | 1 | 1 | 95 | 8.631 | 3.3739
2018-07-01 17:00 | 181 | 1 | 1 | 96 | 8.8135 | 3.416
2018-07-01 18:00 | 181 | 1 | 1 | 97 | 9.0009 | 3.4594
2018-07-01 19:00 | 181 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-07-01 20:00 | 181 | 1 | 1 | 92 | 8.1125 | 3.255
2018-07-01 21:00 | 181 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-07-01 22:00 | 181 | 1 | 1 | 90 | 7.791 | 3.182
2018-07-01 23:00 | 181 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-07-02 | 182 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-02 01:00 | 182 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-02 02:00 | 182 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-02 03:00 | 182 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-02 04:00 | 182 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-02 05:00 | 182 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-02 06:00 | 182 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-02 07:00 | 182 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-02 08:00 | 182 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-02 09:00 | 182 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-02 10:00 | 182 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-02 11:00 | 182 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-02 12:00 | 182 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-02 13:00 | 182 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-07-02 14:00 | 182 | 1 | 1 | 94 | 8.4533 | 3.333
2018-07-02 15:00 | 182 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-07-02 16:00 | 182 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-07-02 17:00 | 182 | 1 | 1 | 92 | 8.1125 | 3.255
2018-07-02 18:00 | 182 | 1 | 1 | 90 | 7.791 | 3.182
2018-07-02 19:00 | 182 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-02 20:00 | 182 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-02 21:00 | 182 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-02 22:00 | 182 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-02 23:00 | 182 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-03 | 183 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-03 01:00 | 183 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-03 02:00 | 183 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-03 03:00 | 183 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-03 04:00 | 183 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-03 05:00 | 183 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-03 06:00 | 183 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-03 07:00 | 183 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-03 08:00 | 183 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-03 09:00 | 183 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-03 10:00 | 183 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-03 11:00 | 183 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-03 12:00 | 183 | 1 | 1 | 90 | 7.791 | 3.182
2018-07-03 13:00 | 183 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-07-03 14:00 | 183 | 1 | 1 | 90 | 7.791 | 3.182
2018-07-03 15:00 | 183 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-03 16:00 | 183 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-03 17:00 | 183 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-03 18:00 | 183 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-03 19:00 | 183 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-03 20:00 | 183 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-03 21:00 | 183 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-03 22:00 | 183 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-03 23:00 | 183 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-04 | 184 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-04 01:00 | 184 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-04 02:00 | 184 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-04 03:00 | 184 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-04 04:00 | 184 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-04 05:00 | 184 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-04 06:00 | 184 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-04 07:00 | 184 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-04 08:00 | 184 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-04 09:00 | 184 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-04 10:00 | 184 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-04 11:00 | 184 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-04 12:00 | 184 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-04 13:00 | 184 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-04 14:00 | 184 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-07-04 15:00 | 184 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-04 16:00 | 184 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-04 17:00 | 184 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-04 18:00 | 184 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-04 19:00 | 184 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-04 20:00 | 184 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-04 21:00 | 184 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-04 22:00 | 184 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-04 23:00 | 184 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-05 | 185 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-05 01:00 | 185 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-05 02:00 | 185 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-05 03:00 | 185 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-05 04:00 | 185 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-05 05:00 | 185 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-05 06:00 | 185 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-05 07:00 | 185 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-05 08:00 | 185 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-05 09:00 | 185 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-05 10:00 | 185 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-05 11:00 | 185 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-05 12:00 | 185 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-05 13:00 | 185 | 1 | 1 | 90 | 7.791 | 3.182
2018-07-05 14:00 | 185 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-07-05 15:00 | 185 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-05 16:00 | 185 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-05 17:00 | 185 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-05 18:00 | 185 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-05 19:00 | 185 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-05 20:00 | 185 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-05 21:00 | 185 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-05 22:00 | 185 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-05 23:00 | 185 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-06 | 186 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-06 01:00 | 186 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-06 02:00 | 186 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-06 03:00 | 186 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-06 04:00 | 186 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-06 05:00 | 186 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-06 06:00 | 186 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-06 07:00 | 186 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-06 08:00 | 186 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-06 09:00 | 186 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-06 10:00 | 186 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-06 11:00 | 186 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-06 12:00 | 186 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-06 13:00 | 186 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-06 14:00 | 186 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-06 15:00 | 186 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-06 16:00 | 186 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-06 17:00 | 186 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-06 18:00 | 186 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-06 19:00 | 186 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-06 20:00 | 186 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-06 21:00 | 186 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-06 22:00 | 186 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-06 23:00 | 186 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-07 | 187 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-07 01:00 | 187 | 1 | 1 | 71 | 5.705 | 2.7373
2018-07-07 02:00 | 187 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-07-07 03:00 | 187 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-07-07 04:00 | 187 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-07-07 05:00 | 187 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-07-07 06:00 | 187 | 1 | 1 | 64 | 5.3779 | 2.687
2018-07-07 07:00 | 187 | 1 | 1 | 64 | 5.3779 | 2.687
2018-07-07 08:00 | 187 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-07-07 09:00 | 187 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-07-07 10:00 | 187 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-07-07 11:00 | 187 | 1 | 1 | 71 | 5.705 | 2.7373
2018-07-07 12:00 | 187 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-07 13:00 | 187 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-07 14:00 | 187 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-07 15:00 | 187 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-07 16:00 | 187 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-07 17:00 | 187 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-07 18:00 | 187 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-07 19:00 | 187 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-07 20:00 | 187 | 1 | 1 | 71 | 5.705 | 2.7373
2018-07-07 21:00 | 187 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-07-07 22:00 | 187 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-07-07 23:00 | 187 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-07-08 | 188 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-07-08 01:00 | 188 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-07-08 02:00 | 188 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-07-08 03:00 | 188 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-07-08 04:00 | 188 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-07-08 05:00 | 188 | 1 | 1 | 67 | 5.489 | 2.7011
2018-07-08 06:00 | 188 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-07-08 07:00 | 188 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-07-08 08:00 | 188 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-07-08 09:00 | 188 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-08 10:00 | 188 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-08 11:00 | 188 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-08 12:00 | 188 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-08 13:00 | 188 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-08 14:00 | 188 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-08 15:00 | 188 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-08 16:00 | 188 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-08 17:00 | 188 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-08 18:00 | 188 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-08 19:00 | 188 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-08 20:00 | 188 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-08 21:00 | 188 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-08 22:00 | 188 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-08 23:00 | 188 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-09 | 189 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-09 01:00 | 189 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-09 02:00 | 189 | 1 | 1 | 71 | 5.705 | 2.7373
2018-07-09 03:00 | 189 | 1 | 1 | 71 | 5.705 | 2.7373
2018-07-09 04:00 | 189 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-07-09 05:00 | 189 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-07-09 06:00 | 189 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-07-09 07:00 | 189 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-09 08:00 | 189 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-09 09:00 | 189 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-09 10:00 | 189 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-09 11:00 | 189 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-09 12:00 | 189 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-09 13:00 | 189 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-07-09 14:00 | 189 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-07-09 15:00 | 189 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-09 16:00 | 189 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-09 17:00 | 189 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-09 18:00 | 189 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-09 19:00 | 189 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-09 20:00 | 189 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-09 21:00 | 189 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-09 22:00 | 189 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-09 23:00 | 189 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-10 | 190 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-10 01:00 | 190 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-10 02:00 | 190 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-10 03:00 | 190 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-10 04:00 | 190 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-10 05:00 | 190 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-10 06:00 | 190 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-10 07:00 | 190 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-10 08:00 | 190 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-10 09:00 | 190 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-10 10:00 | 190 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-10 11:00 | 190 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-07-10 12:00 | 190 | 1 | 1 | 92 | 8.1125 | 3.255
2018-07-10 13:00 | 190 | 1 | 1 | 92 | 8.1125 | 3.255
2018-07-10 14:00 | 190 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-07-10 15:00 | 190 | 1 | 1 | 94 | 8.4533 | 3.333
2018-07-10 16:00 | 190 | 1 | 1 | 95 | 8.631 | 3.3739
2018-07-10 17:00 | 190 | 1 | 1 | 94 | 8.4533 | 3.333
2018-07-10 18:00 | 190 | 1 | 1 | 95 | 8.631 | 3.3739
2018-07-10 19:00 | 190 | 1 | 1 | 90 | 7.791 | 3.182
2018-07-10 20:00 | 190 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-07-10 21:00 | 190 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-10 22:00 | 190 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-10 23:00 | 190 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-11 | 191 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-11 01:00 | 191 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-11 02:00 | 191 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-11 03:00 | 191 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-11 04:00 | 191 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-11 05:00 | 191 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-11 06:00 | 191 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-11 07:00 | 191 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-11 08:00 | 191 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-11 09:00 | 191 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-11 10:00 | 191 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-11 11:00 | 191 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-11 12:00 | 191 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-11 13:00 | 191 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-11 14:00 | 191 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-11 15:00 | 191 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-11 16:00 | 191 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-11 17:00 | 191 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-11 18:00 | 191 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-11 19:00 | 191 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-11 20:00 | 191 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-11 21:00 | 191 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-11 22:00 | 191 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-11 23:00 | 191 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-12 | 192 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-12 01:00 | 192 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-12 02:00 | 192 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-12 03:00 | 192 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-12 04:00 | 192 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-12 05:00 | 192 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-12 06:00 | 192 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-07-12 07:00 | 192 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-07-12 08:00 | 192 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-12 09:00 | 192 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-12 10:00 | 192 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-12 11:00 | 192 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-12 12:00 | 192 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-12 13:00 | 192 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-12 14:00 | 192 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-12 15:00 | 192 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-12 16:00 | 192 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-12 17:00 | 192 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-12 18:00 | 192 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-12 19:00 | 192 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-12 20:00 | 192 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-12 21:00 | 192 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-12 22:00 | 192 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-12 23:00 | 192 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-13 | 193 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-13 01:00 | 193 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-13 02:00 | 193 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-13 03:00 | 193 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-13 04:00 | 193 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-13 05:00 | 193 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-13 06:00 | 193 | 1 | 1 | 71 | 5.705 | 2.7373
2018-07-13 07:00 | 193 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-13 08:00 | 193 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-13 09:00 | 193 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-13 10:00 | 193 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-13 11:00 | 193 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-13 12:00 | 193 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-13 13:00 | 193 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-13 14:00 | 193 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-13 15:00 | 193 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-13 16:00 | 193 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-13 17:00 | 193 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-13 18:00 | 193 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-13 19:00 | 193 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-13 20:00 | 193 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-13 21:00 | 193 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-13 22:00 | 193 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-13 23:00 | 193 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-14 | 194 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-14 01:00 | 194 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-14 02:00 | 194 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-14 03:00 | 194 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-14 04:00 | 194 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-14 05:00 | 194 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-14 06:00 | 194 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-14 07:00 | 194 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-14 08:00 | 194 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-14 09:00 | 194 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-14 10:00 | 194 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-14 11:00 | 194 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-14 12:00 | 194 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-07-14 13:00 | 194 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-07-14 14:00 | 194 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-07-14 15:00 | 194 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-07-14 16:00 | 194 | 1 | 1 | 90 | 7.791 | 3.182
2018-07-14 17:00 | 194 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-07-14 18:00 | 194 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-14 19:00 | 194 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-07-14 20:00 | 194 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-07-14 21:00 | 194 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-14 22:00 | 194 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-07-14 23:00 | 194 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-15 | 195 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-15 01:00 | 195 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-15 02:00 | 195 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-15 03:00 | 195 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-15 04:00 | 195 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-15 05:00 | 195 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-15 06:00 | 195 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-15 07:00 | 195 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-15 08:00 | 195 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-15 09:00 | 195 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-15 10:00 | 195 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-15 11:00 | 195 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-15 12:00 | 195 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-15 13:00 | 195 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-15 14:00 | 195 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-15 15:00 | 195 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-15 16:00 | 195 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-15 17:00 | 195 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-15 18:00 | 195 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-15 19:00 | 195 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-15 20:00 | 195 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-15 21:00 | 195 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-15 22:00 | 195 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-15 23:00 | 195 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-16 | 196 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-16 01:00 | 196 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-16 02:00 | 196 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-16 03:00 | 196 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-16 04:00 | 196 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-16 05:00 | 196 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-16 06:00 | 196 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-16 07:00 | 196 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-16 08:00 | 196 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-16 09:00 | 196 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-16 10:00 | 196 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-16 11:00 | 196 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-16 12:00 | 196 | 1 | 1 | 90 | 7.791 | 3.182
2018-07-16 13:00 | 196 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-07-16 14:00 | 196 | 1 | 1 | 92 | 8.1125 | 3.255
2018-07-16 15:00 | 196 | 1 | 1 | 90 | 7.791 | 3.182
2018-07-16 16:00 | 196 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-07-16 17:00 | 196 | 1 | 1 | 90 | 7.791 | 3.182
2018-07-16 18:00 | 196 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-16 19:00 | 196 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-16 20:00 | 196 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-16 21:00 | 196 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-16 22:00 | 196 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-16 23:00 | 196 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-17 | 197 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-17 01:00 | 197 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-17 02:00 | 197 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-17 03:00 | 197 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-17 04:00 | 197 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-17 05:00 | 197 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-17 06:00 | 197 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-17 07:00 | 197 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-17 08:00 | 197 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-17 09:00 | 197 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-17 10:00 | 197 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-17 11:00 | 197 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-17 12:00 | 197 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-17 13:00 | 197 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-17 14:00 | 197 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-17 15:00 | 197 | 1 | 1 | 80.5 | 6.5292 | 2.9034
2018-07-17 16:00 | 197 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-17 17:00 | 197 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-17 18:00 | 197 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-17 19:00 | 197 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-17 20:00 | 197 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-17 21:00 | 197 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-17 22:00 | 197 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-17 23:00 | 197 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-18 | 198 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-18 01:00 | 198 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-18 02:00 | 198 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-18 03:00 | 198 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-18 04:00 | 198 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-18 05:00 | 198 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-18 06:00 | 198 | 1 | 1 | 71 | 5.705 | 2.7373
2018-07-18 07:00 | 198 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-18 08:00 | 198 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-18 09:00 | 198 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-18 10:00 | 198 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-18 11:00 | 198 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-18 12:00 | 198 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-18 13:00 | 198 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-18 14:00 | 198 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-18 15:00 | 198 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-18 16:00 | 198 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-18 17:00 | 198 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-18 18:00 | 198 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-18 19:00 | 198 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-18 20:00 | 198 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-18 21:00 | 198 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-18 22:00 | 198 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-18 23:00 | 198 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-19 | 199 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-19 01:00 | 199 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-19 02:00 | 199 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-19 03:00 | 199 | 1 | 1 | 71 | 5.705 | 2.7373
2018-07-19 04:00 | 199 | 1 | 1 | 71 | 5.705 | 2.7373
2018-07-19 05:00 | 199 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-07-19 06:00 | 199 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-07-19 07:00 | 199 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-07-19 08:00 | 199 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-07-19 09:00 | 199 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-19 10:00 | 199 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-19 11:00 | 199 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-19 12:00 | 199 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-19 13:00 | 199 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-19 14:00 | 199 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-19 15:00 | 199 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-19 16:00 | 199 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-19 17:00 | 199 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-19 18:00 | 199 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-19 19:00 | 199 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-19 20:00 | 199 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-19 21:00 | 199 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-19 22:00 | 199 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-19 23:00 | 199 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-20 | 200 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-20 01:00 | 200 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-20 02:00 | 200 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-20 03:00 | 200 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-20 04:00 | 200 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-20 05:00 | 200 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-20 06:00 | 200 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-20 07:00 | 200 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-07-20 08:00 | 200 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-20 09:00 | 200 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-20 10:00 | 200 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-20 11:00 | 200 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-20 12:00 | 200 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-20 13:00 | 200 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-20 14:00 | 200 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-20 15:00 | 200 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-20 16:00 | 200 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-20 17:00 | 200 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-20 18:00 | 200 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-20 19:00 | 200 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-20 20:00 | 200 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-20 21:00 | 200 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-20 22:00 | 200 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-20 23:00 | 200 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-21 | 201 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-21 01:00 | 201 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-21 02:00 | 201 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-21 03:00 | 201 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-21 04:00 | 201 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-21 05:00 | 201 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-07-21 06:00 | 201 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-07-21 07:00 | 201 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-21 08:00 | 201 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-21 09:00 | 201 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-21 10:00 | 201 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-21 11:00 | 201 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-21 12:00 | 201 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-21 13:00 | 201 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-21 14:00 | 201 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-21 15:00 | 201 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-21 16:00 | 201 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-21 17:00 | 201 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-21 18:00 | 201 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-21 19:00 | 201 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-21 20:00 | 201 | 1 | 1 | 71 | 5.705 | 2.7373
2018-07-21 21:00 | 201 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-07-21 22:00 | 201 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-07-21 23:00 | 201 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-07-22 | 202 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-07-22 01:00 | 202 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-22 02:00 | 202 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-22 03:00 | 202 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-22 04:00 | 202 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-22 05:00 | 202 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-22 06:00 | 202 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-22 07:00 | 202 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-22 08:00 | 202 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-22 09:00 | 202 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-22 10:00 | 202 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-22 11:00 | 202 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-22 12:00 | 202 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-22 13:00 | 202 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-22 14:00 | 202 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-22 15:00 | 202 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-22 16:00 | 202 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-22 17:00 | 202 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-22 18:00 | 202 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-22 19:00 | 202 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-22 20:00 | 202 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-22 21:00 | 202 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-22 22:00 | 202 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-22 23:00 | 202 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-23 | 203 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-23 01:00 | 203 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-23 02:00 | 203 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-23 03:00 | 203 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-23 04:00 | 203 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-23 05:00 | 203 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-23 06:00 | 203 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-23 07:00 | 203 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-23 08:00 | 203 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-23 09:00 | 203 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-23 10:00 | 203 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-23 11:00 | 203 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-23 12:00 | 203 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-23 13:00 | 203 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-23 14:00 | 203 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-23 15:00 | 203 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-23 16:00 | 203 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-23 17:00 | 203 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-23 18:00 | 203 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-23 19:00 | 203 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-23 20:00 | 203 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-23 21:00 | 203 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-23 22:00 | 203 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-23 23:00 | 203 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-24 | 204 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-24 01:00 | 204 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-24 02:00 | 204 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-24 03:00 | 204 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-24 04:00 | 204 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-24 05:00 | 204 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-24 06:00 | 204 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-24 07:00 | 204 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-24 08:00 | 204 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-24 09:00 | 204 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-24 10:00 | 204 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-24 11:00 | 204 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-24 12:00 | 204 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-24 13:00 | 204 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-24 14:00 | 204 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-24 15:00 | 204 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-24 16:00 | 204 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-24 17:00 | 204 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-24 18:00 | 204 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-24 19:00 | 204 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-24 20:00 | 204 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-24 21:00 | 204 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-24 22:00 | 204 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-24 23:00 | 204 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-25 | 205 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-25 01:00 | 205 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-25 02:00 | 205 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-25 03:00 | 205 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-25 04:00 | 205 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-25 05:00 | 205 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-25 06:00 | 205 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-25 07:00 | 205 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-25 08:00 | 205 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-25 09:00 | 205 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-25 10:00 | 205 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-25 11:00 | 205 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-25 12:00 | 205 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-25 13:00 | 205 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-25 14:00 | 205 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-25 15:00 | 205 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-25 16:00 | 205 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-25 17:00 | 205 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-25 18:00 | 205 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-25 19:00 | 205 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-25 20:00 | 205 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-25 21:00 | 205 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-25 22:00 | 205 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-25 23:00 | 205 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-26 | 206 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-26 01:00 | 206 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-26 02:00 | 206 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-26 03:00 | 206 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-26 04:00 | 206 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-26 05:00 | 206 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-26 06:00 | 206 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-26 07:00 | 206 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-26 08:00 | 206 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-26 09:00 | 206 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-26 10:00 | 206 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-26 11:00 | 206 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-26 12:00 | 206 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-26 13:00 | 206 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-26 14:00 | 206 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-26 15:00 | 206 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-07-26 16:00 | 206 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-26 17:00 | 206 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-26 18:00 | 206 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-26 19:00 | 206 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-26 20:00 | 206 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-26 21:00 | 206 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-26 22:00 | 206 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-26 23:00 | 206 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-27 | 207 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-27 01:00 | 207 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-27 02:00 | 207 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-27 03:00 | 207 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-27 04:00 | 207 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-27 05:00 | 207 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-27 06:00 | 207 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-27 07:00 | 207 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-27 08:00 | 207 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-27 09:00 | 207 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-27 10:00 | 207 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-27 11:00 | 207 | 1 | 1 | 86 | 7.2064 | 3.051
2018-07-27 12:00 | 207 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-27 13:00 | 207 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-07-27 14:00 | 207 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-07-27 15:00 | 207 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-27 16:00 | 207 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-27 17:00 | 207 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-27 18:00 | 207 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-27 19:00 | 207 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-27 20:00 | 207 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-27 21:00 | 207 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-27 22:00 | 207 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-27 23:00 | 207 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-28 | 208 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-28 01:00 | 208 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-28 02:00 | 208 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-28 03:00 | 208 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-28 04:00 | 208 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-28 05:00 | 208 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-28 06:00 | 208 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-28 07:00 | 208 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-28 08:00 | 208 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-28 09:00 | 208 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-28 10:00 | 208 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-28 11:00 | 208 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-28 12:00 | 208 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-28 13:00 | 208 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-28 14:00 | 208 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-28 15:00 | 208 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-28 16:00 | 208 | 1 | 1 | 88 | 7.489 | 3.114
2018-07-28 17:00 | 208 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-07-28 18:00 | 208 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-07-28 19:00 | 208 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-28 20:00 | 208 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-28 21:00 | 208 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-28 22:00 | 208 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-28 23:00 | 208 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-29 | 209 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-29 01:00 | 209 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-29 02:00 | 209 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-29 03:00 | 209 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-29 04:00 | 209 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-29 05:00 | 209 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-29 06:00 | 209 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-29 07:00 | 209 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-29 08:00 | 209 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-29 09:00 | 209 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-29 10:00 | 209 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-29 11:00 | 209 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-29 12:00 | 209 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-29 13:00 | 209 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-29 14:00 | 209 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-29 15:00 | 209 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-29 16:00 | 209 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-29 17:00 | 209 | 1 | 1 | 84 | 6.9431 | 2.993
2018-07-29 18:00 | 209 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-07-29 19:00 | 209 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-29 20:00 | 209 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-29 21:00 | 209 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-29 22:00 | 209 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-29 23:00 | 209 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-30 | 210 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-30 01:00 | 210 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-30 02:00 | 210 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-07-30 03:00 | 210 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-30 04:00 | 210 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-30 05:00 | 210 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-30 06:00 | 210 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-30 07:00 | 210 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-30 08:00 | 210 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-30 09:00 | 210 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-30 10:00 | 210 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-30 11:00 | 210 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-30 12:00 | 210 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-30 13:00 | 210 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-30 14:00 | 210 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-30 15:00 | 210 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-30 16:00 | 210 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-30 17:00 | 210 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-30 18:00 | 210 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-30 19:00 | 210 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-30 20:00 | 210 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-07-30 21:00 | 210 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-30 22:00 | 210 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-30 23:00 | 210 | 1 | 1 | 74 | 5.918 | 2.7776
2018-07-31 | 211 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-31 01:00 | 211 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-31 02:00 | 211 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-31 03:00 | 211 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-31 04:00 | 211 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-31 05:00 | 211 | 1 | 1 | 71 | 5.705 | 2.7373
2018-07-31 06:00 | 211 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-31 07:00 | 211 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-07-31 08:00 | 211 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-07-31 09:00 | 211 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-31 10:00 | 211 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-31 11:00 | 211 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-31 12:00 | 211 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-31 13:00 | 211 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-31 14:00 | 211 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-07-31 15:00 | 211 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-31 16:00 | 211 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-31 17:00 | 211 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-07-31 18:00 | 211 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-07-31 19:00 | 211 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-07-31 20:00 | 211 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-31 21:00 | 211 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-07-31 22:00 | 211 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-07-31 23:00 | 211 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-01 | 212 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-01 01:00 | 212 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-01 02:00 | 212 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-01 03:00 | 212 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-01 04:00 | 212 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-01 05:00 | 212 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-01 06:00 | 212 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-01 07:00 | 212 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-01 08:00 | 212 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-01 09:00 | 212 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-01 10:00 | 212 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-01 11:00 | 212 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-01 12:00 | 212 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-01 13:00 | 212 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-01 14:00 | 212 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-01 15:00 | 212 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-01 16:00 | 212 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-01 17:00 | 212 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-01 18:00 | 212 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-01 19:00 | 212 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-01 20:00 | 212 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-08-01 21:00 | 212 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-01 22:00 | 212 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-01 23:00 | 212 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-08-02 | 213 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-02 01:00 | 213 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-08-02 02:00 | 213 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-02 03:00 | 213 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-02 04:00 | 213 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-02 05:00 | 213 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-02 06:00 | 213 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-02 07:00 | 213 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-02 08:00 | 213 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-02 09:00 | 213 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-02 10:00 | 213 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-02 11:00 | 213 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-02 12:00 | 213 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-02 13:00 | 213 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-02 14:00 | 213 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-02 15:00 | 213 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-02 16:00 | 213 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-02 17:00 | 213 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-08-02 18:00 | 213 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-02 19:00 | 213 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-02 20:00 | 213 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-08-02 21:00 | 213 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-02 22:00 | 213 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-02 23:00 | 213 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-03 | 214 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-03 01:00 | 214 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-03 02:00 | 214 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-03 03:00 | 214 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-03 04:00 | 214 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-03 05:00 | 214 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-03 06:00 | 214 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-03 07:00 | 214 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-03 08:00 | 214 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-03 09:00 | 214 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-03 10:00 | 214 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-03 11:00 | 214 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-03 12:00 | 214 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-03 13:00 | 214 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-03 14:00 | 214 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-08-03 15:00 | 214 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-03 16:00 | 214 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-03 17:00 | 214 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-03 18:00 | 214 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-03 19:00 | 214 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-03 20:00 | 214 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-03 21:00 | 214 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-03 22:00 | 214 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-03 23:00 | 214 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-04 | 215 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-04 01:00 | 215 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-04 02:00 | 215 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-04 03:00 | 215 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-04 04:00 | 215 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-04 05:00 | 215 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-04 06:00 | 215 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-04 07:00 | 215 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-04 08:00 | 215 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-04 09:00 | 215 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-04 10:00 | 215 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-04 11:00 | 215 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-04 12:00 | 215 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-04 13:00 | 215 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-04 14:00 | 215 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-04 15:00 | 215 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-04 16:00 | 215 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-04 17:00 | 215 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-04 18:00 | 215 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-04 19:00 | 215 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-04 20:00 | 215 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-08-04 21:00 | 215 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-04 22:00 | 215 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-04 23:00 | 215 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-05 | 216 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-05 01:00 | 216 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-05 02:00 | 216 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-05 03:00 | 216 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-05 04:00 | 216 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-05 05:00 | 216 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-05 06:00 | 216 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-05 07:00 | 216 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-05 08:00 | 216 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-05 09:00 | 216 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-05 10:00 | 216 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-05 11:00 | 216 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-05 12:00 | 216 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-05 13:00 | 216 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-05 14:00 | 216 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-08-05 15:00 | 216 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-08-05 16:00 | 216 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-08-05 17:00 | 216 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-05 18:00 | 216 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-05 19:00 | 216 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-05 20:00 | 216 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-05 21:00 | 216 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-05 22:00 | 216 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-05 23:00 | 216 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-08-06 | 217 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-06 01:00 | 217 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-08-06 02:00 | 217 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-08-06 03:00 | 217 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-06 04:00 | 217 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-06 05:00 | 217 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-08-06 06:00 | 217 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-06 07:00 | 217 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-06 08:00 | 217 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-06 09:00 | 217 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-06 10:00 | 217 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-06 11:00 | 217 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-06 12:00 | 217 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-06 13:00 | 217 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-06 14:00 | 217 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-08-06 15:00 | 217 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-08-06 16:00 | 217 | 1 | 1 | 95 | 8.631 | 3.3739
2018-08-06 17:00 | 217 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-06 18:00 | 217 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-06 19:00 | 217 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-06 20:00 | 217 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-06 21:00 | 217 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-06 22:00 | 217 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-06 23:00 | 217 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-07 | 218 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-07 01:00 | 218 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-07 02:00 | 218 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-08-07 03:00 | 218 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-07 04:00 | 218 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-07 05:00 | 218 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-07 06:00 | 218 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-07 07:00 | 218 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-07 08:00 | 218 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-07 09:00 | 218 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-07 10:00 | 218 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-07 11:00 | 218 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-07 12:00 | 218 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-07 13:00 | 218 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-07 14:00 | 218 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-07 15:00 | 218 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-07 16:00 | 218 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-07 17:00 | 218 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-08-07 18:00 | 218 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-07 19:00 | 218 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-07 20:00 | 218 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-07 21:00 | 218 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-07 22:00 | 218 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-07 23:00 | 218 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-08 | 219 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-08 01:00 | 219 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-08 02:00 | 219 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-08 03:00 | 219 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-08 04:00 | 219 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-08 05:00 | 219 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-08 06:00 | 219 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-08 07:00 | 219 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-08 08:00 | 219 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-08 09:00 | 219 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-08 10:00 | 219 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-08 11:00 | 219 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-08-08 12:00 | 219 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-08 13:00 | 219 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-08 14:00 | 219 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-08 15:00 | 219 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-08 16:00 | 219 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-08 17:00 | 219 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-08 18:00 | 219 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-08 19:00 | 219 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-08 20:00 | 219 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-08-08 21:00 | 219 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-08 22:00 | 219 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-08 23:00 | 219 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-08-09 | 220 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-09 01:00 | 220 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-09 02:00 | 220 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-08-09 03:00 | 220 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-09 04:00 | 220 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-09 05:00 | 220 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-09 06:00 | 220 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-09 07:00 | 220 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-09 08:00 | 220 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-09 09:00 | 220 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-09 10:00 | 220 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-09 11:00 | 220 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-08-09 12:00 | 220 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-09 13:00 | 220 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-09 14:00 | 220 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-08-09 15:00 | 220 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-09 16:00 | 220 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-09 17:00 | 220 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-08-09 18:00 | 220 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-09 19:00 | 220 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-09 20:00 | 220 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-08-09 21:00 | 220 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-09 22:00 | 220 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-09 23:00 | 220 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-10 | 221 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-10 01:00 | 221 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-10 02:00 | 221 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-10 03:00 | 221 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-10 04:00 | 221 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-10 05:00 | 221 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-10 06:00 | 221 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-10 07:00 | 221 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-10 08:00 | 221 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-10 09:00 | 221 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-10 10:00 | 221 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-10 11:00 | 221 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-10 12:00 | 221 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-10 13:00 | 221 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-10 14:00 | 221 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-10 15:00 | 221 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-10 16:00 | 221 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-10 17:00 | 221 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-10 18:00 | 221 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-10 19:00 | 221 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-10 20:00 | 221 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-08-10 21:00 | 221 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-10 22:00 | 221 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-10 23:00 | 221 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-11 | 222 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-11 01:00 | 222 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-11 02:00 | 222 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-08-11 03:00 | 222 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-11 04:00 | 222 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-11 05:00 | 222 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-11 06:00 | 222 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-11 07:00 | 222 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-11 08:00 | 222 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-11 09:00 | 222 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-11 10:00 | 222 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-11 11:00 | 222 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-11 12:00 | 222 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-11 13:00 | 222 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-11 14:00 | 222 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-11 15:00 | 222 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-11 16:00 | 222 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-11 17:00 | 222 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-11 18:00 | 222 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-11 19:00 | 222 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-11 20:00 | 222 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-11 21:00 | 222 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-11 22:00 | 222 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-11 23:00 | 222 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-12 | 223 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-12 01:00 | 223 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-12 02:00 | 223 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-12 03:00 | 223 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-12 04:00 | 223 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-12 05:00 | 223 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-12 06:00 | 223 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-12 07:00 | 223 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-12 08:00 | 223 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-12 09:00 | 223 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-12 10:00 | 223 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-12 11:00 | 223 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-12 12:00 | 223 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-12 13:00 | 223 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-12 14:00 | 223 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-12 15:00 | 223 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-12 16:00 | 223 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-12 17:00 | 223 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-08-12 18:00 | 223 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-12 19:00 | 223 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-12 20:00 | 223 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-12 21:00 | 223 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-12 22:00 | 223 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-12 23:00 | 223 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-13 | 224 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-13 01:00 | 224 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-13 02:00 | 224 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-13 03:00 | 224 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-13 04:00 | 224 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-13 05:00 | 224 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-13 06:00 | 224 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-13 07:00 | 224 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-13 08:00 | 224 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-13 09:00 | 224 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-13 10:00 | 224 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-13 11:00 | 224 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-13 12:00 | 224 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-13 13:00 | 224 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-13 14:00 | 224 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-13 15:00 | 224 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-13 16:00 | 224 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-13 17:00 | 224 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-13 18:00 | 224 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-13 19:00 | 224 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-13 20:00 | 224 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-13 21:00 | 224 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-13 22:00 | 224 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-13 23:00 | 224 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-14 | 225 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-14 01:00 | 225 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-14 02:00 | 225 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-14 03:00 | 225 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-14 04:00 | 225 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-14 05:00 | 225 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-14 06:00 | 225 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-14 07:00 | 225 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-14 08:00 | 225 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-14 09:00 | 225 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-14 10:00 | 225 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-14 11:00 | 225 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-14 12:00 | 225 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-14 13:00 | 225 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-14 14:00 | 225 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-08-14 15:00 | 225 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-14 16:00 | 225 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-14 17:00 | 225 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-14 18:00 | 225 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-14 19:00 | 225 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-14 20:00 | 225 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-14 21:00 | 225 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-14 22:00 | 225 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-14 23:00 | 225 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-15 | 226 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-15 01:00 | 226 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-15 02:00 | 226 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-15 03:00 | 226 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-15 04:00 | 226 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-15 05:00 | 226 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-15 06:00 | 226 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-15 07:00 | 226 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-15 08:00 | 226 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-15 09:00 | 226 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-15 10:00 | 226 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-15 11:00 | 226 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-15 12:00 | 226 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-15 13:00 | 226 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-15 14:00 | 226 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-15 15:00 | 226 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-15 16:00 | 226 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-15 17:00 | 226 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-08-15 18:00 | 226 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-15 19:00 | 226 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-15 20:00 | 226 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-15 21:00 | 226 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-15 22:00 | 226 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-15 23:00 | 226 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-08-16 | 227 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-16 01:00 | 227 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-08-16 02:00 | 227 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-08-16 03:00 | 227 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-16 04:00 | 227 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-16 05:00 | 227 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-16 06:00 | 227 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-16 07:00 | 227 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-16 08:00 | 227 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-16 09:00 | 227 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-16 10:00 | 227 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-16 11:00 | 227 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-16 12:00 | 227 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-16 13:00 | 227 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-16 14:00 | 227 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-16 15:00 | 227 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-16 16:00 | 227 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-16 17:00 | 227 | 1 | 1 | 92 | 8.1125 | 3.255
2018-08-16 18:00 | 227 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-16 19:00 | 227 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-16 20:00 | 227 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-08-16 21:00 | 227 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-16 22:00 | 227 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-16 23:00 | 227 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-17 | 228 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-17 01:00 | 228 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-08-17 02:00 | 228 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-17 03:00 | 228 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-17 04:00 | 228 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-17 05:00 | 228 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-17 06:00 | 228 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-17 07:00 | 228 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-17 08:00 | 228 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-08-17 09:00 | 228 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-17 10:00 | 228 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-17 11:00 | 228 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-17 12:00 | 228 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-17 13:00 | 228 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-17 14:00 | 228 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-17 15:00 | 228 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-17 16:00 | 228 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-17 17:00 | 228 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-08-17 18:00 | 228 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-17 19:00 | 228 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-17 20:00 | 228 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-17 21:00 | 228 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-17 22:00 | 228 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-17 23:00 | 228 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-18 | 229 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-18 01:00 | 229 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-18 02:00 | 229 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-18 03:00 | 229 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-18 04:00 | 229 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-18 05:00 | 229 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-18 06:00 | 229 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-18 07:00 | 229 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-18 08:00 | 229 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-18 09:00 | 229 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-18 10:00 | 229 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-18 11:00 | 229 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-08-18 12:00 | 229 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-18 13:00 | 229 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-18 14:00 | 229 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-08-18 15:00 | 229 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-18 16:00 | 229 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-08-18 17:00 | 229 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-08-18 18:00 | 229 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-18 19:00 | 229 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-18 20:00 | 229 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-18 21:00 | 229 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-18 22:00 | 229 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-18 23:00 | 229 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-19 | 230 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-19 01:00 | 230 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-19 02:00 | 230 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-19 03:00 | 230 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-19 04:00 | 230 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-19 05:00 | 230 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-19 06:00 | 230 | 1 | 1 | 71 | 5.705 | 2.7373
2018-08-19 07:00 | 230 | 1 | 1 | 71 | 5.705 | 2.7373
2018-08-19 08:00 | 230 | 1 | 1 | 71 | 5.705 | 2.7373
2018-08-19 09:00 | 230 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-08-19 10:00 | 230 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-19 11:00 | 230 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-19 12:00 | 230 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-19 13:00 | 230 | 1 | 1 | 71 | 5.705 | 2.7373
2018-08-19 14:00 | 230 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-19 15:00 | 230 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-19 16:00 | 230 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-19 17:00 | 230 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-19 18:00 | 230 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-19 19:00 | 230 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-19 20:00 | 230 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-19 21:00 | 230 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-19 22:00 | 230 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-19 23:00 | 230 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-20 | 231 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-20 01:00 | 231 | 1 | 1 | 71 | 5.705 | 2.7373
2018-08-20 02:00 | 231 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-08-20 03:00 | 231 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-08-20 04:00 | 231 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-08-20 05:00 | 231 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-08-20 06:00 | 231 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-08-20 07:00 | 231 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-08-20 08:00 | 231 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-08-20 09:00 | 231 | 1 | 1 | 71 | 5.705 | 2.7373
2018-08-20 10:00 | 231 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-08-20 11:00 | 231 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-20 12:00 | 231 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-20 13:00 | 231 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-20 14:00 | 231 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-20 15:00 | 231 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-20 16:00 | 231 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-20 17:00 | 231 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-20 18:00 | 231 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-20 19:00 | 231 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-20 20:00 | 231 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-20 21:00 | 231 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-20 22:00 | 231 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-20 23:00 | 231 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-21 | 232 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-21 01:00 | 232 | 1 | 1 | 71 | 5.705 | 2.7373
2018-08-21 02:00 | 232 | 1 | 1 | 70.5 | 5.6738 | 2.7317
2018-08-21 03:00 | 232 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-08-21 04:00 | 232 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-08-21 05:00 | 232 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-08-21 06:00 | 232 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-08-21 07:00 | 232 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-08-21 08:00 | 232 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-08-21 09:00 | 232 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-21 10:00 | 232 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-21 11:00 | 232 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-21 12:00 | 232 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-21 13:00 | 232 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-21 14:00 | 232 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-21 15:00 | 232 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-21 16:00 | 232 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-21 17:00 | 232 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-21 18:00 | 232 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-21 19:00 | 232 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-21 20:00 | 232 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-21 21:00 | 232 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-21 22:00 | 232 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-21 23:00 | 232 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-22 | 233 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-22 01:00 | 233 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-22 02:00 | 233 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-22 03:00 | 233 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-22 04:00 | 233 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-22 05:00 | 233 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-22 06:00 | 233 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-22 07:00 | 233 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-22 08:00 | 233 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-22 09:00 | 233 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-22 10:00 | 233 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-22 11:00 | 233 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-22 12:00 | 233 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-22 13:00 | 233 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-22 14:00 | 233 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-08-22 15:00 | 233 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-22 16:00 | 233 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-22 17:00 | 233 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-22 18:00 | 233 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-22 19:00 | 233 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-22 20:00 | 233 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-22 21:00 | 233 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-22 22:00 | 233 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-22 23:00 | 233 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-23 | 234 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-23 01:00 | 234 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-23 02:00 | 234 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-23 03:00 | 234 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-23 04:00 | 234 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-23 05:00 | 234 | 1 | 1 | 71 | 5.705 | 2.7373
2018-08-23 06:00 | 234 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-08-23 07:00 | 234 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-08-23 08:00 | 234 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-08-23 09:00 | 234 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-08-23 10:00 | 234 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-23 11:00 | 234 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-23 12:00 | 234 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-23 13:00 | 234 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-23 14:00 | 234 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-23 15:00 | 234 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-23 16:00 | 234 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-23 17:00 | 234 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-23 18:00 | 234 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-23 19:00 | 234 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-23 20:00 | 234 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-23 21:00 | 234 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-23 22:00 | 234 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-23 23:00 | 234 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-24 | 235 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-24 01:00 | 235 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-24 02:00 | 235 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-24 03:00 | 235 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-24 04:00 | 235 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-24 05:00 | 235 | 1 | 1 | 71 | 5.705 | 2.7373
2018-08-24 06:00 | 235 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-08-24 07:00 | 235 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-24 08:00 | 235 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-24 09:00 | 235 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-24 10:00 | 235 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-24 11:00 | 235 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-24 12:00 | 235 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-24 13:00 | 235 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-24 14:00 | 235 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-08-24 15:00 | 235 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-24 16:00 | 235 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-24 17:00 | 235 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-08-24 18:00 | 235 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-24 19:00 | 235 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-24 20:00 | 235 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-24 21:00 | 235 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-24 22:00 | 235 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-24 23:00 | 235 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-25 | 236 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-25 01:00 | 236 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-25 02:00 | 236 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-25 03:00 | 236 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-25 04:00 | 236 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-25 05:00 | 236 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-25 06:00 | 236 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-25 07:00 | 236 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-25 08:00 | 236 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-25 09:00 | 236 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-25 10:00 | 236 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-25 11:00 | 236 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-25 12:00 | 236 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-25 13:00 | 236 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-25 14:00 | 236 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-25 15:00 | 236 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-25 16:00 | 236 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-25 17:00 | 236 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-25 18:00 | 236 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-25 19:00 | 236 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-25 20:00 | 236 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-25 21:00 | 236 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-25 22:00 | 236 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-25 23:00 | 236 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-26 | 237 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-26 01:00 | 237 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-26 02:00 | 237 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-26 03:00 | 237 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-26 04:00 | 237 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-26 05:00 | 237 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-26 06:00 | 237 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-26 07:00 | 237 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-08-26 08:00 | 237 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-26 09:00 | 237 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-26 10:00 | 237 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-26 11:00 | 237 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-26 12:00 | 237 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-26 13:00 | 237 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-26 14:00 | 237 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-26 15:00 | 237 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-26 16:00 | 237 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-26 17:00 | 237 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-26 18:00 | 237 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-26 19:00 | 237 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-26 20:00 | 237 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-26 21:00 | 237 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-26 22:00 | 237 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-26 23:00 | 237 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-27 | 238 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-27 01:00 | 238 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-27 02:00 | 238 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-08-27 03:00 | 238 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-27 04:00 | 238 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-27 05:00 | 238 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-27 06:00 | 238 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-27 07:00 | 238 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-27 08:00 | 238 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-27 09:00 | 238 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-27 10:00 | 238 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-27 11:00 | 238 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-08-27 12:00 | 238 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-27 13:00 | 238 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-27 14:00 | 238 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-08-27 15:00 | 238 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-27 16:00 | 238 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-27 17:00 | 238 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-27 18:00 | 238 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-27 19:00 | 238 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-27 20:00 | 238 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-27 21:00 | 238 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-27 22:00 | 238 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-27 23:00 | 238 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-08-28 | 239 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-28 01:00 | 239 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-08-28 02:00 | 239 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-08-28 03:00 | 239 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-28 04:00 | 239 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-28 05:00 | 239 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-28 06:00 | 239 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-28 07:00 | 239 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-28 08:00 | 239 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-08-28 09:00 | 239 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-28 10:00 | 239 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-28 11:00 | 239 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-08-28 12:00 | 239 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-08-28 13:00 | 239 | 1 | 1 | 95 | 8.631 | 3.3739
2018-08-28 14:00 | 239 | 1 | 1 | 96 | 8.8135 | 3.416
2018-08-28 15:00 | 239 | 1 | 1 | 97 | 9.0009 | 3.4594
2018-08-28 16:00 | 239 | 1 | 1 | 97 | 9.0009 | 3.4594
2018-08-28 17:00 | 239 | 1 | 1 | 97 | 9.0009 | 3.4594
2018-08-28 18:00 | 239 | 1 | 1 | 97 | 9.0009 | 3.4594
2018-08-28 19:00 | 239 | 1 | 1 | 95 | 8.631 | 3.3739
2018-08-28 20:00 | 239 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-08-28 21:00 | 239 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-28 22:00 | 239 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-28 23:00 | 239 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-29 | 240 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-29 01:00 | 240 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-29 02:00 | 240 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-08-29 03:00 | 240 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-29 04:00 | 240 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-29 05:00 | 240 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-29 06:00 | 240 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-29 07:00 | 240 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-29 08:00 | 240 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-29 09:00 | 240 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-29 10:00 | 240 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-29 11:00 | 240 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-08-29 12:00 | 240 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-08-29 13:00 | 240 | 1 | 1 | 97 | 9.0009 | 3.4594
2018-08-29 14:00 | 240 | 1 | 1 | 96 | 8.8135 | 3.416
2018-08-29 15:00 | 240 | 1 | 1 | 97 | 9.0009 | 3.4594
2018-08-29 16:00 | 240 | 1 | 1 | 97 | 9.0009 | 3.4594
2018-08-29 17:00 | 240 | 1 | 1 | 97 | 9.0009 | 3.4594
2018-08-29 18:00 | 240 | 1 | 1 | 97 | 9.0009 | 3.4594
2018-08-29 19:00 | 240 | 1 | 1 | 95 | 8.631 | 3.3739
2018-08-29 20:00 | 240 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-08-29 21:00 | 240 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-29 22:00 | 240 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-08-29 23:00 | 240 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-30 | 241 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-30 01:00 | 241 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-30 02:00 | 241 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-08-30 03:00 | 241 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-30 04:00 | 241 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-30 05:00 | 241 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-08-30 06:00 | 241 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-30 07:00 | 241 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-30 08:00 | 241 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-30 09:00 | 241 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-30 10:00 | 241 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-30 11:00 | 241 | 1 | 1 | 86 | 7.2064 | 3.051
2018-08-30 12:00 | 241 | 1 | 1 | 88 | 7.489 | 3.114
2018-08-30 13:00 | 241 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-30 14:00 | 241 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-30 15:00 | 241 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-30 16:00 | 241 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-30 17:00 | 241 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-08-30 18:00 | 241 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-30 19:00 | 241 | 1 | 1 | 90 | 7.791 | 3.182
2018-08-30 20:00 | 241 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-08-30 21:00 | 241 | 1 | 1 | 84 | 6.9431 | 2.993
2018-08-30 22:00 | 241 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-30 23:00 | 241 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-08-31 | 242 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-08-31 01:00 | 242 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-08-31 02:00 | 242 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-08-31 03:00 | 242 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-31 04:00 | 242 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-31 05:00 | 242 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-31 06:00 | 242 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-31 07:00 | 242 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-31 08:00 | 242 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-31 09:00 | 242 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-31 10:00 | 242 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-31 11:00 | 242 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-31 12:00 | 242 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-08-31 13:00 | 242 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-31 14:00 | 242 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-08-31 15:00 | 242 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-31 16:00 | 242 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-31 17:00 | 242 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-31 18:00 | 242 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-31 19:00 | 242 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-31 20:00 | 242 | 1 | 1 | 74 | 5.918 | 2.7776
2018-08-31 21:00 | 242 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-08-31 22:00 | 242 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-08-31 23:00 | 242 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-01 | 243 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-01 01:00 | 243 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-01 02:00 | 243 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-01 03:00 | 243 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-01 04:00 | 243 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-01 05:00 | 243 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-01 06:00 | 243 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-01 07:00 | 243 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-01 08:00 | 243 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-01 09:00 | 243 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-01 10:00 | 243 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-01 11:00 | 243 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-01 12:00 | 243 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-01 13:00 | 243 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-01 14:00 | 243 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-01 15:00 | 243 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-01 16:00 | 243 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-01 17:00 | 243 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-01 18:00 | 243 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-01 19:00 | 243 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-01 20:00 | 243 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-01 21:00 | 243 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-01 22:00 | 243 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-01 23:00 | 243 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-02 | 244 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-02 01:00 | 244 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-02 02:00 | 244 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-02 03:00 | 244 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-02 04:00 | 244 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-02 05:00 | 244 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-02 06:00 | 244 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-02 07:00 | 244 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-02 08:00 | 244 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-02 09:00 | 244 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-02 10:00 | 244 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-02 11:00 | 244 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-09-02 12:00 | 244 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-02 13:00 | 244 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-02 14:00 | 244 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-09-02 15:00 | 244 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-02 16:00 | 244 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-02 17:00 | 244 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-02 18:00 | 244 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-02 19:00 | 244 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-02 20:00 | 244 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-02 21:00 | 244 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-02 22:00 | 244 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-02 23:00 | 244 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-09-03 | 245 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-03 01:00 | 245 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-09-03 02:00 | 245 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-03 03:00 | 245 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-03 04:00 | 245 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-03 05:00 | 245 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-09-03 06:00 | 245 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-03 07:00 | 245 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-03 08:00 | 245 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-03 09:00 | 245 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-03 10:00 | 245 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-03 11:00 | 245 | 1 | 1 | 86 | 7.2064 | 3.051
2018-09-03 12:00 | 245 | 1 | 1 | 88 | 7.489 | 3.114
2018-09-03 13:00 | 245 | 1 | 1 | 90 | 7.791 | 3.182
2018-09-03 14:00 | 245 | 1 | 1 | 92 | 8.1125 | 3.255
2018-09-03 15:00 | 245 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-09-03 16:00 | 245 | 1 | 1 | 90 | 7.791 | 3.182
2018-09-03 17:00 | 245 | 1 | 1 | 88 | 7.489 | 3.114
2018-09-03 18:00 | 245 | 1 | 1 | 86 | 7.2064 | 3.051
2018-09-03 19:00 | 245 | 1 | 1 | 84 | 6.9431 | 2.993
2018-09-03 20:00 | 245 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-09-03 21:00 | 245 | 1 | 1 | 84 | 6.9431 | 2.993
2018-09-03 22:00 | 245 | 1 | 1 | 84 | 6.9431 | 2.993
2018-09-03 23:00 | 245 | 1 | 1 | 86 | 7.2064 | 3.051
2018-09-04 | 246 | 1 | 1 | 84 | 6.9431 | 2.993
2018-09-04 01:00 | 246 | 1 | 1 | 84 | 6.9431 | 2.993
2018-09-04 02:00 | 246 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-09-04 03:00 | 246 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-04 04:00 | 246 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-04 05:00 | 246 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-04 06:00 | 246 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-04 07:00 | 246 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-04 08:00 | 246 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-04 09:00 | 246 | 1 | 1 | 84 | 6.9431 | 2.993
2018-09-04 10:00 | 246 | 1 | 1 | 88 | 7.489 | 3.114
2018-09-04 11:00 | 246 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-09-04 12:00 | 246 | 1 | 1 | 90 | 7.791 | 3.182
2018-09-04 13:00 | 246 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-09-04 14:00 | 246 | 1 | 1 | 90 | 7.791 | 3.182
2018-09-04 15:00 | 246 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-09-04 16:00 | 246 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-09-04 17:00 | 246 | 1 | 1 | 92 | 8.1125 | 3.255
2018-09-04 18:00 | 246 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-09-04 19:00 | 246 | 1 | 1 | 90 | 7.791 | 3.182
2018-09-04 20:00 | 246 | 1 | 1 | 90 | 7.791 | 3.182
2018-09-04 21:00 | 246 | 1 | 1 | 88 | 7.489 | 3.114
2018-09-04 22:00 | 246 | 1 | 1 | 84 | 6.9431 | 2.993
2018-09-04 23:00 | 246 | 1 | 1 | 84 | 6.9431 | 2.993
2018-09-05 | 247 | 1 | 1 | 84 | 6.9431 | 2.993
2018-09-05 01:00 | 247 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-05 02:00 | 247 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-05 03:00 | 247 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-05 04:00 | 247 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-05 05:00 | 247 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-09-05 06:00 | 247 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-05 07:00 | 247 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-05 08:00 | 247 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-09-05 09:00 | 247 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-05 10:00 | 247 | 1 | 1 | 84 | 6.9431 | 2.993
2018-09-05 11:00 | 247 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-09-05 12:00 | 247 | 1 | 1 | 88 | 7.489 | 3.114
2018-09-05 13:00 | 247 | 1 | 1 | 90 | 7.791 | 3.182
2018-09-05 14:00 | 247 | 1 | 1 | 90 | 7.791 | 3.182
2018-09-05 15:00 | 247 | 1 | 1 | 90 | 7.791 | 3.182
2018-09-05 16:00 | 247 | 1 | 1 | 90 | 7.791 | 3.182
2018-09-05 17:00 | 247 | 1 | 1 | 87 | 7.3453 | 3.0819
2018-09-05 18:00 | 247 | 1 | 1 | 86 | 7.2064 | 3.051
2018-09-05 19:00 | 247 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-05 20:00 | 247 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-05 21:00 | 247 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-05 22:00 | 247 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-05 23:00 | 247 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-09-06 | 248 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-06 01:00 | 248 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-09-06 02:00 | 248 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-09-06 03:00 | 248 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-06 04:00 | 248 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-06 05:00 | 248 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-06 06:00 | 248 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-06 07:00 | 248 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-06 08:00 | 248 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-06 09:00 | 248 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-06 10:00 | 248 | 1 | 1 | 84 | 6.9431 | 2.993
2018-09-06 11:00 | 248 | 1 | 1 | 89 | 7.6376 | 3.1474
2018-09-06 12:00 | 248 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-09-06 13:00 | 248 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-09-06 14:00 | 248 | 1 | 1 | 96 | 8.8135 | 3.416
2018-09-06 15:00 | 248 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-09-06 16:00 | 248 | 1 | 1 | 93 | 8.2804 | 3.2934
2018-09-06 17:00 | 248 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-09-06 18:00 | 248 | 1 | 1 | 91 | 7.9493 | 3.2179
2018-09-06 19:00 | 248 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-06 20:00 | 248 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-06 21:00 | 248 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-06 22:00 | 248 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-06 23:00 | 248 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-07 | 249 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-07 01:00 | 249 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-07 02:00 | 249 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-07 03:00 | 249 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-07 04:00 | 249 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-07 05:00 | 249 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-07 06:00 | 249 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-07 07:00 | 249 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-07 08:00 | 249 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-07 09:00 | 249 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-07 10:00 | 249 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-07 11:00 | 249 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-07 12:00 | 249 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-07 13:00 | 249 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-07 14:00 | 249 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-07 15:00 | 249 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-07 16:00 | 249 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-07 17:00 | 249 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-07 18:00 | 249 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-07 19:00 | 249 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-07 20:00 | 249 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-07 21:00 | 249 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-07 22:00 | 249 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-07 23:00 | 249 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-08 | 250 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-08 01:00 | 250 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-08 02:00 | 250 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-08 03:00 | 250 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-08 04:00 | 250 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-08 05:00 | 250 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-08 06:00 | 250 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-08 07:00 | 250 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-08 08:00 | 250 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-08 09:00 | 250 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-08 10:00 | 250 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-08 11:00 | 250 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-08 12:00 | 250 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-08 13:00 | 250 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-08 14:00 | 250 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-08 15:00 | 250 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-08 16:00 | 250 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-09-08 17:00 | 250 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-09-08 18:00 | 250 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-08 19:00 | 250 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-08 20:00 | 250 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-09-08 21:00 | 250 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-08 22:00 | 250 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-08 23:00 | 250 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-09 | 251 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-09 01:00 | 251 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-09 02:00 | 251 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-09 03:00 | 251 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-09 04:00 | 251 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-09 05:00 | 251 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-09-09 06:00 | 251 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-09-09 07:00 | 251 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-09-09 08:00 | 251 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-09-09 09:00 | 251 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-09-09 10:00 | 251 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-09-09 11:00 | 251 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-09 12:00 | 251 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-09 13:00 | 251 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-09 14:00 | 251 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-09 15:00 | 251 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-09 16:00 | 251 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-09-09 17:00 | 251 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-09 18:00 | 251 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-09-09 19:00 | 251 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-09 20:00 | 251 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-09 21:00 | 251 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-09 22:00 | 251 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-09 23:00 | 251 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-09-10 | 252 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-09-10 01:00 | 252 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-09-10 02:00 | 252 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-09-10 03:00 | 252 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-09-10 04:00 | 252 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-09-10 05:00 | 252 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-09-10 06:00 | 252 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-09-10 07:00 | 252 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-10 08:00 | 252 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-10 09:00 | 252 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-10 10:00 | 252 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-10 11:00 | 252 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-10 12:00 | 252 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-10 13:00 | 252 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-10 14:00 | 252 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-10 15:00 | 252 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-10 16:00 | 252 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-10 17:00 | 252 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-10 18:00 | 252 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-10 19:00 | 252 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-10 20:00 | 252 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-10 21:00 | 252 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-10 22:00 | 252 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-10 23:00 | 252 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-09-11 | 253 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-11 01:00 | 253 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-09-11 02:00 | 253 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-11 03:00 | 253 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-11 04:00 | 253 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-11 05:00 | 253 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-11 06:00 | 253 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-11 07:00 | 253 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-11 08:00 | 253 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-09-11 09:00 | 253 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-11 10:00 | 253 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-11 11:00 | 253 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-09-11 12:00 | 253 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-11 13:00 | 253 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-11 14:00 | 253 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-11 15:00 | 253 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-11 16:00 | 253 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-11 17:00 | 253 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-11 18:00 | 253 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-11 19:00 | 253 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-11 20:00 | 253 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-11 21:00 | 253 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-11 22:00 | 253 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-11 23:00 | 253 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-12 | 254 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-12 01:00 | 254 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-12 02:00 | 254 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-12 03:00 | 254 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-12 04:00 | 254 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-12 05:00 | 254 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-12 06:00 | 254 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-12 07:00 | 254 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-12 08:00 | 254 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-12 09:00 | 254 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-12 10:00 | 254 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-12 11:00 | 254 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-12 12:00 | 254 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-12 13:00 | 254 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-12 14:00 | 254 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-12 15:00 | 254 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-12 16:00 | 254 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-12 17:00 | 254 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-12 18:00 | 254 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-12 19:00 | 254 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-12 20:00 | 254 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-12 21:00 | 254 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-12 22:00 | 254 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-12 23:00 | 254 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-13 | 255 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-13 01:00 | 255 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-13 02:00 | 255 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-13 03:00 | 255 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-13 04:00 | 255 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-13 05:00 | 255 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-13 06:00 | 255 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-13 07:00 | 255 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-13 08:00 | 255 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-13 09:00 | 255 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-13 10:00 | 255 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-13 11:00 | 255 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-13 12:00 | 255 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-13 13:00 | 255 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-13 14:00 | 255 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-13 15:00 | 255 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-13 16:00 | 255 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-13 17:00 | 255 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-13 18:00 | 255 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-13 19:00 | 255 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-13 20:00 | 255 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-13 21:00 | 255 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-13 22:00 | 255 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-13 23:00 | 255 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-14 | 256 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-14 01:00 | 256 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-14 02:00 | 256 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-14 03:00 | 256 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-14 04:00 | 256 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-14 05:00 | 256 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-14 06:00 | 256 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-14 07:00 | 256 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-14 08:00 | 256 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-14 09:00 | 256 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-14 10:00 | 256 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-14 11:00 | 256 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-14 12:00 | 256 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-14 13:00 | 256 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-14 14:00 | 256 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-14 15:00 | 256 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-14 16:00 | 256 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-14 17:00 | 256 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-14 18:00 | 256 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-14 19:00 | 256 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-14 20:00 | 256 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-14 21:00 | 256 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-14 22:00 | 256 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-14 23:00 | 256 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-15 | 257 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-15 01:00 | 257 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-15 02:00 | 257 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-15 03:00 | 257 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-15 04:00 | 257 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-15 05:00 | 257 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-15 06:00 | 257 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-15 07:00 | 257 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-15 08:00 | 257 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-15 09:00 | 257 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-15 10:00 | 257 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-15 11:00 | 257 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-15 12:00 | 257 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-15 13:00 | 257 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-15 14:00 | 257 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-15 15:00 | 257 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-15 16:00 | 257 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-15 17:00 | 257 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-09-15 18:00 | 257 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-15 19:00 | 257 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-15 20:00 | 257 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-15 21:00 | 257 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-15 22:00 | 257 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-15 23:00 | 257 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-16 | 258 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-16 01:00 | 258 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-16 02:00 | 258 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-16 03:00 | 258 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-16 04:00 | 258 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-16 05:00 | 258 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-16 06:00 | 258 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-16 07:00 | 258 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-16 08:00 | 258 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-16 09:00 | 258 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-16 10:00 | 258 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-16 11:00 | 258 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-09-16 12:00 | 258 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-16 13:00 | 258 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-16 14:00 | 258 | 1 | 1 | 85 | 7.0723 | 3.0213
2018-09-16 15:00 | 258 | 1 | 1 | 84 | 6.9431 | 2.993
2018-09-16 16:00 | 258 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-16 17:00 | 258 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-09-16 18:00 | 258 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-16 19:00 | 258 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-16 20:00 | 258 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-16 21:00 | 258 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-16 22:00 | 258 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-16 23:00 | 258 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-17 | 259 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-17 01:00 | 259 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-17 02:00 | 259 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-17 03:00 | 259 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-17 04:00 | 259 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-17 05:00 | 259 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-17 06:00 | 259 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-17 07:00 | 259 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-17 08:00 | 259 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-17 09:00 | 259 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-17 10:00 | 259 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-17 11:00 | 259 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-17 12:00 | 259 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-17 13:00 | 259 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-17 14:00 | 259 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-17 15:00 | 259 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-17 16:00 | 259 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-17 17:00 | 259 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-17 18:00 | 259 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-17 19:00 | 259 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-17 20:00 | 259 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-17 21:00 | 259 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-17 22:00 | 259 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-17 23:00 | 259 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-18 | 260 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-18 01:00 | 260 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-18 02:00 | 260 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-18 03:00 | 260 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-18 04:00 | 260 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-18 05:00 | 260 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-18 06:00 | 260 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-18 07:00 | 260 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-18 08:00 | 260 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-09-18 09:00 | 260 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-18 10:00 | 260 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-18 11:00 | 260 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-09-18 12:00 | 260 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-18 13:00 | 260 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-18 14:00 | 260 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-18 15:00 | 260 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-18 16:00 | 260 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-18 17:00 | 260 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-18 18:00 | 260 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-18 19:00 | 260 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-18 20:00 | 260 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-18 21:00 | 260 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-18 22:00 | 260 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-18 23:00 | 260 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-19 | 261 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-19 01:00 | 261 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-19 02:00 | 261 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-19 03:00 | 261 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-19 04:00 | 261 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-19 05:00 | 261 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-19 06:00 | 261 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-19 07:00 | 261 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-19 08:00 | 261 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-19 09:00 | 261 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-19 10:00 | 261 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-19 11:00 | 261 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-09-19 12:00 | 261 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-09-19 13:00 | 261 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-09-19 14:00 | 261 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-09-19 15:00 | 261 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-19 16:00 | 261 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-09-19 17:00 | 261 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-19 18:00 | 261 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-09-19 19:00 | 261 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-19 20:00 | 261 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-19 21:00 | 261 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-19 22:00 | 261 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-19 23:00 | 261 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-20 | 262 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-20 01:00 | 262 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-20 02:00 | 262 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-09-20 03:00 | 262 | 1 | 1 | 67 | 5.489 | 2.7011
2018-09-20 04:00 | 262 | 1 | 1 | 67 | 5.489 | 2.7011
2018-09-20 05:00 | 262 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-20 06:00 | 262 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-20 07:00 | 262 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-20 08:00 | 262 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-20 09:00 | 262 | 1 | 1 | 67 | 5.489 | 2.7011
2018-09-20 10:00 | 262 | 1 | 1 | 67 | 5.489 | 2.7011
2018-09-20 11:00 | 262 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-20 12:00 | 262 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-09-20 13:00 | 262 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-20 14:00 | 262 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-20 15:00 | 262 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-20 16:00 | 262 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-20 17:00 | 262 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-20 18:00 | 262 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-20 19:00 | 262 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-20 20:00 | 262 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-20 21:00 | 262 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-20 22:00 | 262 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-20 23:00 | 262 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-21 | 263 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-21 01:00 | 263 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-21 02:00 | 263 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-21 03:00 | 263 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-21 04:00 | 263 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-21 05:00 | 263 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-21 06:00 | 263 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-21 07:00 | 263 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-21 08:00 | 263 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-21 09:00 | 263 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-21 10:00 | 263 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-21 11:00 | 263 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-21 12:00 | 263 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-21 13:00 | 263 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-21 14:00 | 263 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-21 15:00 | 263 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-21 16:00 | 263 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-21 17:00 | 263 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-21 18:00 | 263 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-21 19:00 | 263 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-21 20:00 | 263 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-21 21:00 | 263 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-21 22:00 | 263 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-21 23:00 | 263 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-22 | 264 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-22 01:00 | 264 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-22 02:00 | 264 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-22 03:00 | 264 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-22 04:00 | 264 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-22 05:00 | 264 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-22 06:00 | 264 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-22 07:00 | 264 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-22 08:00 | 264 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-22 09:00 | 264 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-22 10:00 | 264 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-22 11:00 | 264 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-22 12:00 | 264 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-22 13:00 | 264 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-22 14:00 | 264 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-22 15:00 | 264 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-22 16:00 | 264 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-22 17:00 | 264 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-22 18:00 | 264 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-22 19:00 | 264 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-09-22 20:00 | 264 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-09-22 21:00 | 264 | 1 | 1 | 67 | 5.489 | 2.7011
2018-09-22 22:00 | 264 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-22 23:00 | 264 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-09-23 | 265 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-23 01:00 | 265 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-23 02:00 | 265 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-23 03:00 | 265 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-23 04:00 | 265 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-23 05:00 | 265 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-23 06:00 | 265 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-23 07:00 | 265 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-23 08:00 | 265 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-23 09:00 | 265 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-23 10:00 | 265 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-23 11:00 | 265 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-23 12:00 | 265 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-09-23 13:00 | 265 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-23 14:00 | 265 | 1 | 1 | 67 | 5.489 | 2.7011
2018-09-23 15:00 | 265 | 1 | 1 | 67 | 5.489 | 2.7011
2018-09-23 16:00 | 265 | 1 | 1 | 67 | 5.489 | 2.7011
2018-09-23 17:00 | 265 | 1 | 1 | 67 | 5.489 | 2.7011
2018-09-23 18:00 | 265 | 1 | 1 | 67 | 5.489 | 2.7011
2018-09-23 19:00 | 265 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-23 20:00 | 265 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-23 21:00 | 265 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-23 22:00 | 265 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-23 23:00 | 265 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-24 | 266 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-24 01:00 | 266 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-09-24 02:00 | 266 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-24 03:00 | 266 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-24 04:00 | 266 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-24 05:00 | 266 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-09-24 06:00 | 266 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-09-24 07:00 | 266 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-09-24 08:00 | 266 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-09-24 09:00 | 266 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-24 10:00 | 266 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-24 11:00 | 266 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-24 12:00 | 266 | 1 | 1 | 67 | 5.489 | 2.7011
2018-09-24 13:00 | 266 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-24 14:00 | 266 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-24 15:00 | 266 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-24 16:00 | 266 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-24 17:00 | 266 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-09-24 18:00 | 266 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-24 19:00 | 266 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-24 20:00 | 266 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-24 21:00 | 266 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-24 22:00 | 266 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-24 23:00 | 266 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-25 | 267 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-25 01:00 | 267 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-25 02:00 | 267 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-09-25 03:00 | 267 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-09-25 04:00 | 267 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-09-25 05:00 | 267 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-09-25 06:00 | 267 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-09-25 07:00 | 267 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-09-25 08:00 | 267 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-09-25 09:00 | 267 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-25 10:00 | 267 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-25 11:00 | 267 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-25 12:00 | 267 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-25 13:00 | 267 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-25 14:00 | 267 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-25 15:00 | 267 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-25 16:00 | 267 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-25 17:00 | 267 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-25 18:00 | 267 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-25 19:00 | 267 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-25 20:00 | 267 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-25 21:00 | 267 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-25 22:00 | 267 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-25 23:00 | 267 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-26 | 268 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-26 01:00 | 268 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-26 02:00 | 268 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-26 03:00 | 268 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-26 04:00 | 268 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-26 05:00 | 268 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-26 06:00 | 268 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-26 07:00 | 268 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-26 08:00 | 268 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-26 09:00 | 268 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-26 10:00 | 268 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-26 11:00 | 268 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-09-26 12:00 | 268 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-09-26 13:00 | 268 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-26 14:00 | 268 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-09-26 15:00 | 268 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-26 16:00 | 268 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-09-26 17:00 | 268 | 1 | 1 | 83 | 6.8188 | 2.9658
2018-09-26 18:00 | 268 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-09-26 19:00 | 268 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-09-26 20:00 | 268 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-26 21:00 | 268 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-26 22:00 | 268 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-09-26 23:00 | 268 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-27 | 269 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-27 01:00 | 269 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-27 02:00 | 269 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-27 03:00 | 269 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-27 04:00 | 269 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-27 05:00 | 269 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-09-27 06:00 | 269 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-09-27 07:00 | 269 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-27 08:00 | 269 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-27 09:00 | 269 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-27 10:00 | 269 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-09-27 11:00 | 269 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-09-27 12:00 | 269 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-27 13:00 | 269 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-27 14:00 | 269 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-27 15:00 | 269 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-27 16:00 | 269 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-27 17:00 | 269 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-27 18:00 | 269 | 1 | 1 | 71 | 5.705 | 2.7373
2018-09-27 19:00 | 269 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-27 20:00 | 269 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-27 21:00 | 269 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-09-27 22:00 | 269 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-09-27 23:00 | 269 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-09-28 | 270 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-09-28 01:00 | 270 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-09-28 02:00 | 270 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-09-28 03:00 | 270 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-09-28 04:00 | 270 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-28 05:00 | 270 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-28 06:00 | 270 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-28 07:00 | 270 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-28 08:00 | 270 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-09-28 09:00 | 270 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-09-28 10:00 | 270 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-09-28 11:00 | 270 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-09-28 12:00 | 270 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-09-28 13:00 | 270 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-09-28 14:00 | 270 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-09-28 15:00 | 270 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-28 16:00 | 270 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-28 17:00 | 270 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-28 18:00 | 270 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-28 19:00 | 270 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-28 20:00 | 270 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-28 21:00 | 270 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-28 22:00 | 270 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-28 23:00 | 270 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-29 | 271 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-29 01:00 | 271 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-29 02:00 | 271 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-29 03:00 | 271 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-09-29 04:00 | 271 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-09-29 05:00 | 271 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-09-29 06:00 | 271 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-09-29 07:00 | 271 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-09-29 08:00 | 271 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-09-29 09:00 | 271 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-29 10:00 | 271 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-29 11:00 | 271 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-09-29 12:00 | 271 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-29 13:00 | 271 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-29 14:00 | 271 | 1 | 1 | 74 | 5.918 | 2.7776
2018-09-29 15:00 | 271 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-29 16:00 | 271 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-09-29 17:00 | 271 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-09-29 18:00 | 271 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-29 19:00 | 271 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-29 20:00 | 271 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-09-29 21:00 | 271 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-09-29 22:00 | 271 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-29 23:00 | 271 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-30 | 272 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-30 01:00 | 272 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-30 02:00 | 272 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-30 03:00 | 272 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-09-30 04:00 | 272 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-09-30 05:00 | 272 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-09-30 06:00 | 272 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-09-30 07:00 | 272 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-09-30 08:00 | 272 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-09-30 09:00 | 272 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-09-30 10:00 | 272 | 1 | 1 | 64 | 5.3779 | 2.687
2018-09-30 11:00 | 272 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-09-30 12:00 | 272 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-30 13:00 | 272 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-30 14:00 | 272 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-30 15:00 | 272 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-30 16:00 | 272 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-09-30 17:00 | 272 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-09-30 18:00 | 272 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-09-30 19:00 | 272 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-30 20:00 | 272 | 1 | 1 | 67 | 5.489 | 2.7011
2018-09-30 21:00 | 272 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-30 22:00 | 272 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-09-30 23:00 | 272 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-01 | 273 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-01 01:00 | 273 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-01 02:00 | 273 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-01 03:00 | 273 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-01 04:00 | 273 | 1 | 1 | 64 | 5.3779 | 2.687
2018-10-01 05:00 | 273 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-01 06:00 | 273 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-01 07:00 | 273 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-01 08:00 | 273 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-01 09:00 | 273 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-01 10:00 | 273 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-01 11:00 | 273 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-01 12:00 | 273 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-01 13:00 | 273 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-01 14:00 | 273 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-10-01 15:00 | 273 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-01 16:00 | 273 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-01 17:00 | 273 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-10-01 18:00 | 273 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-01 19:00 | 273 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-01 20:00 | 273 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-01 21:00 | 273 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-01 22:00 | 273 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-01 23:00 | 273 | 1 | 1 | 72.5 | 5.8061 | 2.756
2018-10-02 | 274 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-02 01:00 | 274 | 1 | 1 | 71 | 5.705 | 2.7373
2018-10-02 02:00 | 274 | 1 | 1 | 71 | 5.705 | 2.7373
2018-10-02 03:00 | 274 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-02 04:00 | 274 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-02 05:00 | 274 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-02 06:00 | 274 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-02 07:00 | 274 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-02 08:00 | 274 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-02 09:00 | 274 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-02 10:00 | 274 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-02 11:00 | 274 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-10-02 12:00 | 274 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-02 13:00 | 274 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-02 14:00 | 274 | 1 | 1 | 78 | 6.2699 | 2.8488
2018-10-02 15:00 | 274 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-10-02 16:00 | 274 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-02 17:00 | 274 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-02 18:00 | 274 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-02 19:00 | 274 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-02 20:00 | 274 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-10-02 21:00 | 274 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-02 22:00 | 274 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-02 23:00 | 274 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-03 | 275 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-03 01:00 | 275 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-03 02:00 | 275 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-03 03:00 | 275 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-03 04:00 | 275 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-03 05:00 | 275 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-03 06:00 | 275 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-03 07:00 | 275 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-03 08:00 | 275 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-10-03 09:00 | 275 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-03 10:00 | 275 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-03 11:00 | 275 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-03 12:00 | 275 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-03 13:00 | 275 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-03 14:00 | 275 | 1 | 1 | 74 | 5.918 | 2.7776
2018-10-03 15:00 | 275 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-03 16:00 | 275 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-03 17:00 | 275 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-03 18:00 | 275 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-03 19:00 | 275 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-03 20:00 | 275 | 1 | 1 | 71 | 5.705 | 2.7373
2018-10-03 21:00 | 275 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-03 22:00 | 275 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-03 23:00 | 275 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-04 | 276 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-04 01:00 | 276 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-04 02:00 | 276 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-04 03:00 | 276 | 1 | 1 | 64 | 5.3779 | 2.687
2018-10-04 04:00 | 276 | 1 | 1 | 64 | 5.3779 | 2.687
2018-10-04 05:00 | 276 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-04 06:00 | 276 | 1 | 1 | 64 | 5.3779 | 2.687
2018-10-04 07:00 | 276 | 1 | 1 | 64 | 5.3779 | 2.687
2018-10-04 08:00 | 276 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-04 09:00 | 276 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-04 10:00 | 276 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-04 11:00 | 276 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-04 12:00 | 276 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-04 13:00 | 276 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-10-04 14:00 | 276 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-04 15:00 | 276 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-04 16:00 | 276 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-04 17:00 | 276 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-10-04 18:00 | 276 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-04 19:00 | 276 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-04 20:00 | 276 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-10-04 21:00 | 276 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-10-04 22:00 | 276 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-10-04 23:00 | 276 | 1 | 1 | 74 | 5.918 | 2.7776
2018-10-05 | 277 | 1 | 1 | 74 | 5.918 | 2.7776
2018-10-05 01:00 | 277 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-05 02:00 | 277 | 1 | 1 | 71 | 5.705 | 2.7373
2018-10-05 03:00 | 277 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-05 04:00 | 277 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-05 05:00 | 277 | 1 | 1 | 64 | 5.3779 | 2.687
2018-10-05 06:00 | 277 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-05 07:00 | 277 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-10-05 08:00 | 277 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-05 09:00 | 277 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-05 10:00 | 277 | 1 | 1 | 64 | 5.3779 | 2.687
2018-10-05 11:00 | 277 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-05 12:00 | 277 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-05 13:00 | 277 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-05 14:00 | 277 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-05 15:00 | 277 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-10-05 16:00 | 277 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-05 17:00 | 277 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-10-05 18:00 | 277 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-10-05 19:00 | 277 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-05 20:00 | 277 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-05 21:00 | 277 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-05 22:00 | 277 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-05 23:00 | 277 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-06 | 278 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-06 01:00 | 278 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-06 02:00 | 278 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-06 03:00 | 278 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-06 04:00 | 278 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-06 05:00 | 278 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-06 06:00 | 278 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-06 07:00 | 278 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-06 08:00 | 278 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-06 09:00 | 278 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-06 10:00 | 278 | 1 | 1 | 64 | 5.3779 | 2.687
2018-10-06 11:00 | 278 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-06 12:00 | 278 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-06 13:00 | 278 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-06 14:00 | 278 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-06 15:00 | 278 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-06 16:00 | 278 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-06 17:00 | 278 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-06 18:00 | 278 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-06 19:00 | 278 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-06 20:00 | 278 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-06 21:00 | 278 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-06 22:00 | 278 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-06 23:00 | 278 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-10-07 | 279 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-10-07 01:00 | 279 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-07 02:00 | 279 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-07 03:00 | 279 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-07 04:00 | 279 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-07 05:00 | 279 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-07 06:00 | 279 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-07 07:00 | 279 | 1 | 1 | 71 | 5.705 | 2.7373
2018-10-07 08:00 | 279 | 1 | 1 | 71 | 5.705 | 2.7373
2018-10-07 09:00 | 279 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-07 10:00 | 279 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-07 11:00 | 279 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-07 12:00 | 279 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-07 13:00 | 279 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-07 14:00 | 279 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-10-07 15:00 | 279 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-10-07 16:00 | 279 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-10-07 17:00 | 279 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-10-07 18:00 | 279 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-10-07 19:00 | 279 | 1 | 1 | 80 | 6.4749 | 2.8918
2018-10-07 20:00 | 279 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-10-07 21:00 | 279 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-10-07 22:00 | 279 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-07 23:00 | 279 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-10-08 | 280 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-08 01:00 | 280 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-08 02:00 | 280 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-08 03:00 | 280 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-08 04:00 | 280 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-08 05:00 | 280 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-08 06:00 | 280 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-08 07:00 | 280 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-08 08:00 | 280 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-08 09:00 | 280 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-08 10:00 | 280 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-08 11:00 | 280 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-08 12:00 | 280 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-08 13:00 | 280 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-08 14:00 | 280 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-08 15:00 | 280 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-08 16:00 | 280 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-08 17:00 | 280 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-08 18:00 | 280 | 1 | 1 | 64 | 5.3779 | 2.687
2018-10-08 19:00 | 280 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-08 20:00 | 280 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-08 21:00 | 280 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-08 22:00 | 280 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-08 23:00 | 280 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-09 | 281 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-09 01:00 | 281 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-09 02:00 | 281 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-09 03:00 | 281 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-09 04:00 | 281 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-09 05:00 | 281 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-10-09 06:00 | 281 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-09 07:00 | 281 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-09 08:00 | 281 | 1 | 1 | 71 | 5.705 | 2.7373
2018-10-09 09:00 | 281 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-09 10:00 | 281 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-09 11:00 | 281 | 1 | 1 | 74 | 5.918 | 2.7776
2018-10-09 12:00 | 281 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-09 13:00 | 281 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-09 14:00 | 281 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-09 15:00 | 281 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-09 16:00 | 281 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-09 17:00 | 281 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-10-09 18:00 | 281 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-09 19:00 | 281 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-09 20:00 | 281 | 1 | 1 | 74 | 5.918 | 2.7776
2018-10-09 21:00 | 281 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-09 22:00 | 281 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-09 23:00 | 281 | 1 | 1 | 74 | 5.918 | 2.7776
2018-10-10 | 282 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-10 01:00 | 282 | 1 | 1 | 74 | 5.918 | 2.7776
2018-10-10 02:00 | 282 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-10 03:00 | 282 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-10 04:00 | 282 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-10 05:00 | 282 | 1 | 1 | 71 | 5.705 | 2.7373
2018-10-10 06:00 | 282 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-10 07:00 | 282 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-10 08:00 | 282 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-10 09:00 | 282 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-10 10:00 | 282 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-10 11:00 | 282 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-10 12:00 | 282 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-10 13:00 | 282 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-10-10 14:00 | 282 | 1 | 1 | 81 | 6.5847 | 2.9152
2018-10-10 15:00 | 282 | 1 | 1 | 82 | 6.6993 | 2.9399
2018-10-10 16:00 | 282 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-10 17:00 | 282 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-10-10 18:00 | 282 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-10 19:00 | 282 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-10 20:00 | 282 | 1 | 1 | 74 | 5.918 | 2.7776
2018-10-10 21:00 | 282 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-10 22:00 | 282 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-10 23:00 | 282 | 1 | 1 | 74 | 5.918 | 2.7776
2018-10-11 | 283 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-11 01:00 | 283 | 1 | 1 | 74 | 5.918 | 2.7776
2018-10-11 02:00 | 283 | 1 | 1 | 73.5 | 5.8795 | 2.7701
2018-10-11 03:00 | 283 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-11 04:00 | 283 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-11 05:00 | 283 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-11 06:00 | 283 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-11 07:00 | 283 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-11 08:00 | 283 | 1 | 1 | 74 | 5.918 | 2.7776
2018-10-11 09:00 | 283 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-11 10:00 | 283 | 1 | 1 | 75 | 5.9987 | 2.7935
2018-10-11 11:00 | 283 | 1 | 1 | 76 | 6.0842 | 2.8107
2018-10-11 12:00 | 283 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-11 13:00 | 283 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-11 14:00 | 283 | 1 | 1 | 77 | 6.1746 | 2.8291
2018-10-11 15:00 | 283 | 1 | 1 | 79 | 6.3699 | 2.8697
2018-10-11 16:00 | 283 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-11 17:00 | 283 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-11 18:00 | 283 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-11 19:00 | 283 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-11 20:00 | 283 | 1 | 1 | 73 | 5.8422 | 2.7629
2018-10-11 21:00 | 283 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-11 22:00 | 283 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-11 23:00 | 283 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-12 | 284 | 1 | 1 | 72 | 5.7712 | 2.7495
2018-10-12 01:00 | 284 | 1 | 1 | 71 | 5.705 | 2.7373
2018-10-12 02:00 | 284 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-12 03:00 | 284 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-12 04:00 | 284 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-12 05:00 | 284 | 1 | 1 | 64 | 5.3779 | 2.687
2018-10-12 06:00 | 284 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-12 07:00 | 284 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-10-12 08:00 | 284 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-10-12 09:00 | 284 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-10-12 10:00 | 284 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-10-12 11:00 | 284 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-10-12 12:00 | 284 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-10-12 13:00 | 284 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-12 14:00 | 284 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-10-12 15:00 | 284 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-12 16:00 | 284 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-12 17:00 | 284 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-10-12 18:00 | 284 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-10-12 19:00 | 284 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-12 20:00 | 284 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-12 21:00 | 284 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-12 22:00 | 284 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-12 23:00 | 284 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-13 | 285 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-13 01:00 | 285 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-13 02:00 | 285 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-13 03:00 | 285 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-13 04:00 | 285 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-13 05:00 | 285 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-10-13 06:00 | 285 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-13 07:00 | 285 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-13 08:00 | 285 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-13 09:00 | 285 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-13 10:00 | 285 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-13 11:00 | 285 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-13 12:00 | 285 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-13 13:00 | 285 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-13 14:00 | 285 | 1 | 1 | 56 | 5.295 | 2.7043
2018-10-13 15:00 | 285 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-13 16:00 | 285 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-13 17:00 | 285 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-10-13 18:00 | 285 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-13 19:00 | 285 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-13 20:00 | 285 | 1 | 1 | 56 | 5.295 | 2.7043
2018-10-13 21:00 | 285 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-13 22:00 | 285 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-13 23:00 | 285 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-14 | 286 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-14 01:00 | 286 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-14 02:00 | 286 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-10-14 03:00 | 286 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-14 04:00 | 286 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-14 05:00 | 286 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-14 06:00 | 286 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-14 07:00 | 286 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-14 08:00 | 286 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-14 09:00 | 286 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-14 10:00 | 286 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-14 11:00 | 286 | 1 | 1 | 56 | 5.295 | 2.7043
2018-10-14 12:00 | 286 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-10-14 13:00 | 286 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-10-14 14:00 | 286 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-10-14 15:00 | 286 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-10-14 16:00 | 286 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-10-14 17:00 | 286 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-10-14 18:00 | 286 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-14 19:00 | 286 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-14 20:00 | 286 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-10-14 21:00 | 286 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-14 22:00 | 286 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-14 23:00 | 286 | 1 | 1 | 56 | 5.295 | 2.7043
2018-10-15 | 287 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-15 01:00 | 287 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-15 02:00 | 287 | 1 | 1 | 56 | 5.295 | 2.7043
2018-10-15 03:00 | 287 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-15 04:00 | 287 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-15 05:00 | 287 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-15 06:00 | 287 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-15 07:00 | 287 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-10-15 08:00 | 287 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-10-15 09:00 | 287 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-10-15 10:00 | 287 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-10-15 11:00 | 287 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-15 12:00 | 287 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-15 13:00 | 287 | 1 | 1 | 64 | 5.3779 | 2.687
2018-10-15 14:00 | 287 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-15 15:00 | 287 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-15 16:00 | 287 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-15 17:00 | 287 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-15 18:00 | 287 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-15 19:00 | 287 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-15 20:00 | 287 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-10-15 21:00 | 287 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-10-15 22:00 | 287 | 1 | 1 | 69 | 5.5873 | 2.7167
2018-10-15 23:00 | 287 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-10-16 | 288 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-10-16 01:00 | 288 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-16 02:00 | 288 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-10-16 03:00 | 288 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-10-16 04:00 | 288 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-10-16 05:00 | 288 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-16 06:00 | 288 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-16 07:00 | 288 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-16 08:00 | 288 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-10-16 09:00 | 288 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-10-16 10:00 | 288 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-16 11:00 | 288 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-10-16 12:00 | 288 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-16 13:00 | 288 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-16 14:00 | 288 | 1 | 1 | 56 | 5.295 | 2.7043
2018-10-16 15:00 | 288 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-16 16:00 | 288 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-16 17:00 | 288 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-16 18:00 | 288 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-16 19:00 | 288 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-16 20:00 | 288 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-16 21:00 | 288 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-16 22:00 | 288 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-16 23:00 | 288 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-17 | 289 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-17 01:00 | 289 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-17 02:00 | 289 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-10-17 03:00 | 289 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-10-17 04:00 | 289 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-17 05:00 | 289 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-10-17 06:00 | 289 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-10-17 07:00 | 289 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-10-17 08:00 | 289 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-10-17 09:00 | 289 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-10-17 10:00 | 289 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-17 11:00 | 289 | 1 | 1 | 56 | 5.295 | 2.7043
2018-10-17 12:00 | 289 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-17 13:00 | 289 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-17 14:00 | 289 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-17 15:00 | 289 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-17 16:00 | 289 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-17 17:00 | 289 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-17 18:00 | 289 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-10-17 19:00 | 289 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-17 20:00 | 289 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-17 21:00 | 289 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-17 22:00 | 289 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-17 23:00 | 289 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-18 | 290 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-18 01:00 | 290 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-10-18 02:00 | 290 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-18 03:00 | 290 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-18 04:00 | 290 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-10-18 05:00 | 290 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-18 06:00 | 290 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-18 07:00 | 290 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-10-18 08:00 | 290 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-10-18 09:00 | 290 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-18 10:00 | 290 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-18 11:00 | 290 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-10-18 12:00 | 290 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-18 13:00 | 290 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-18 14:00 | 290 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-10-18 15:00 | 290 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-18 16:00 | 290 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-18 17:00 | 290 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-18 18:00 | 290 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-18 19:00 | 290 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-18 20:00 | 290 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-18 21:00 | 290 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-18 22:00 | 290 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-18 23:00 | 290 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-19 | 291 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-19 01:00 | 291 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-19 02:00 | 291 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-10-19 03:00 | 291 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-19 04:00 | 291 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-19 05:00 | 291 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-10-19 06:00 | 291 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-19 07:00 | 291 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-19 08:00 | 291 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-10-19 09:00 | 291 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-19 10:00 | 291 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-19 11:00 | 291 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-10-19 12:00 | 291 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-19 13:00 | 291 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-10-19 14:00 | 291 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-10-19 15:00 | 291 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-19 16:00 | 291 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-19 17:00 | 291 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-10-19 18:00 | 291 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-10-19 19:00 | 291 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-10-19 20:00 | 291 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-10-19 21:00 | 291 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-19 22:00 | 291 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-19 23:00 | 291 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-10-20 | 292 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-10-20 01:00 | 292 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-10-20 02:00 | 292 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-10-20 03:00 | 292 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-20 04:00 | 292 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-20 05:00 | 292 | 1 | 1 | 56 | 5.295 | 2.7043
2018-10-20 06:00 | 292 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-20 07:00 | 292 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-20 08:00 | 292 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-20 09:00 | 292 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-20 10:00 | 292 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-20 11:00 | 292 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-10-20 12:00 | 292 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-10-20 13:00 | 292 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-10-20 14:00 | 292 | 1 | 1 | 62 | 5.3281 | 2.6838
2018-10-20 15:00 | 292 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-20 16:00 | 292 | 1 | 1 | 64 | 5.3779 | 2.687
2018-10-20 17:00 | 292 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-20 18:00 | 292 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-20 19:00 | 292 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-20 20:00 | 292 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-10-20 21:00 | 292 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-20 22:00 | 292 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-20 23:00 | 292 | 1 | 1 | 56 | 5.295 | 2.7043
2018-10-21 | 293 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-21 01:00 | 293 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-21 02:00 | 293 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-21 03:00 | 293 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-21 04:00 | 293 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-21 05:00 | 293 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-21 06:00 | 293 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-21 07:00 | 293 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-21 08:00 | 293 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-21 09:00 | 293 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-21 10:00 | 293 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-21 11:00 | 293 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-21 12:00 | 293 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-21 13:00 | 293 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-21 14:00 | 293 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-10-21 15:00 | 293 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-21 16:00 | 293 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-21 17:00 | 293 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-21 18:00 | 293 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-21 19:00 | 293 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-21 20:00 | 293 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-21 21:00 | 293 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-21 22:00 | 293 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-21 23:00 | 293 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-10-22 | 294 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-10-22 01:00 | 294 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-10-22 02:00 | 294 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-10-22 03:00 | 294 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-10-22 04:00 | 294 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-10-22 05:00 | 294 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-10-22 06:00 | 294 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-22 07:00 | 294 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-22 08:00 | 294 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-22 09:00 | 294 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-22 10:00 | 294 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-22 11:00 | 294 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-22 12:00 | 294 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-22 13:00 | 294 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-22 14:00 | 294 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-22 15:00 | 294 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-22 16:00 | 294 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-22 17:00 | 294 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-22 18:00 | 294 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-22 19:00 | 294 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-22 20:00 | 294 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-10-22 21:00 | 294 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-22 22:00 | 294 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-22 23:00 | 294 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-10-23 | 295 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-23 01:00 | 295 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-10-23 02:00 | 295 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-10-23 03:00 | 295 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-10-23 04:00 | 295 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-10-23 05:00 | 295 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-23 06:00 | 295 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-23 07:00 | 295 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-23 08:00 | 295 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-23 09:00 | 295 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-10-23 10:00 | 295 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-23 11:00 | 295 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-23 12:00 | 295 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-10-23 13:00 | 295 | 1 | 1 | 64 | 5.3779 | 2.687
2018-10-23 14:00 | 295 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-23 15:00 | 295 | 1 | 1 | 67 | 5.489 | 2.7011
2018-10-23 16:00 | 295 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-23 17:00 | 295 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-10-23 18:00 | 295 | 1 | 1 | 64 | 5.3779 | 2.687
2018-10-23 19:00 | 295 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-10-23 20:00 | 295 | 1 | 1 | 56 | 5.295 | 2.7043
2018-10-23 21:00 | 295 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-23 22:00 | 295 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-23 23:00 | 295 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-10-24 | 296 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-24 01:00 | 296 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-10-24 02:00 | 296 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-24 03:00 | 296 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-24 04:00 | 296 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-10-24 05:00 | 296 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-24 06:00 | 296 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-10-24 07:00 | 296 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-24 08:00 | 296 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-24 09:00 | 296 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-24 10:00 | 296 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-24 11:00 | 296 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-10-24 12:00 | 296 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-24 13:00 | 296 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-24 14:00 | 296 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-24 15:00 | 296 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-24 16:00 | 296 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-24 17:00 | 296 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-24 18:00 | 296 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-24 19:00 | 296 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-24 20:00 | 296 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-24 21:00 | 296 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-24 22:00 | 296 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-24 23:00 | 296 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-25 | 297 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-25 01:00 | 297 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-10-25 02:00 | 297 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-25 03:00 | 297 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-25 04:00 | 297 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-25 05:00 | 297 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-25 06:00 | 297 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-25 07:00 | 297 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-25 08:00 | 297 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-10-25 09:00 | 297 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-25 10:00 | 297 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-25 11:00 | 297 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-10-25 12:00 | 297 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-25 13:00 | 297 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-25 14:00 | 297 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-10-25 15:00 | 297 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-25 16:00 | 297 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-25 17:00 | 297 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-10-25 18:00 | 297 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-25 19:00 | 297 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-25 20:00 | 297 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-25 21:00 | 297 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-25 22:00 | 297 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-25 23:00 | 297 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-10-26 | 298 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-10-26 01:00 | 298 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-10-26 02:00 | 298 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-10-26 03:00 | 298 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-10-26 04:00 | 298 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-10-26 05:00 | 298 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-10-26 06:00 | 298 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-10-26 07:00 | 298 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-10-26 08:00 | 298 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-10-26 09:00 | 298 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-26 10:00 | 298 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-26 11:00 | 298 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-26 12:00 | 298 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-26 13:00 | 298 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-26 14:00 | 298 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-26 15:00 | 298 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-26 16:00 | 298 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-26 17:00 | 298 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-26 18:00 | 298 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-26 19:00 | 298 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-26 20:00 | 298 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-26 21:00 | 298 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-26 22:00 | 298 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-26 23:00 | 298 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-27 | 299 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-27 01:00 | 299 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-10-27 02:00 | 299 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-27 03:00 | 299 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-27 04:00 | 299 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-27 05:00 | 299 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-10-27 06:00 | 299 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-27 07:00 | 299 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-27 08:00 | 299 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-10-27 09:00 | 299 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-27 10:00 | 299 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-27 11:00 | 299 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-10-27 12:00 | 299 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-27 13:00 | 299 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-27 14:00 | 299 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-10-27 15:00 | 299 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-27 16:00 | 299 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-27 17:00 | 299 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-27 18:00 | 299 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-27 19:00 | 299 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-27 20:00 | 299 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-27 21:00 | 299 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-27 22:00 | 299 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-27 23:00 | 299 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-10-28 | 300 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-28 01:00 | 300 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-28 02:00 | 300 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-28 03:00 | 300 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-28 04:00 | 300 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-28 05:00 | 300 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-28 06:00 | 300 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-28 07:00 | 300 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-28 08:00 | 300 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-28 09:00 | 300 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-28 10:00 | 300 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-28 11:00 | 300 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-28 12:00 | 300 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-28 13:00 | 300 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-28 14:00 | 300 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-10-28 15:00 | 300 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-28 16:00 | 300 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-28 17:00 | 300 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-10-28 18:00 | 300 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-28 19:00 | 300 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-28 20:00 | 300 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-10-28 21:00 | 300 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-28 22:00 | 300 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-28 23:00 | 300 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-10-29 | 301 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-29 01:00 | 301 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-29 02:00 | 301 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-29 03:00 | 301 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-29 04:00 | 301 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-29 05:00 | 301 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-29 06:00 | 301 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-29 07:00 | 301 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-29 08:00 | 301 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-29 09:00 | 301 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-29 10:00 | 301 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-29 11:00 | 301 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-10-29 12:00 | 301 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-29 13:00 | 301 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-29 14:00 | 301 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-29 15:00 | 301 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-29 16:00 | 301 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-29 17:00 | 301 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-29 18:00 | 301 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-29 19:00 | 301 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-29 20:00 | 301 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-29 21:00 | 301 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-29 22:00 | 301 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-29 23:00 | 301 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-30 | 302 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-30 01:00 | 302 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-10-30 02:00 | 302 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-10-30 03:00 | 302 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-30 04:00 | 302 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-30 05:00 | 302 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-10-30 06:00 | 302 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-30 07:00 | 302 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-30 08:00 | 302 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-10-30 09:00 | 302 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-30 10:00 | 302 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-30 11:00 | 302 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-10-30 12:00 | 302 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-30 13:00 | 302 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-30 14:00 | 302 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-30 15:00 | 302 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-30 16:00 | 302 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-30 17:00 | 302 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-30 18:00 | 302 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-30 19:00 | 302 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-30 20:00 | 302 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-10-30 21:00 | 302 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-30 22:00 | 302 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-30 23:00 | 302 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-31 | 303 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-31 01:00 | 303 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-31 02:00 | 303 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-10-31 03:00 | 303 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-10-31 04:00 | 303 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-10-31 05:00 | 303 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-10-31 06:00 | 303 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-31 07:00 | 303 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-10-31 08:00 | 303 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-10-31 09:00 | 303 | 1 | 1 | 52 | 5.37 | 2.7429
2018-10-31 10:00 | 303 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-10-31 11:00 | 303 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-10-31 12:00 | 303 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-10-31 13:00 | 303 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-31 14:00 | 303 | 1 | 1 | 64 | 5.3779 | 2.687
2018-10-31 15:00 | 303 | 1 | 1 | 64 | 5.3779 | 2.687
2018-10-31 16:00 | 303 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-31 17:00 | 303 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-10-31 18:00 | 303 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-10-31 19:00 | 303 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-10-31 20:00 | 303 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-10-31 21:00 | 303 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-10-31 22:00 | 303 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-10-31 23:00 | 303 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-11-01 | 304 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-11-01 01:00 | 304 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-11-01 02:00 | 304 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-11-01 03:00 | 304 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-11-01 04:00 | 304 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-11-01 05:00 | 304 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-11-01 06:00 | 304 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-11-01 07:00 | 304 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-11-01 08:00 | 304 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-11-01 09:00 | 304 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-11-01 10:00 | 304 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-11-01 11:00 | 304 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-11-01 12:00 | 304 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-11-01 13:00 | 304 | 1 | 1 | 70 | 5.6438 | 2.7264
2018-11-01 14:00 | 304 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-11-01 15:00 | 304 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-11-01 16:00 | 304 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-11-01 17:00 | 304 | 1 | 1 | 67 | 5.489 | 2.7011
2018-11-01 18:00 | 304 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-11-01 19:00 | 304 | 1 | 1 | 64 | 5.3779 | 2.687
2018-11-01 20:00 | 304 | 1 | 1 | 64 | 5.3779 | 2.687
2018-11-01 21:00 | 304 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-11-01 22:00 | 304 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-11-01 23:00 | 304 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-11-02 | 305 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-11-02 01:00 | 305 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-11-02 02:00 | 305 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-11-02 03:00 | 305 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-11-02 04:00 | 305 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-11-02 05:00 | 305 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-11-02 06:00 | 305 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-11-02 07:00 | 305 | 1 | 1 | 64 | 5.3779 | 2.687
2018-11-02 08:00 | 305 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-11-02 09:00 | 305 | 1 | 1 | 64 | 5.3779 | 2.687
2018-11-02 10:00 | 305 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-11-02 11:00 | 305 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-11-02 12:00 | 305 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-11-02 13:00 | 305 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-11-02 14:00 | 305 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-11-02 15:00 | 305 | 1 | 1 | 68 | 5.5357 | 2.7083
2018-11-02 16:00 | 305 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-11-02 17:00 | 305 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-11-02 18:00 | 305 | 1 | 1 | 64 | 5.3779 | 2.687
2018-11-02 19:00 | 305 | 1 | 1 | 64 | 5.3779 | 2.687
2018-11-02 20:00 | 305 | 1 | 1 | 65 | 5.4101 | 2.6904
2018-11-02 21:00 | 305 | 1 | 1 | 64 | 5.3779 | 2.687
2018-11-02 22:00 | 305 | 1 | 1 | 64 | 5.3779 | 2.687
2018-11-02 23:00 | 305 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-11-03 | 306 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-11-03 01:00 | 306 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-11-03 02:00 | 306 | 1 | 1 | 66 | 5.4471 | 2.6951
2018-11-03 03:00 | 306 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-11-03 04:00 | 306 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-11-03 05:00 | 306 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-11-03 06:00 | 306 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-11-03 07:00 | 306 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-11-03 08:00 | 306 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-11-03 09:00 | 306 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-11-03 10:00 | 306 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-11-03 11:00 | 306 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-03 12:00 | 306 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-03 13:00 | 306 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-03 14:00 | 306 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-11-03 15:00 | 306 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-11-03 16:00 | 306 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-11-03 17:00 | 306 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-11-03 18:00 | 306 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-03 19:00 | 306 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-03 20:00 | 306 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-03 21:00 | 306 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-03 22:00 | 306 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-03 23:00 | 306 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-04 | 307 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-04 01:00 | 307 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-11-04 01:00 | 307 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-11-04 02:00 | 307 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-04 03:00 | 307 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-04 04:00 | 307 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-04 05:00 | 307 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-04 06:00 | 307 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-04 07:00 | 307 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-04 08:00 | 307 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-04 09:00 | 307 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-04 10:00 | 307 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-04 11:00 | 307 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-04 12:00 | 307 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-04 13:00 | 307 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-04 14:00 | 307 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-04 15:00 | 307 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-04 16:00 | 307 | 1 | 1 | 56 | 5.295 | 2.7043
2018-11-04 17:00 | 307 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-04 18:00 | 307 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-04 19:00 | 307 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-11-04 20:00 | 307 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-04 21:00 | 307 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-04 22:00 | 307 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-11-04 23:00 | 307 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-05 | 308 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-11-05 01:00 | 308 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-11-05 02:00 | 308 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-05 03:00 | 308 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-05 04:00 | 308 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-05 05:00 | 308 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-05 06:00 | 308 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-05 07:00 | 308 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-11-05 08:00 | 308 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-05 09:00 | 308 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-05 10:00 | 308 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-05 11:00 | 308 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-05 12:00 | 308 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-05 13:00 | 308 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-05 14:00 | 308 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-05 15:00 | 308 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-05 16:00 | 308 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-05 17:00 | 308 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-05 18:00 | 308 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-05 19:00 | 308 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-11-05 20:00 | 308 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-05 21:00 | 308 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-05 22:00 | 308 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-05 23:00 | 308 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-06 | 309 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-11-06 01:00 | 309 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-11-06 02:00 | 309 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-06 03:00 | 309 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-06 04:00 | 309 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-06 05:00 | 309 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-06 06:00 | 309 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-06 07:00 | 309 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-11-06 08:00 | 309 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-06 09:00 | 309 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-06 10:00 | 309 | 1 | 1 | 56 | 5.295 | 2.7043
2018-11-06 11:00 | 309 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-06 12:00 | 309 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-06 13:00 | 309 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-11-06 14:00 | 309 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-11-06 15:00 | 309 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-11-06 16:00 | 309 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-11-06 17:00 | 309 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-11-06 18:00 | 309 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-11-06 19:00 | 309 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-11-06 20:00 | 309 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-11-06 21:00 | 309 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-11-06 22:00 | 309 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-11-06 23:00 | 309 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-11-07 | 310 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-11-07 01:00 | 310 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-11-07 02:00 | 310 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-11-07 03:00 | 310 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-11-07 04:00 | 310 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-11-07 05:00 | 310 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-07 06:00 | 310 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-07 07:00 | 310 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-11-07 08:00 | 310 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-07 09:00 | 310 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-07 10:00 | 310 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-11-07 11:00 | 310 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-11-07 12:00 | 310 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-11-07 13:00 | 310 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-11-07 14:00 | 310 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-11-07 15:00 | 310 | 1 | 1 | 64 | 5.3779 | 2.687
2018-11-07 16:00 | 310 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-11-07 17:00 | 310 | 1 | 1 | 63 | 5.3506 | 2.6848
2018-11-07 18:00 | 310 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-11-07 19:00 | 310 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-11-07 20:00 | 310 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-11-07 21:00 | 310 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-11-07 22:00 | 310 | 1 | 1 | 60 | 5.2976 | 2.6856
2018-11-07 23:00 | 310 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-11-08 | 311 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-11-08 01:00 | 311 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-11-08 02:00 | 311 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-08 03:00 | 311 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-08 04:00 | 311 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-08 05:00 | 311 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-08 06:00 | 311 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-08 07:00 | 311 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-08 08:00 | 311 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-08 09:00 | 311 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-08 10:00 | 311 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-08 11:00 | 311 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-08 12:00 | 311 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-08 13:00 | 311 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-08 14:00 | 311 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-08 15:00 | 311 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-11-08 16:00 | 311 | 1 | 1 | 56 | 5.295 | 2.7043
2018-11-08 17:00 | 311 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-08 18:00 | 311 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-08 19:00 | 311 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-11-08 20:00 | 311 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-08 21:00 | 311 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-08 22:00 | 311 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-08 23:00 | 311 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-09 | 312 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-09 01:00 | 312 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-09 02:00 | 312 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-09 03:00 | 312 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-09 04:00 | 312 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-11-09 05:00 | 312 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-09 06:00 | 312 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-09 07:00 | 312 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-11-09 08:00 | 312 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-09 09:00 | 312 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-09 10:00 | 312 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-11-09 11:00 | 312 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-09 12:00 | 312 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-09 13:00 | 312 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-09 14:00 | 312 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-09 15:00 | 312 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-09 16:00 | 312 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-09 17:00 | 312 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-09 18:00 | 312 | 1 | 1 | 51.5 | 5.3848 | 2.7491
2018-11-09 19:00 | 312 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-11-09 20:00 | 312 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-09 21:00 | 312 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-09 22:00 | 312 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-09 23:00 | 312 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-10 | 313 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-11-10 01:00 | 313 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-10 02:00 | 313 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-10 03:00 | 313 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-10 04:00 | 313 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-10 05:00 | 313 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-10 06:00 | 313 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-10 07:00 | 313 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-10 08:00 | 313 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-10 09:00 | 313 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-10 10:00 | 313 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-10 11:00 | 313 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-10 12:00 | 313 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-10 13:00 | 313 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-10 14:00 | 313 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-10 15:00 | 313 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-10 16:00 | 313 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-11-10 17:00 | 313 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-10 18:00 | 313 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-10 19:00 | 313 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-11-10 20:00 | 313 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-10 21:00 | 313 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-10 22:00 | 313 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-10 23:00 | 313 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-11 | 314 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-11-11 01:00 | 314 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-11-11 02:00 | 314 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-11 03:00 | 314 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-11 04:00 | 314 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-11-11 05:00 | 314 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-11 06:00 | 314 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-11 07:00 | 314 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-11 08:00 | 314 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-11 09:00 | 314 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-11 10:00 | 314 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-11 11:00 | 314 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-11 12:00 | 314 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-11 13:00 | 314 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-11 14:00 | 314 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-11 15:00 | 314 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-11 16:00 | 314 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-11 17:00 | 314 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-11 18:00 | 314 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-11 19:00 | 314 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-11 20:00 | 314 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-11 21:00 | 314 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-11 22:00 | 314 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-11-11 23:00 | 314 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-12 | 315 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-12 01:00 | 315 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-11-12 02:00 | 315 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-12 03:00 | 315 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-12 04:00 | 315 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-12 05:00 | 315 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-12 06:00 | 315 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-12 07:00 | 315 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-11-12 08:00 | 315 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-12 09:00 | 315 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-12 10:00 | 315 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-12 11:00 | 315 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-12 12:00 | 315 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-12 13:00 | 315 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-11-12 14:00 | 315 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-12 15:00 | 315 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-12 16:00 | 315 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-12 17:00 | 315 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-12 18:00 | 315 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-12 19:00 | 315 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-12 20:00 | 315 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-12 21:00 | 315 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-12 22:00 | 315 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-12 23:00 | 315 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-13 | 316 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-13 01:00 | 316 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-13 02:00 | 316 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-13 03:00 | 316 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-13 04:00 | 316 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-13 05:00 | 316 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-13 06:00 | 316 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-13 07:00 | 316 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-13 08:00 | 316 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-13 09:00 | 316 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-13 10:00 | 316 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-13 11:00 | 316 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-13 12:00 | 316 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-13 13:00 | 316 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-13 14:00 | 316 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-13 15:00 | 316 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-13 16:00 | 316 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-11-13 17:00 | 316 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-13 18:00 | 316 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-13 19:00 | 316 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-13 20:00 | 316 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-13 21:00 | 316 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-13 22:00 | 316 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-13 23:00 | 316 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-14 | 317 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-11-14 01:00 | 317 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-14 02:00 | 317 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-14 03:00 | 317 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-14 04:00 | 317 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-14 05:00 | 317 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-14 06:00 | 317 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-14 07:00 | 317 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-11-14 08:00 | 317 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-14 09:00 | 317 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-14 10:00 | 317 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-11-14 11:00 | 317 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-14 12:00 | 317 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-14 13:00 | 317 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-14 14:00 | 317 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-14 15:00 | 317 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-14 16:00 | 317 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-11-14 17:00 | 317 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-14 18:00 | 317 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-14 19:00 | 317 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-11-14 20:00 | 317 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-11-14 21:00 | 317 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-11-14 22:00 | 317 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-11-14 23:00 | 317 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-11-15 | 318 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-11-15 01:00 | 318 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-11-15 02:00 | 318 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-15 03:00 | 318 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-11-15 04:00 | 318 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-11-15 05:00 | 318 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-11-15 06:00 | 318 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-11-15 07:00 | 318 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-15 08:00 | 318 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-15 09:00 | 318 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-15 10:00 | 318 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-11-15 11:00 | 318 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-11-15 12:00 | 318 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-11-15 13:00 | 318 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-11-15 14:00 | 318 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-11-15 15:00 | 318 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-11-15 16:00 | 318 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-11-15 17:00 | 318 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-11-15 18:00 | 318 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-11-15 19:00 | 318 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-11-15 20:00 | 318 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-11-15 21:00 | 318 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-11-15 22:00 | 318 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-11-15 23:00 | 318 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-16 | 319 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-11-16 01:00 | 319 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-11-16 02:00 | 319 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-16 03:00 | 319 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-16 04:00 | 319 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-11-16 05:00 | 319 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-16 06:00 | 319 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-11-16 07:00 | 319 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-11-16 08:00 | 319 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-16 09:00 | 319 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-16 10:00 | 319 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-16 11:00 | 319 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-16 12:00 | 319 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-16 13:00 | 319 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-16 14:00 | 319 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-16 15:00 | 319 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-16 16:00 | 319 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-16 17:00 | 319 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-16 18:00 | 319 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-16 19:00 | 319 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-16 20:00 | 319 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-16 21:00 | 319 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-16 22:00 | 319 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-16 23:00 | 319 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-17 | 320 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-11-17 01:00 | 320 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-11-17 02:00 | 320 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-17 03:00 | 320 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-17 04:00 | 320 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-17 05:00 | 320 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-17 06:00 | 320 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-17 07:00 | 320 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-11-17 08:00 | 320 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-17 09:00 | 320 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-17 10:00 | 320 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-17 11:00 | 320 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-17 12:00 | 320 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-17 13:00 | 320 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-17 14:00 | 320 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-17 15:00 | 320 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-17 16:00 | 320 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-17 17:00 | 320 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-17 18:00 | 320 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-17 19:00 | 320 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-17 20:00 | 320 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-17 21:00 | 320 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-17 22:00 | 320 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-17 23:00 | 320 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-18 | 321 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-11-18 01:00 | 321 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-11-18 02:00 | 321 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-18 03:00 | 321 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-18 04:00 | 321 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-18 05:00 | 321 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-18 06:00 | 321 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-18 07:00 | 321 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-11-18 08:00 | 321 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-18 09:00 | 321 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-18 10:00 | 321 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-18 11:00 | 321 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-18 12:00 | 321 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-18 13:00 | 321 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-18 14:00 | 321 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-18 15:00 | 321 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-18 16:00 | 321 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-11-18 17:00 | 321 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-18 18:00 | 321 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-18 19:00 | 321 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-11-18 20:00 | 321 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-18 21:00 | 321 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-18 22:00 | 321 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-18 23:00 | 321 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-19 | 322 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-11-19 01:00 | 322 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-11-19 02:00 | 322 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-19 03:00 | 322 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-19 04:00 | 322 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-11-19 05:00 | 322 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-19 06:00 | 322 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-19 07:00 | 322 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-19 08:00 | 322 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-19 09:00 | 322 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-19 10:00 | 322 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-19 11:00 | 322 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-19 12:00 | 322 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-19 13:00 | 322 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-11-19 14:00 | 322 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-19 15:00 | 322 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-19 16:00 | 322 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-11-19 17:00 | 322 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-19 18:00 | 322 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-19 19:00 | 322 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-11-19 20:00 | 322 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-19 21:00 | 322 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-19 22:00 | 322 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-19 23:00 | 322 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-20 | 323 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-20 01:00 | 323 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-20 02:00 | 323 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-20 03:00 | 323 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-20 04:00 | 323 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-20 05:00 | 323 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-20 06:00 | 323 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-20 07:00 | 323 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-20 08:00 | 323 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-20 09:00 | 323 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-20 10:00 | 323 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-11-20 11:00 | 323 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-20 12:00 | 323 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-20 13:00 | 323 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-20 14:00 | 323 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-20 15:00 | 323 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-20 16:00 | 323 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-20 17:00 | 323 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-20 18:00 | 323 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-20 19:00 | 323 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-20 20:00 | 323 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-20 21:00 | 323 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-20 22:00 | 323 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-20 23:00 | 323 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-21 | 324 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-21 01:00 | 324 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-11-21 02:00 | 324 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-21 03:00 | 324 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-21 04:00 | 324 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-21 05:00 | 324 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-21 06:00 | 324 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-21 07:00 | 324 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-11-21 08:00 | 324 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-21 09:00 | 324 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-21 10:00 | 324 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-21 11:00 | 324 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-21 12:00 | 324 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-21 13:00 | 324 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-11-21 14:00 | 324 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-21 15:00 | 324 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-21 16:00 | 324 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-21 17:00 | 324 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-21 18:00 | 324 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-21 19:00 | 324 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-11-21 20:00 | 324 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-21 21:00 | 324 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-11-21 22:00 | 324 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-11-21 23:00 | 324 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-11-22 | 325 | 1 | 1 | 29 | 7.307 | 3.3521
2018-11-22 01:00 | 325 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-11-22 02:00 | 325 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-11-22 03:00 | 325 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-11-22 04:00 | 325 | 1 | 1 | 24 | 8.0675 | 3.5718
2018-11-22 05:00 | 325 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-11-22 06:00 | 325 | 1 | 1 | 21 | 8.5821 | 3.7186
2018-11-22 07:00 | 325 | 1 | 1 | 21 | 8.5821 | 3.7186
2018-11-22 08:00 | 325 | 1 | 1 | 21 | 8.5821 | 3.7186
2018-11-22 09:00 | 325 | 1 | 1 | 21 | 8.5821 | 3.7186
2018-11-22 10:00 | 325 | 1 | 1 | 23 | 8.2342 | 3.6195
2018-11-22 11:00 | 325 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-11-22 12:00 | 325 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-11-22 13:00 | 325 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-11-22 14:00 | 325 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-11-22 15:00 | 325 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-11-22 16:00 | 325 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-11-22 17:00 | 325 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-11-22 18:00 | 325 | 1 | 1 | 25 | 7.9057 | 3.5254
2018-11-22 19:00 | 325 | 1 | 1 | 24 | 8.0675 | 3.5718
2018-11-22 20:00 | 325 | 1 | 1 | 21 | 8.5821 | 3.7186
2018-11-22 21:00 | 325 | 1 | 1 | 21 | 8.5821 | 3.7186
2018-11-22 22:00 | 325 | 1 | 1 | 21 | 8.5821 | 3.7186
2018-11-22 23:00 | 325 | 1 | 1 | 19 | 8.9494 | 3.8227
2018-11-23 | 326 | 1 | 1 | 19 | 8.9494 | 3.8227
2018-11-23 01:00 | 326 | 1 | 1 | 19 | 8.9494 | 3.8227
2018-11-23 02:00 | 326 | 1 | 1 | 19 | 8.9494 | 3.8227
2018-11-23 03:00 | 326 | 1 | 1 | 18 | 9.1403 | 3.8767
2018-11-23 04:00 | 326 | 1 | 1 | 18 | 9.1403 | 3.8767
2018-11-23 05:00 | 326 | 1 | 1 | 18 | 9.1403 | 3.8767
2018-11-23 06:00 | 326 | 1 | 1 | 18 | 9.1403 | 3.8767
2018-11-23 07:00 | 326 | 1 | 1 | 17 | 9.3361 | 3.9318
2018-11-23 08:00 | 326 | 1 | 1 | 19 | 8.9494 | 3.8227
2018-11-23 09:00 | 326 | 1 | 1 | 23 | 8.2342 | 3.6195
2018-11-23 10:00 | 326 | 1 | 1 | 22 | 8.4057 | 3.6684
2018-11-23 11:00 | 326 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-11-23 12:00 | 326 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-11-23 13:00 | 326 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-11-23 14:00 | 326 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-11-23 15:00 | 326 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-11-23 16:00 | 326 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-23 17:00 | 326 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-23 18:00 | 326 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-23 19:00 | 326 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-23 20:00 | 326 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-23 21:00 | 326 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-23 22:00 | 326 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-23 23:00 | 326 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-24 | 327 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-24 01:00 | 327 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-24 02:00 | 327 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-24 03:00 | 327 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-24 04:00 | 327 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-24 05:00 | 327 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-11-24 06:00 | 327 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-11-24 07:00 | 327 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-11-24 08:00 | 327 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-11-24 09:00 | 327 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-11-24 10:00 | 327 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-11-24 11:00 | 327 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-24 12:00 | 327 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-24 13:00 | 327 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-11-24 14:00 | 327 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-24 15:00 | 327 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-24 16:00 | 327 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-24 17:00 | 327 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-24 18:00 | 327 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-24 19:00 | 327 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-24 20:00 | 327 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-24 21:00 | 327 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-24 22:00 | 327 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-24 23:00 | 327 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-25 | 328 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-11-25 01:00 | 328 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-25 02:00 | 328 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-25 03:00 | 328 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-25 04:00 | 328 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-25 05:00 | 328 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-25 06:00 | 328 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-25 07:00 | 328 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-25 08:00 | 328 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-25 09:00 | 328 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-25 10:00 | 328 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-25 11:00 | 328 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-25 12:00 | 328 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-25 13:00 | 328 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-25 14:00 | 328 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-25 15:00 | 328 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-25 16:00 | 328 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-25 17:00 | 328 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-25 18:00 | 328 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-25 19:00 | 328 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-11-25 20:00 | 328 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-25 21:00 | 328 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-25 22:00 | 328 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-25 23:00 | 328 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-26 | 329 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-11-26 01:00 | 329 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-26 02:00 | 329 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-26 03:00 | 329 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-26 04:00 | 329 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-26 05:00 | 329 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-26 06:00 | 329 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-26 07:00 | 329 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-26 08:00 | 329 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-26 09:00 | 329 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-26 10:00 | 329 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-11-26 11:00 | 329 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-26 12:00 | 329 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-26 13:00 | 329 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-11-26 14:00 | 329 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-11-26 15:00 | 329 | 1 | 1 | 52 | 5.37 | 2.7429
2018-11-26 16:00 | 329 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-11-26 17:00 | 329 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-26 18:00 | 329 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-26 19:00 | 329 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-11-26 20:00 | 329 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-26 21:00 | 329 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-26 22:00 | 329 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-11-26 23:00 | 329 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-27 | 330 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-11-27 01:00 | 330 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-27 02:00 | 330 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-27 03:00 | 330 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-27 04:00 | 330 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-27 05:00 | 330 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-27 06:00 | 330 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-27 07:00 | 330 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-11-27 08:00 | 330 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-27 09:00 | 330 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-27 10:00 | 330 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-11-27 11:00 | 330 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-27 12:00 | 330 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-27 13:00 | 330 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-27 14:00 | 330 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-27 15:00 | 330 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-27 16:00 | 330 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-27 17:00 | 330 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-27 18:00 | 330 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-27 19:00 | 330 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-11-27 20:00 | 330 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-27 21:00 | 330 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-27 22:00 | 330 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-27 23:00 | 330 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-28 | 331 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-11-28 01:00 | 331 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-11-28 02:00 | 331 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-28 03:00 | 331 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-28 04:00 | 331 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-28 05:00 | 331 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-28 06:00 | 331 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-28 07:00 | 331 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-11-28 08:00 | 331 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-28 09:00 | 331 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-11-28 10:00 | 331 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-28 11:00 | 331 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-28 12:00 | 331 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-28 13:00 | 331 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-28 14:00 | 331 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-28 15:00 | 331 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-28 16:00 | 331 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-11-28 17:00 | 331 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-28 18:00 | 331 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-28 19:00 | 331 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-11-28 20:00 | 331 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-28 21:00 | 331 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-28 22:00 | 331 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-11-28 23:00 | 331 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-29 | 332 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-11-29 01:00 | 332 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-29 02:00 | 332 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-29 03:00 | 332 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-29 04:00 | 332 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-29 05:00 | 332 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-29 06:00 | 332 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-29 07:00 | 332 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-11-29 08:00 | 332 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-29 09:00 | 332 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-29 10:00 | 332 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-29 11:00 | 332 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-29 12:00 | 332 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-29 13:00 | 332 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-29 14:00 | 332 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-11-29 15:00 | 332 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-11-29 16:00 | 332 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-11-29 17:00 | 332 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-29 18:00 | 332 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-29 19:00 | 332 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-11-29 20:00 | 332 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-29 21:00 | 332 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-29 22:00 | 332 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-29 23:00 | 332 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-30 | 333 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-11-30 01:00 | 333 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-11-30 02:00 | 333 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-30 03:00 | 333 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-30 04:00 | 333 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-30 05:00 | 333 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-30 06:00 | 333 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-30 07:00 | 333 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-30 08:00 | 333 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-30 09:00 | 333 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-30 10:00 | 333 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-11-30 11:00 | 333 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-30 12:00 | 333 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-30 13:00 | 333 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-30 14:00 | 333 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-30 15:00 | 333 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-11-30 16:00 | 333 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-30 17:00 | 333 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-30 18:00 | 333 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-30 19:00 | 333 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-11-30 20:00 | 333 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-11-30 21:00 | 333 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-30 22:00 | 333 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-11-30 23:00 | 333 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-01 | 334 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-01 01:00 | 334 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-01 02:00 | 334 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-01 03:00 | 334 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-01 04:00 | 334 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-01 05:00 | 334 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-01 06:00 | 334 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-01 07:00 | 334 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-01 08:00 | 334 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-01 09:00 | 334 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-01 10:00 | 334 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-01 11:00 | 334 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-01 12:00 | 334 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-01 13:00 | 334 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-12-01 14:00 | 334 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-01 15:00 | 334 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-01 16:00 | 334 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-01 17:00 | 334 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-01 18:00 | 334 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-01 19:00 | 334 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-12-01 20:00 | 334 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-01 21:00 | 334 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-01 22:00 | 334 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-01 23:00 | 334 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-02 | 335 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-02 01:00 | 335 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-02 02:00 | 335 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-02 03:00 | 335 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-02 04:00 | 335 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-12-02 05:00 | 335 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-02 06:00 | 335 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-02 07:00 | 335 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-02 08:00 | 335 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-02 09:00 | 335 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-02 10:00 | 335 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-12-02 11:00 | 335 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-12-02 12:00 | 335 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-12-02 13:00 | 335 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-12-02 14:00 | 335 | 1 | 1 | 52 | 5.37 | 2.7429
2018-12-02 15:00 | 335 | 1 | 1 | 52 | 5.37 | 2.7429
2018-12-02 16:00 | 335 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-12-02 17:00 | 335 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-12-02 18:00 | 335 | 1 | 1 | 52 | 5.37 | 2.7429
2018-12-02 19:00 | 335 | 1 | 1 | 52 | 5.37 | 2.7429
2018-12-02 20:00 | 335 | 1 | 1 | 52 | 5.37 | 2.7429
2018-12-02 21:00 | 335 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-12-02 22:00 | 335 | 1 | 1 | 52 | 5.37 | 2.7429
2018-12-02 23:00 | 335 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-03 | 336 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-12-03 01:00 | 336 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-03 02:00 | 336 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-03 03:00 | 336 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-03 04:00 | 336 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-03 05:00 | 336 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-03 06:00 | 336 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-03 07:00 | 336 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-03 08:00 | 336 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-03 09:00 | 336 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-03 10:00 | 336 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-03 11:00 | 336 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-03 12:00 | 336 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-12-03 13:00 | 336 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-12-03 14:00 | 336 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-12-03 15:00 | 336 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-12-03 16:00 | 336 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-12-03 17:00 | 336 | 1 | 1 | 52 | 5.37 | 2.7429
2018-12-03 18:00 | 336 | 1 | 1 | 52 | 5.37 | 2.7429
2018-12-03 19:00 | 336 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-12-03 20:00 | 336 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-12-03 21:00 | 336 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-12-03 22:00 | 336 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-12-03 23:00 | 336 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-04 | 337 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-04 01:00 | 337 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-04 02:00 | 337 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-04 03:00 | 337 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-04 04:00 | 337 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-04 05:00 | 337 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-04 06:00 | 337 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-04 07:00 | 337 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-04 08:00 | 337 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-04 09:00 | 337 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-04 10:00 | 337 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-04 11:00 | 337 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-04 12:00 | 337 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-04 13:00 | 337 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-04 14:00 | 337 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-04 15:00 | 337 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-04 16:00 | 337 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-04 17:00 | 337 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-04 18:00 | 337 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-04 19:00 | 337 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-04 20:00 | 337 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-04 21:00 | 337 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-04 22:00 | 337 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-12-04 23:00 | 337 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-05 | 338 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-05 01:00 | 338 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-12-05 02:00 | 338 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-05 03:00 | 338 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-05 04:00 | 338 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-05 05:00 | 338 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-05 06:00 | 338 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-12-05 07:00 | 338 | 1 | 1 | 29 | 7.307 | 3.3521
2018-12-05 08:00 | 338 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-05 09:00 | 338 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-05 10:00 | 338 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-05 11:00 | 338 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-05 12:00 | 338 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-05 13:00 | 338 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-05 14:00 | 338 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-05 15:00 | 338 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-05 16:00 | 338 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-05 17:00 | 338 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-05 18:00 | 338 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-05 19:00 | 338 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-05 20:00 | 338 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-05 21:00 | 338 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-05 22:00 | 338 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-05 23:00 | 338 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-06 | 339 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-06 01:00 | 339 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-06 02:00 | 339 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-06 03:00 | 339 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-12-06 04:00 | 339 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-12-06 05:00 | 339 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-12-06 06:00 | 339 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-06 07:00 | 339 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-12-06 08:00 | 339 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-12-06 09:00 | 339 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-06 10:00 | 339 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-06 11:00 | 339 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-06 12:00 | 339 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-06 13:00 | 339 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-06 14:00 | 339 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-06 15:00 | 339 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-06 16:00 | 339 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-06 17:00 | 339 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-06 18:00 | 339 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-06 19:00 | 339 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-06 20:00 | 339 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-06 21:00 | 339 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-06 22:00 | 339 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-06 23:00 | 339 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-07 | 340 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-07 01:00 | 340 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-07 02:00 | 340 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-07 03:00 | 340 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-07 04:00 | 340 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-07 05:00 | 340 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-07 06:00 | 340 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-07 07:00 | 340 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-07 08:00 | 340 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-07 09:00 | 340 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-07 10:00 | 340 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-07 11:00 | 340 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-07 12:00 | 340 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-07 13:00 | 340 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-07 14:00 | 340 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-07 15:00 | 340 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-07 16:00 | 340 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-07 17:00 | 340 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-07 18:00 | 340 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-07 19:00 | 340 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-12-07 20:00 | 340 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-07 21:00 | 340 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-07 22:00 | 340 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-07 23:00 | 340 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-08 | 341 | 1 | 1 | 29 | 7.307 | 3.3521
2018-12-08 01:00 | 341 | 1 | 1 | 29 | 7.307 | 3.3521
2018-12-08 02:00 | 341 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-12-08 03:00 | 341 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-12-08 04:00 | 341 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-12-08 05:00 | 341 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-12-08 06:00 | 341 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-12-08 07:00 | 341 | 1 | 1 | 26 | 7.7488 | 3.4802
2018-12-08 08:00 | 341 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-12-08 09:00 | 341 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-12-08 10:00 | 341 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-08 11:00 | 341 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-08 12:00 | 341 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-08 13:00 | 341 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-08 14:00 | 341 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-08 15:00 | 341 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-08 16:00 | 341 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-08 17:00 | 341 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-08 18:00 | 341 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-08 19:00 | 341 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-08 20:00 | 341 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-08 21:00 | 341 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-08 22:00 | 341 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-08 23:00 | 341 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-09 | 342 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-12-09 01:00 | 342 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-09 02:00 | 342 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-09 03:00 | 342 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-09 04:00 | 342 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-12-09 05:00 | 342 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-09 06:00 | 342 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-09 07:00 | 342 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-09 08:00 | 342 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-09 09:00 | 342 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-09 10:00 | 342 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-12-09 11:00 | 342 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-09 12:00 | 342 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-09 13:00 | 342 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-09 14:00 | 342 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-09 15:00 | 342 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-09 16:00 | 342 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-09 17:00 | 342 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-09 18:00 | 342 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-09 19:00 | 342 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-09 20:00 | 342 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-09 21:00 | 342 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-09 22:00 | 342 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-09 23:00 | 342 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-10 | 343 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-12-10 01:00 | 343 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-10 02:00 | 343 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-10 03:00 | 343 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-10 04:00 | 343 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-12-10 05:00 | 343 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-10 06:00 | 343 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-10 07:00 | 343 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-10 08:00 | 343 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-10 09:00 | 343 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-10 10:00 | 343 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-10 11:00 | 343 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-10 12:00 | 343 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-10 13:00 | 343 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-10 14:00 | 343 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-10 15:00 | 343 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-10 16:00 | 343 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-10 17:00 | 343 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-10 18:00 | 343 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-10 19:00 | 343 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-10 20:00 | 343 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-10 21:00 | 343 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-10 22:00 | 343 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-10 23:00 | 343 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-11 | 344 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-11 01:00 | 344 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-11 02:00 | 344 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-11 03:00 | 344 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-11 04:00 | 344 | 1 | 1 | 31 | 7.0367 | 3.2729
2018-12-11 05:00 | 344 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-11 06:00 | 344 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-11 07:00 | 344 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-11 08:00 | 344 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-11 09:00 | 344 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-11 10:00 | 344 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-11 11:00 | 344 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-11 12:00 | 344 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-11 13:00 | 344 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-11 14:00 | 344 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-11 15:00 | 344 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-11 16:00 | 344 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-11 17:00 | 344 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-11 18:00 | 344 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-11 19:00 | 344 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-11 20:00 | 344 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-11 21:00 | 344 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-11 22:00 | 344 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-11 23:00 | 344 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-12 | 345 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-12 01:00 | 345 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-12 02:00 | 345 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-12 03:00 | 345 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-12 04:00 | 345 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-12 05:00 | 345 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-12 06:00 | 345 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-12 07:00 | 345 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-12 08:00 | 345 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-12 09:00 | 345 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-12 10:00 | 345 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-12 11:00 | 345 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-12 12:00 | 345 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-12 13:00 | 345 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-12 14:00 | 345 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-12 15:00 | 345 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-12 16:00 | 345 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-12 17:00 | 345 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-12 18:00 | 345 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-12 19:00 | 345 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-12 20:00 | 345 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-12 21:00 | 345 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-12 22:00 | 345 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-12 23:00 | 345 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-13 | 346 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-13 01:00 | 346 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-13 02:00 | 346 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-13 03:00 | 346 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-13 04:00 | 346 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-13 05:00 | 346 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-13 06:00 | 346 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-13 07:00 | 346 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-13 08:00 | 346 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-13 09:00 | 346 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-13 10:00 | 346 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-13 11:00 | 346 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-13 12:00 | 346 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-13 13:00 | 346 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-13 14:00 | 346 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-13 15:00 | 346 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-13 16:00 | 346 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-13 17:00 | 346 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-13 18:00 | 346 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-13 19:00 | 346 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-13 20:00 | 346 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-13 21:00 | 346 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-13 22:00 | 346 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-13 23:00 | 346 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-14 | 347 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-14 01:00 | 347 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-14 02:00 | 347 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-14 03:00 | 347 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-14 04:00 | 347 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-14 05:00 | 347 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-14 06:00 | 347 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-14 07:00 | 347 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-14 08:00 | 347 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-14 09:00 | 347 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-14 10:00 | 347 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-12-14 11:00 | 347 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-14 12:00 | 347 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-14 13:00 | 347 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-14 14:00 | 347 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-14 15:00 | 347 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-14 16:00 | 347 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-12-14 17:00 | 347 | 1 | 1 | 52 | 5.37 | 2.7429
2018-12-14 18:00 | 347 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-12-14 19:00 | 347 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-12-14 20:00 | 347 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-12-14 21:00 | 347 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-12-14 22:00 | 347 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-12-14 23:00 | 347 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-12-15 | 348 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-12-15 01:00 | 348 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-12-15 02:00 | 348 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-15 03:00 | 348 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-15 04:00 | 348 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-15 05:00 | 348 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-15 06:00 | 348 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-15 07:00 | 348 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-12-15 08:00 | 348 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-15 09:00 | 348 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-15 10:00 | 348 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-12-15 11:00 | 348 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-15 12:00 | 348 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-15 13:00 | 348 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-12-15 14:00 | 348 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-12-15 15:00 | 348 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-12-15 16:00 | 348 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-12-15 17:00 | 348 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-12-15 18:00 | 348 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-15 19:00 | 348 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-12-15 20:00 | 348 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-15 21:00 | 348 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-15 22:00 | 348 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-12-15 23:00 | 348 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-16 | 349 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-16 01:00 | 349 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-16 02:00 | 349 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-16 03:00 | 349 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-16 04:00 | 349 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-16 05:00 | 349 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-16 06:00 | 349 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-16 07:00 | 349 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-16 08:00 | 349 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-16 09:00 | 349 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-16 10:00 | 349 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-16 11:00 | 349 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-16 12:00 | 349 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-16 13:00 | 349 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-16 14:00 | 349 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-16 15:00 | 349 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-16 16:00 | 349 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-16 17:00 | 349 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-16 18:00 | 349 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-16 19:00 | 349 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-16 20:00 | 349 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-16 21:00 | 349 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-16 22:00 | 349 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-16 23:00 | 349 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-17 | 350 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-17 01:00 | 350 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-17 02:00 | 350 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-17 03:00 | 350 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-17 04:00 | 350 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-17 05:00 | 350 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-17 06:00 | 350 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-17 07:00 | 350 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-17 08:00 | 350 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-17 09:00 | 350 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-17 10:00 | 350 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-17 11:00 | 350 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-17 12:00 | 350 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-17 13:00 | 350 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-17 14:00 | 350 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-17 15:00 | 350 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-17 16:00 | 350 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-12-17 17:00 | 350 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-17 18:00 | 350 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-17 19:00 | 350 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-17 20:00 | 350 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-17 21:00 | 350 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-17 22:00 | 350 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-17 23:00 | 350 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-18 | 351 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-18 01:00 | 351 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-18 02:00 | 351 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-18 03:00 | 351 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-18 04:00 | 351 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-18 05:00 | 351 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-18 06:00 | 351 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-18 07:00 | 351 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-12-18 08:00 | 351 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-18 09:00 | 351 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-18 10:00 | 351 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-18 11:00 | 351 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-18 12:00 | 351 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-18 13:00 | 351 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-18 14:00 | 351 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-18 15:00 | 351 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-18 16:00 | 351 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-18 17:00 | 351 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-18 18:00 | 351 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-18 19:00 | 351 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-12-18 20:00 | 351 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-18 21:00 | 351 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-18 22:00 | 351 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-18 23:00 | 351 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-12-19 | 352 | 1 | 1 | 29 | 7.307 | 3.3521
2018-12-19 01:00 | 352 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-12-19 02:00 | 352 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-12-19 03:00 | 352 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-12-19 04:00 | 352 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-12-19 05:00 | 352 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-12-19 06:00 | 352 | 1 | 1 | 27 | 7.5966 | 3.4362
2018-12-19 07:00 | 352 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-12-19 08:00 | 352 | 1 | 1 | 28 | 7.4494 | 3.3935
2018-12-19 09:00 | 352 | 1 | 1 | 30 | 7.1694 | 3.3119
2018-12-19 10:00 | 352 | 1 | 1 | 32 | 6.9088 | 3.2352
2018-12-19 11:00 | 352 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-19 12:00 | 352 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-19 13:00 | 352 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-19 14:00 | 352 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-19 15:00 | 352 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-19 16:00 | 352 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-19 17:00 | 352 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-19 18:00 | 352 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-19 19:00 | 352 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-19 20:00 | 352 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-19 21:00 | 352 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-19 22:00 | 352 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-19 23:00 | 352 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-20 | 353 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-20 01:00 | 353 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-20 02:00 | 353 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-20 03:00 | 353 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-20 04:00 | 353 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-20 05:00 | 353 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-20 06:00 | 353 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-20 07:00 | 353 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-20 08:00 | 353 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-20 09:00 | 353 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-20 10:00 | 353 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-20 11:00 | 353 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-20 12:00 | 353 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-20 13:00 | 353 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-20 14:00 | 353 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-20 15:00 | 353 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-20 16:00 | 353 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-20 17:00 | 353 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-20 18:00 | 353 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-20 19:00 | 353 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-20 20:00 | 353 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-20 21:00 | 353 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-20 22:00 | 353 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-12-20 23:00 | 353 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-21 | 354 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-21 01:00 | 354 | 1 | 1 | 56 | 5.295 | 2.7043
2018-12-21 02:00 | 354 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-21 03:00 | 354 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-12-21 04:00 | 354 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-12-21 05:00 | 354 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-12-21 06:00 | 354 | 1 | 1 | 59 | 5.2897 | 2.6884
2018-12-21 07:00 | 354 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-12-21 08:00 | 354 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-12-21 09:00 | 354 | 1 | 1 | 61 | 5.3104 | 2.6841
2018-12-21 10:00 | 354 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-12-21 11:00 | 354 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-12-21 12:00 | 354 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-12-21 13:00 | 354 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-12-21 14:00 | 354 | 1 | 1 | 56 | 5.295 | 2.7043
2018-12-21 15:00 | 354 | 1 | 1 | 56 | 5.295 | 2.7043
2018-12-21 16:00 | 354 | 1 | 1 | 56 | 5.295 | 2.7043
2018-12-21 17:00 | 354 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-21 18:00 | 354 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-12-21 19:00 | 354 | 1 | 1 | 56 | 5.295 | 2.7043
2018-12-21 20:00 | 354 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-12-21 21:00 | 354 | 1 | 1 | 56 | 5.295 | 2.7043
2018-12-21 22:00 | 354 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-12-21 23:00 | 354 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-12-22 | 355 | 1 | 1 | 52 | 5.37 | 2.7429
2018-12-22 01:00 | 355 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-12-22 02:00 | 355 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-12-22 03:00 | 355 | 1 | 1 | 51 | 5.4008 | 2.7556
2018-12-22 04:00 | 355 | 1 | 1 | 52 | 5.37 | 2.7429
2018-12-22 05:00 | 355 | 1 | 1 | 52 | 5.37 | 2.7429
2018-12-22 06:00 | 355 | 1 | 1 | 52 | 5.37 | 2.7429
2018-12-22 07:00 | 355 | 1 | 1 | 49 | 5.4771 | 2.7849
2018-12-22 08:00 | 355 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-12-22 09:00 | 355 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-22 10:00 | 355 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-22 11:00 | 355 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-22 12:00 | 355 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-22 13:00 | 355 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-22 14:00 | 355 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-22 15:00 | 355 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-22 16:00 | 355 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-12-22 17:00 | 355 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-22 18:00 | 355 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-22 19:00 | 355 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-22 20:00 | 355 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-22 21:00 | 355 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-22 22:00 | 355 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-22 23:00 | 355 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-23 | 356 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-23 01:00 | 356 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-23 02:00 | 356 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-23 03:00 | 356 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-23 04:00 | 356 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-23 05:00 | 356 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-23 06:00 | 356 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-23 07:00 | 356 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-23 08:00 | 356 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-23 09:00 | 356 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-23 10:00 | 356 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-23 11:00 | 356 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-23 12:00 | 356 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-23 13:00 | 356 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-23 14:00 | 356 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-23 15:00 | 356 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-23 16:00 | 356 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-23 17:00 | 356 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-23 18:00 | 356 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-23 19:00 | 356 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-23 20:00 | 356 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-23 21:00 | 356 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-23 22:00 | 356 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-23 23:00 | 356 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-24 | 357 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-24 01:00 | 357 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-24 02:00 | 357 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-24 03:00 | 357 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-24 04:00 | 357 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-24 05:00 | 357 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-24 06:00 | 357 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-24 07:00 | 357 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-24 08:00 | 357 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-24 09:00 | 357 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-24 10:00 | 357 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-24 11:00 | 357 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-24 12:00 | 357 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-24 13:00 | 357 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-24 14:00 | 357 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-24 15:00 | 357 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-24 16:00 | 357 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-24 17:00 | 357 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-24 18:00 | 357 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-24 19:00 | 357 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-24 20:00 | 357 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-24 21:00 | 357 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-24 22:00 | 357 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-24 23:00 | 357 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-25 | 358 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-25 01:00 | 358 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-25 02:00 | 358 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-25 03:00 | 358 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-25 04:00 | 358 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-25 05:00 | 358 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-25 06:00 | 358 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-25 07:00 | 358 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-25 08:00 | 358 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-25 09:00 | 358 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-25 10:00 | 358 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-25 11:00 | 358 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-25 12:00 | 358 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-25 13:00 | 358 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-25 14:00 | 358 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-25 15:00 | 358 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-25 16:00 | 358 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-25 17:00 | 358 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-25 18:00 | 358 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-25 19:00 | 358 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-25 20:00 | 358 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-25 21:00 | 358 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-25 22:00 | 358 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-25 23:00 | 358 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-26 | 359 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-26 01:00 | 359 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-26 02:00 | 359 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-26 03:00 | 359 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-12-26 04:00 | 359 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-12-26 05:00 | 359 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-26 06:00 | 359 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-26 07:00 | 359 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-26 08:00 | 359 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-26 09:00 | 359 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-26 10:00 | 359 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-26 11:00 | 359 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-26 12:00 | 359 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-26 13:00 | 359 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-26 14:00 | 359 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-26 15:00 | 359 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-26 16:00 | 359 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-26 17:00 | 359 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-26 18:00 | 359 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-26 19:00 | 359 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-26 20:00 | 359 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-26 21:00 | 359 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-26 22:00 | 359 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-26 23:00 | 359 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-27 | 360 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-27 01:00 | 360 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-27 02:00 | 360 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-27 03:00 | 360 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-27 04:00 | 360 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-27 05:00 | 360 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-27 06:00 | 360 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-27 07:00 | 360 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-27 08:00 | 360 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-27 09:00 | 360 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-27 10:00 | 360 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-27 11:00 | 360 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-27 12:00 | 360 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-27 13:00 | 360 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-27 14:00 | 360 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-27 15:00 | 360 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-27 16:00 | 360 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-27 17:00 | 360 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-27 18:00 | 360 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-27 19:00 | 360 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-27 20:00 | 360 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-27 21:00 | 360 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-27 22:00 | 360 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-27 23:00 | 360 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-28 | 361 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-28 01:00 | 361 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-12-28 02:00 | 361 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-28 03:00 | 361 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-28 04:00 | 361 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-12-28 05:00 | 361 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-28 06:00 | 361 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-28 07:00 | 361 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-28 08:00 | 361 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-28 09:00 | 361 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-12-28 10:00 | 361 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-12-28 11:00 | 361 | 1 | 1 | 52 | 5.37 | 2.7429
2018-12-28 12:00 | 361 | 1 | 1 | 52 | 5.37 | 2.7429
2018-12-28 13:00 | 361 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-12-28 14:00 | 361 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-12-28 15:00 | 361 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-12-28 16:00 | 361 | 1 | 1 | 53 | 5.3439 | 2.7314
2018-12-28 17:00 | 361 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-12-28 18:00 | 361 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-28 19:00 | 361 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-12-28 20:00 | 361 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-12-28 21:00 | 361 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-12-28 22:00 | 361 | 1 | 1 | 58 | 5.2866 | 2.6925
2018-12-28 23:00 | 361 | 1 | 1 | 57 | 5.2884 | 2.6978
2018-12-29 | 362 | 1 | 1 | 56 | 5.295 | 2.7043
2018-12-29 01:00 | 362 | 1 | 1 | 56 | 5.295 | 2.7043
2018-12-29 02:00 | 362 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-29 03:00 | 362 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-12-29 04:00 | 362 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-12-29 05:00 | 362 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-29 06:00 | 362 | 1 | 1 | 55 | 5.3065 | 2.7121
2018-12-29 07:00 | 362 | 1 | 1 | 54 | 5.3228 | 2.7211
2018-12-29 08:00 | 362 | 1 | 1 | 52 | 5.37 | 2.7429
2018-12-29 09:00 | 362 | 1 | 1 | 52 | 5.37 | 2.7429
2018-12-29 10:00 | 362 | 1 | 1 | 50 | 5.4365 | 2.7696
2018-12-29 11:00 | 362 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-12-29 12:00 | 362 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-29 13:00 | 362 | 1 | 1 | 48 | 5.5225 | 2.8014
2018-12-29 14:00 | 362 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-29 15:00 | 362 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-29 16:00 | 362 | 1 | 1 | 47 | 5.5728 | 2.8192
2018-12-29 17:00 | 362 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-29 18:00 | 362 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-29 19:00 | 362 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-12-29 20:00 | 362 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-29 21:00 | 362 | 1 | 1 | 43 | 5.8224 | 2.9027
2018-12-29 22:00 | 362 | 1 | 1 | 41 | 5.9762 | 2.9519
2018-12-29 23:00 | 362 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-30 | 363 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-30 01:00 | 363 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-30 02:00 | 363 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-30 03:00 | 363 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-30 04:00 | 363 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-30 05:00 | 363 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-30 06:00 | 363 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-30 07:00 | 363 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-30 08:00 | 363 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-30 09:00 | 363 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-30 10:00 | 363 | 1 | 1 | 33 | 6.7858 | 3.1987
2018-12-30 11:00 | 363 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-30 12:00 | 363 | 1 | 1 | 34 | 6.6676 | 3.1635
2018-12-30 13:00 | 363 | 1 | 1 | 35 | 6.5543 | 3.1295
2018-12-30 14:00 | 363 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-30 15:00 | 363 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-30 16:00 | 363 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-30 17:00 | 363 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-30 18:00 | 363 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-30 19:00 | 363 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-30 20:00 | 363 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-30 21:00 | 363 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-30 22:00 | 363 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-30 23:00 | 363 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-31 | 364 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-31 01:00 | 364 | 1 | 1 | 40 | 6.0605 | 2.9784
2018-12-31 02:00 | 364 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-31 03:00 | 364 | 1 | 1 | 39 | 6.1495 | 3.0061
2018-12-31 04:00 | 364 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-31 05:00 | 364 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-31 06:00 | 364 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-31 07:00 | 364 | 1 | 1 | 36 | 6.4458 | 3.0968
2018-12-31 08:00 | 364 | 1 | 1 | 37 | 6.3422 | 3.0653
2018-12-31 09:00 | 364 | 1 | 1 | 38 | 6.2434 | 3.0351
2018-12-31 10:00 | 364 | 1 | 1 | 42 | 5.8969 | 2.9267
2018-12-31 11:00 | 364 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-31 12:00 | 364 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-31 13:00 | 364 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-31 14:00 | 364 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-31 15:00 | 364 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-31 16:00 | 364 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-12-31 17:00 | 364 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-31 18:00 | 364 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-31 19:00 | 364 | 1 | 1 | 44 | 5.7527 | 2.8799
2018-12-31 20:00 | 364 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-31 21:00 | 364 | 1 | 1 | 45 | 5.6879 | 2.8584
2018-12-31 22:00 | 364 | 1 | 1 | 46 | 5.6279 | 2.8382
2018-12-31 23:00 | 364 | 1 | 1 | 46 | 5.6279 | 2.8382
Formulas:
Day of Year = DAYS([Datetime],A2)
Date = DATE(YEAR([Datetime]),1,1)
Date = [Date, row above]+1
Supply Fan Daily Energy = SUMIFS(F:F,B:B,DAYS([Date],I2))
Return Fan Daily Energy = SUMIFS(G:G,B:B,DAYS([Date],I2))

## Step 7. Results
Day of Week | Supply Fan Average Runtime (Hours/day) | Return Fan Average Runtime (Hours/day)
Monday | 24 | 24
Tuesday | 24 | 24
Wednesday | 24 | 24
Thursday | 24 | 24
Friday | 24 | 24
Saturday | 24 | 24
Sunday | 24 | 24
| Annual Electricity Usage (kWh) |  | TOTAL ANNUAL ELECTRICITY USAGE (kWh)
Supply Fan | 53682.6279 |  | 79219.0491
Return Fan | 25536.4212
Fan Type | Total Days Used in Measurement Period | % of Year
Supply Fan | 295.5833 | 80.98%
Return Fan | 295.5833 | 80.98%